## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4461-14_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4461-14_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4461-14_0_4_node_74 | 0.4 | n |  | TRUE
3 | bus_LV_4461-14_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_4461-14_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_4461-14_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_4461-14_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_4461-14_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_4461-14_0_4_node_62 | 0.4 | n |  | TRUE
9 | bus_LV_4461-14_0_4_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_4461-14_0_4_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_4461-14_0_4_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_4461-14_0_4_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_4461-14_0_4_node_61 | 0.4 | n |  | TRUE
14 | bus_LV_4461-14_0_4_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_4461-14_0_4_node_73 | 0.4 | n |  | TRUE
16 | bus_LV_4461-14_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_4461-14_0_4_node_234 | 0.4 | n |  | TRUE
18 | bus_LV_4461-14_0_4_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_4461-14_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_4461-14_0_4_node_64 | 0.4 | n |  | TRUE
21 | bus_LV_4461-14_0_4_node_58 | 0.4 | n |  | TRUE
22 | bus_LV_4461-14_0_4_node_69 | 0.4 | n |  | TRUE
23 | bus_LV_4461-14_0_4_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_4461-14_0_4_node_131 | 0.4 | n |  | TRUE
25 | bus_LV_4461-14_0_4_node_129 | 0.4 | n |  | TRUE
26 | bus_LV_4461-14_0_4_node_219 | 0.4 | n |  | TRUE
27 | bus_LV_4461-14_0_4_node_130 | 0.4 | n |  | TRUE
28 | bus_LV_4461-14_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_4461-14_0_4_node_55 | 0.4 | n |  | TRUE
30 | bus_LV_4461-14_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_4461-14_0_4_node_99 | 0.4 | n |  | TRUE
32 | bus_LV_4461-14_0_4_node_237 | 0.4 | n |  | TRUE
33 | bus_LV_4461-14_0_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_4461-14_0_4_node_224 | 0.4 | n |  | TRUE
35 | bus_LV_4461-14_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_4461-14_0_4_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_4461-14_0_4_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_4461-14_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_4461-14_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_4461-14_0_4_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_4461-14_0_4_node_194 | 0.4 | n |  | TRUE
42 | bus_LV_4461-14_0_4_node_228 | 0.4 | n |  | TRUE
43 | bus_LV_4461-14_0_4_node_226 | 0.4 | n |  | TRUE
44 | bus_LV_4461-14_0_4_node_179 | 0.4 | n |  | TRUE
45 | bus_LV_4461-14_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_4461-14_0_4_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_4461-14_0_4_node_126 | 0.4 | n |  | TRUE
48 | bus_LV_4461-14_0_4_node_227 | 0.4 | n |  | TRUE
49 | bus_LV_4461-14_0_4_node_233 | 0.4 | n |  | TRUE
50 | bus_LV_4461-14_0_4_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_4461-14_0_4_node_225 | 0.4 | n |  | TRUE
52 | bus_LV_4461-14_0_4_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_4461-14_0_4_node_100 | 0.4 | n |  | TRUE
54 | bus_LV_4461-14_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_4461-14_0_4_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_4461-14_0_4_node_87 | 0.4 | n |  | TRUE
57 | bus_LV_4461-14_0_4_node_84 | 0.4 | n |  | TRUE
58 | bus_LV_4461-14_0_4_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_4461-14_0_4_node_128 | 0.4 | n |  | TRUE
60 | bus_LV_4461-14_0_4_node_124 | 0.4 | n |  | TRUE
61 | bus_LV_4461-14_0_4_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_4461-14_0_4_node_83 | 0.4 | n |  | TRUE
63 | bus_LV_4461-14_0_4_node_80 | 0.4 | n |  | TRUE
64 | bus_LV_4461-14_0_4_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_4461-14_0_4_node_95 | 0.4 | n |  | TRUE
66 | bus_LV_4461-14_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_4461-14_0_4_node_86 | 0.4 | n |  | TRUE
68 | bus_LV_4461-14_0_4_node_60 | 0.4 | n |  | TRUE
69 | bus_LV_4461-14_0_4_node_85 | 0.4 | n |  | TRUE
70 | bus_LV_4461-14_0_4_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_4461-14_0_4_node_97 | 0.4 | n |  | TRUE
72 | bus_LV_4461-14_0_4_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_4461-14_0_4_node_77 | 0.4 | n |  | TRUE
74 | bus_LV_4461-14_0_4_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_4461-14_0_4_node_88 | 0.4 | n |  | TRUE
76 | bus_LV_4461-14_0_4_node_89 | 0.4 | n |  | TRUE
77 | bus_LV_4461-14_0_4_node_63 | 0.4 | n |  | TRUE
78 | bus_LV_4461-14_0_4_node_66 | 0.4 | n |  | TRUE
79 | bus_LV_4461-14_0_4_node_65 | 0.4 | n |  | TRUE
80 | bus_LV_4461-14_0_4_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_4461-14_0_4_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_4461-14_0_4_node_238 | 0.4 | n |  | TRUE
83 | bus_LV_4461-14_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_4461-14_0_4_node_82 | 0.4 | n |  | TRUE
85 | bus_LV_4461-14_0_4_node_94 | 0.4 | n |  | TRUE
86 | bus_LV_4461-14_0_4_node_90 | 0.4 | n |  | TRUE
87 | bus_LV_4461-14_0_4_node_91 | 0.4 | n |  | TRUE
88 | bus_LV_4461-14_0_4_node_93 | 0.4 | n |  | TRUE
89 | bus_LV_4461-14_0_4_node_96 | 0.4 | n |  | TRUE
90 | bus_LV_4461-14_0_4_node_98 | 0.4 | n |  | TRUE
91 | bus_LV_4461-14_0_4_node_235 | 0.4 | n |  | TRUE
92 | bus_LV_4461-14_0_4_node_103 | 0.4 | n |  | TRUE
93 | bus_LV_4461-14_0_4_node_104 | 0.4 | n |  | TRUE
94 | bus_LV_4461-14_0_4_node_105 | 0.4 | n |  | TRUE
95 | bus_LV_4461-14_0_4_node_106 | 0.4 | n |  | TRUE
96 | bus_LV_4461-14_0_4_node_107 | 0.4 | n |  | TRUE
97 | bus_LV_4461-14_0_4_node_221 | 0.4 | n |  | TRUE
98 | bus_LV_4461-14_0_4_node_202 | 0.4 | n |  | TRUE
99 | bus_LV_4461-14_0_4_node_125 | 0.4 | n |  | TRUE
100 | bus_LV_4461-14_0_4_node_127 | 0.4 | n |  | TRUE
101 | bus_LV_4461-14_0_4_node_218 | 0.4 | n |  | TRUE
102 | bus_LV_4461-14_0_4_node_178 | 0.4 | n |  | TRUE
103 | bus_LV_4461-14_0_4_node_180 | 0.4 | n |  | TRUE
104 | bus_LV_4461-14_0_4_node_181 | 0.4 | n |  | TRUE
105 | bus_LV_4461-14_0_4_node_182 | 0.4 | n |  | TRUE
106 | bus_LV_4461-14_0_4_node_183 | 0.4 | n |  | TRUE
107 | bus_LV_4461-14_0_4_node_184 | 0.4 | n |  | TRUE
108 | bus_LV_4461-14_0_4_node_193 | 0.4 | n |  | TRUE
109 | bus_LV_4461-14_0_4_node_216 | 0.4 | n |  | TRUE
110 | bus_LV_4461-14_0_4_node_217 | 0.4 | n |  | TRUE
111 | bus_MV_407_0_node_195 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4461-14_0_4_load_0 | 0 | 0.0047084 | 0.00118 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4461-14_0_4_load_1 | 1 | 0.0082508 | 0.0020678 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4461-14_0_4_load_74 | 2 | 0.0032445 | 0.00081316 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4461-14_0_4_load_2 | 3 | 0.0024657 | 0.00061795 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4461-14_0_4_load_3 | 4 | 0.0086426 | 0.002166 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4461-14_0_4_load_4 | 5 | 0.0031522 | 0.00079001 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4461-14_0_4_load_5 | 6 | 0.003856 | 0.00096639 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4461-14_0_4_load_6 | 7 | 0.0014351 | 0.00035968 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4461-14_0_4_load_62 | 8 | 0.005215 | 0.001307 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4461-14_0_4_load_13 | 9 | 0.0039977 | 0.0010019 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4461-14_0_4_load_61 | 13 | 0.00086509 | 0.00021681 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4461-14_0_4_load_73 | 15 | 0.009355 | 0.0023446 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4461-14_0_4_load_234 | 17 | 0.014495 | 0.0036327 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4461-14_0_4_load_64 | 20 | 0.0021527 | 0.00053952 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4461-14_0_4_load_69 | 22 | 0.0040415 | 0.0010129 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4461-14_0_4_load_131 | 24 | 0.00092986 | 0.00023305 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4461-14_0_4_load_129 | 25 | 0.012597 | 0.0031572 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4461-14_0_4_load_130 | 27 | 0.0032057 | 0.00080343 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4461-14_0_4_load_99 | 31 | 0.00063163 | 0.0001583 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4461-14_0_4_load_237 | 32 | 0.0034222 | 0.00085767 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4461-14_0_4_load_224 | 34 | 0.0037174 | 0.00093168 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4461-14_0_4_load_194 | 41 | 0.0011713 | 0.00029354 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4461-14_0_4_load_228 | 42 | 0.0079415 | 0.0019903 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4461-14_0_4_load_226 | 43 | 0.0011438 | 0.00028665 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4461-14_0_4_load_179 | 44 | 0.0022018 | 0.00055182 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4461-14_0_4_load_126 | 47 | 0.0044654 | 0.0011191 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4461-14_0_4_load_227 | 48 | 0.0008839 | 0.00022153 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4461-14_0_4_load_233 | 49 | 0.00057006 | 0.00014287 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4461-14_0_4_load_225 | 51 | 0.0052456 | 0.0013147 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4461-14_0_4_load_87 | 56 | 0.0030576 | 0.00076629 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4461-14_0_4_load_84 | 57 | 0.0062967 | 0.0015781 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4461-14_0_4_load_128 | 59 | 0.0043797 | 0.0010976 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4461-14_0_4_load_124 | 60 | 0.00044208 | 0.0001108 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4461-14_0_4_load_83 | 62 | 0.00087189 | 0.00021852 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4461-14_0_4_load_80 | 63 | 0.0014466 | 0.00036254 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4461-14_0_4_load_95 | 65 | 0.001414 | 0.00035438 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4461-14_0_4_load_86 | 67 | 0.0013185 | 0.00033045 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4461-14_0_4_load_85 | 69 | 0.0036012 | 0.00090255 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4461-14_0_4_load_97 | 71 | 0.0037495 | 0.00093971 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4461-14_0_4_load_76 | 74 | 0.003958 | 0.00099198 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4461-14_0_4_load_88 | 75 | 0.0030109 | 0.0007546 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4461-14_0_4_load_89 | 76 | 0.0021283 | 0.00053339 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4461-14_0_4_load_63 | 77 | 0.0036066 | 0.00090389 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4461-14_0_4_load_66 | 78 | 0.0024005 | 0.00060163 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4461-14_0_4_load_65 | 79 | 0.0038376 | 0.00096179 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4461-14_0_4_load_67 | 80 | 0.002665 | 0.00066792 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4461-14_0_4_load_72 | 81 | 0.0022299 | 0.00055885 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4461-14_0_4_load_238 | 82 | 0.0010407 | 0.00026082 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4461-14_0_4_load_81 | 83 | 0.0013851 | 0.00034715 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4461-14_0_4_load_82 | 84 | 0.0026811 | 0.00067195 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4461-14_0_4_load_90 | 86 | 0.0093196 | 0.0023357 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4461-14_0_4_load_93 | 88 | 0.003279 | 0.00082178 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4461-14_0_4_load_96 | 89 | 0.00055911 | 0.00014013 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4461-14_0_4_load_98 | 90 | 0.0061118 | 0.0015318 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4461-14_0_4_load_235 | 91 | 0.0077958 | 0.0019538 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4461-14_0_4_load_103 | 92 | 0.001293 | 0.00032406 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4461-14_0_4_load_104 | 93 | 0.0023794 | 0.00059633 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4461-14_0_4_load_105 | 94 | 0.0021089 | 0.00052854 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4461-14_0_4_load_106 | 95 | 0.0023548 | 0.00059016 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4461-14_0_4_load_221 | 97 | 0.0021559 | 0.00054032 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4461-14_0_4_load_202 | 98 | 0.0017151 | 0.00042984 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4461-14_0_4_load_127 | 100 | 0.00030339 | 7.6038e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4461-14_0_4_load_178 | 102 | 0.001722 | 0.00043156 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4461-14_0_4_load_180 | 103 | 0.001325 | 0.00033209 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4461-14_0_4_load_181 | 104 | 0.0011815 | 0.0002961 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4461-14_0_4_load_182 | 105 | 0.0016209 | 0.00040623 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4461-14_0_4_load_183 | 106 | 0.001359 | 0.00034061 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4461-14_0_4_load_184 | 107 | 0.0026182 | 0.00065618 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4461-14_0_4_load_193 | 108 | 0.001369 | 0.0003431 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4461-14_0_4_load_216 | 109 | 0.0016942 | 0.00042461 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4461-14_0_4_load_217 | 110 | 0.0021645 | 0.00054248 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 85 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4461-14_0_4_line_0 |  | 0 | 1 | 0.017952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4461-14_0_4_line_1 |  | 0 | 2 | 0.19016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4461-14_0_4_line_2 |  | 2 | 81 | 0.30498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4461-14_0_4_line_3 |  | 3 | 4 | 0.064233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4461-14_0_4_line_4 |  | 3 | 5 | 0.011489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4461-14_0_4_line_5 |  | 4 | 6 | 0.0057275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4461-14_0_4_line_6 |  | 5 | 7 | 0.014997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4461-14_0_4_line_7 |  | 7 | 8 | 0.018182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4461-14_0_4_line_8 |  | 8 | 68 | 0.02096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4461-14_0_4_line_9 |  | 9 | 10 | 0.029147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4461-14_0_4_line_10 |  | 9 | 11 | 0.014809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4461-14_0_4_line_11 |  | 10 | 12 | 0.011008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4461-14_0_4_line_12 |  | 11 | 13 | 0.027118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4461-14_0_4_line_13 |  | 12 | 14 | 0.031605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4461-14_0_4_line_14 |  | 12 | 15 | 0.020762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4461-14_0_4_line_15 |  | 13 | 78 | 0.0044645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4461-14_0_4_line_16 |  | 14 | 19 | 0.024951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4461-14_0_4_line_17 |  | 14 | 20 | 0.015633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4461-14_0_4_line_18 |  | 15 | 81 | 0.025557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4461-14_0_4_line_19 |  | 16 | 17 | 0.018506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4461-14_0_4_line_20 |  | 16 | 18 | 0.058857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4461-14_0_4_line_21 |  | 18 | 26 | 0.002829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4461-14_0_4_line_22 |  | 18 | 27 | 0.017527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4461-14_0_4_line_23 |  | 19 | 21 | 0.026036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_4461-14_0_4_line_24 |  | 19 | 22 | 0.012754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_4461-14_0_4_line_25 |  | 21 | 75 | 0.017161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_4461-14_0_4_line_26 |  | 21 | 76 | 0.010085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4461-14_0_4_line_27 |  | 22 | 77 | 0.029926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_4461-14_0_4_line_28 |  | 23 | 24 | 0.022009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4461-14_0_4_line_29 |  | 23 | 25 | 0.030968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4461-14_0_4_line_30 |  | 25 | 27 | 0.036786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4461-14_0_4_line_31 |  | 26 | 39 | 0.014363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4461-14_0_4_line_32 |  | 28 | 29 | 0.046285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_4461-14_0_4_line_33 |  | 28 | 30 | 0.049583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_4461-14_0_4_line_34 |  | 28 | 31 | 0.0071931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4461-14_0_4_line_35 |  | 29 | 70 | 0.035175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4461-14_0_4_line_36 |  | 29 | 62 | 0.042741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_4461-14_0_4_line_37 |  | 30 | 32 | 0.013659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4461-14_0_4_line_38 |  | 30 | 33 | 0.022096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_4461-14_0_4_line_39 |  | 33 | 34 | 0.018491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_4461-14_0_4_line_40 |  | 34 | 35 | 0.02113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_4461-14_0_4_line_41 |  | 35 | 36 | 0.035605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4461-14_0_4_line_42 |  | 35 | 37 | 0.031425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_4461-14_0_4_line_43 |  | 36 | 48 | 0.019963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4461-14_0_4_line_44 |  | 37 | 43 | 0.014031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_4461-14_0_4_line_45 |  | 37 | 51 | 0.023608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4461-14_0_4_line_46 |  | 38 | 39 | 0.030127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4461-14_0_4_line_47 |  | 38 | 40 | 0.04272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_4461-14_0_4_line_48 |  | 38 | 41 | 0.023489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_4461-14_0_4_line_49 |  | 39 | 44 | 0.030541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4461-14_0_4_line_50 |  | 40 | 42 | 0.051035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4461-14_0_4_line_51 |  | 40 | 43 | 0.01257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_4461-14_0_4_line_52 |  | 41 | 108 | 0.010025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_4461-14_0_4_line_53 |  | 44 | 102 | 0.031529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4461-14_0_4_line_54 |  | 45 | 46 | 0.03301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4461-14_0_4_line_55 |  | 45 | 47 | 0.024021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4461-14_0_4_line_56 |  | 46 | 49 | 0.035045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4461-14_0_4_line_57 |  | 46 | 50 | 0.015221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4461-14_0_4_line_58 |  | 47 | 99 | 0.019309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4461-14_0_4_line_59 |  | 50 | 57 | 0.095425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4461-14_0_4_line_60 |  | 51 | 52 | 0.040592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4461-14_0_4_line_61 |  | 52 | 53 | 0.013936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4461-14_0_4_line_62 |  | 53 | 91 | 0.003259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4461-14_0_4_line_63 |  | 54 | 55 | 0.011606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_4461-14_0_4_line_64 |  | 54 | 56 | 0.014661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_4461-14_0_4_line_65 |  | 55 | 64 | 0.01092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4461-14_0_4_line_66 |  | 55 | 65 | 0.0032724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_4461-14_0_4_line_67 |  | 56 | 66 | 0.012275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_4461-14_0_4_line_68 |  | 58 | 59 | 0.020787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4461-14_0_4_line_69 |  | 58 | 60 | 0.021318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4461-14_0_4_line_70 |  | 59 | 101 | 0.06614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4461-14_0_4_line_71 |  | 60 | 99 | 0.012434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4461-14_0_4_line_72 |  | 61 | 62 | 0.033989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_4461-14_0_4_line_73 |  | 61 | 63 | 0.013115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_4461-14_0_4_line_74 |  | 63 | 83 | 0.024975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_4461-14_0_4_line_75 |  | 64 | 74 | 0.013264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4461-14_0_4_line_76 |  | 65 | 84 | 0.016045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_4461-14_0_4_line_77 |  | 66 | 67 | 0.020036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4461-14_0_4_line_78 |  | 66 | 68 | 0.01849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_4461-14_0_4_line_79 |  | 66 | 69 | 0.013153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4461-14_0_4_line_80 |  | 68 | 77 | 0.026446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_4461-14_0_4_line_81 |  | 70 | 71 | 0.037385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4461-14_0_4_line_82 |  | 71 | 89 | 0.022424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4461-14_0_4_line_83 |  | 72 | 73 | 0.004128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4461-14_0_4_line_84 |  | 72 | 74 | 0.044188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4461-14_0_4_line_85 |  | 73 | 82 | 0.013114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4461-14_0_4_line_86 |  | 75 | 85 | 0.018756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_4461-14_0_4_line_87 |  | 78 | 79 | 0.015374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4461-14_0_4_line_88 |  | 79 | 80 | 0.018086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4461-14_0_4_line_89 |  | 83 | 84 | 0.015671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_4461-14_0_4_line_90 |  | 85 | 87 | 0.006971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4461-14_0_4_line_91 |  | 86 | 87 | 0.019084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4461-14_0_4_line_92 |  | 87 | 88 | 0.030023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4461-14_0_4_line_93 |  | 89 | 90 | 0.031397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4461-14_0_4_line_94 |  | 92 | 93 | 0.023432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_4461-14_0_4_line_95 |  | 92 | 94 | 0.029215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_4461-14_0_4_line_96 |  | 93 | 95 | 0.0026228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4461-14_0_4_line_97 |  | 94 | 96 | 0.035134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_4461-14_0_4_line_98 |  | 95 | 97 | 0.0193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4461-14_0_4_line_99 |  | 96 | 98 | 0.013075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_4461-14_0_4_line_100 |  | 97 | 100 | 0.00050981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4461-14_0_4_line_101 |  | 98 | 107 | 0.0008126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_4461-14_0_4_line_102 |  | 99 | 100 | 0.014849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4461-14_0_4_line_103 |  | 101 | 110 | 0.02749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4461-14_0_4_line_104 |  | 103 | 104 | 0.014576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_4461-14_0_4_line_105 |  | 103 | 105 | 0.0077349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_4461-14_0_4_line_106 |  | 104 | 106 | 0.013076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_4461-14_0_4_line_107 |  | 105 | 107 | 0.021479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_4461-14_0_4_line_108 |  | 106 | 108 | 0.012424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_4461-14_0_4_line_109 |  | 109 | 110 | 0.036029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4461-14_0_4_trafo_94 | 0.63 MVA 20/0.4 kV | 111 | 85 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2738906.5798 | 1267222.5067 | 2738913.9917 | 1267222.1658 | 2738919.6272 | 1267219.8293 | 2738922.6964 | 1267216.6324
1 | 2738729.5441 | 1267291.9345 | 2738906.5798 | 1267222.5067
2 | 2738729.5441 | 1267291.9345 | 2738731.6273 | 1267297.8225 | 2738735.5152 | 1267304.1532 | 2738740.67 | 1267309.1235 | 2738745.9534 | 1267315.6761 | 2738750.2982 | 1267320.8276 | 2738752.3685 | 1267326.3037 | 2738753.637 | 1267332.5729 | 2738754.8459 | 1267341.054 | 2738755.8023 | 1267351.9537 | 2738766.441 | 1267440.812 | 2738775.3327 | 1267513.636 | 2738782.0607 | 1267567.6464 | 2738784.7721 | 1267587.4041
3 | 2738606.3817 | 1267576.8701 | 2738617.1519 | 1267568.4548 | 2738621.1226 | 1267567.725 | 2738626.4858 | 1267566.7053 | 2738649.8697 | 1267562.7945 | 2738652.8195 | 1267562.8861 | 2738657.1348 | 1267565.1228 | 2738658.3621 | 1267568.655 | 2738658.9416 | 1267574.4347
4 | 2738660.0877 | 1267585.8669 | 2738658.9416 | 1267574.4347
5 | 2738606.3817 | 1267576.8701 | 2738601.8685 | 1267580.3965
6 | 2738661.5838 | 1267600.7895 | 2738660.0877 | 1267585.8669
7 | 2738661.5838 | 1267600.7895 | 2738663.3975 | 1267618.8804
8 | 2738665.4884 | 1267639.7357 | 2738663.3975 | 1267618.8804
9 | 2738802.2078 | 1267632.8719 | 2738831.3351 | 1267631.7941
10 | 2738846.1339 | 1267631.2466 | 2738831.3351 | 1267631.7941
11 | 2738802.2078 | 1267632.8719 | 2738791.1739 | 1267633.2687
12 | 2738846.1339 | 1267631.2466 | 2738838.7887 | 1267609.5974 | 2738838.3178 | 1267605.3667
13 | 2738791.1739 | 1267633.2687 | 2738759.5153 | 1267634.8824
14 | 2738791.1739 | 1267633.2687 | 2738790.0426 | 1267623.4103 | 2738788.6612 | 1267612.66
15 | 2738838.3178 | 1267605.3667 | 2738837.8241 | 1267600.9296
16 | 2738734.5216 | 1267636.1635 | 2738744.8811 | 1267635.6284 | 2738759.5153 | 1267634.8824
17 | 2738759.5153 | 1267634.8824 | 2738758.7114 | 1267619.2696
18 | 2738784.7721 | 1267587.4041 | 2738785.166 | 1267590.2747 | 2738787.9927 | 1267607.4578 | 2738788.6612 | 1267612.66
19 | 2738797.7867 | 1267704.015 | 2738800.2781 | 1267699.9028 | 2738802.7154 | 1267691.3629 | 2738803.0769 | 1267686.5556
20 | 2738778.5318 | 1267745.6477 | 2738775.6026 | 1267742.12 | 2738772.556 | 1267738.456 | 2738775.3998 | 1267736.0093 | 2738786.8905 | 1267726.4253 | 2738787.4828 | 1267725.8943 | 2738782.4352 | 1267721.8273 | 2738797.7867 | 1267704.015
21 | 2738776.358 | 1267747.4651 | 2738778.5318 | 1267745.6477
22 | 2738778.5318 | 1267745.6477 | 2738782.8872 | 1267742.002 | 2738791.8761 | 1267734.2848
23 | 2738720.4323 | 1267648.011 | 2738719.9563 | 1267642.6279 | 2738724.201 | 1267642.4162 | 2738734.8467 | 1267641.8767 | 2738734.5216 | 1267636.1635
24 | 2738734.5216 | 1267636.1635 | 2738721.7841 | 1267636.8142
25 | 2738720.4323 | 1267648.011 | 2738721.9484 | 1267665.1047
26 | 2738720.4323 | 1267648.011 | 2738722.5207 | 1267647.9043 | 2738723.1838 | 1267646.6075 | 2738729.7154 | 1267646.8772
27 | 2738691.8972 | 1267638.341 | 2738721.7841 | 1267636.8142
28 | 2738826.7296 | 1267677.925 | 2738848.1895 | 1267682.8117 | 2738848.1895 | 1267682.8117
29 | 2738826.7296 | 1267677.925 | 2738826.207 | 1267680.6153 | 2738822.1808 | 1267693.956 | 2738816.2119 | 1267706.6503 | 2738816.065 | 1267706.8705
30 | 2738791.8761 | 1267734.2848 | 2738799.8721 | 1267727.4201 | 2738806.995 | 1267719.7688 | 2738808.6485 | 1267717.9837 | 2738816.065 | 1267706.8705
31 | 2738776.358 | 1267747.4651 | 2738767.378 | 1267754.9949 | 2738765.3493 | 1267756.7267
32 | 2738582.8651 | 1267724.3799 | 2738588.716 | 1267721.1807 | 2738591.9142 | 1267723.2021 | 2738613.0041 | 1267716.5792 | 2738615.6654 | 1267713.5609 | 2738616.8891 | 1267709.8749 | 2738616.3646 | 1267703.9902
33 | 2738616.3646 | 1267703.9902 | 2738619.9413 | 1267700.7932 | 2738623.285 | 1267699.1812 | 2738627.3745 | 1267698.1984 | 2738645.4688 | 1267730.3207
34 | 2738616.3646 | 1267703.9902 | 2738616.2213 | 1267701.7513 | 2738616.6555 | 1267699.615 | 2738618.0521 | 1267697.2232
35 | 2738565.2554 | 1267746.6776 | 2738566.2171 | 1267742.5961 | 2738562.7035 | 1267735.4068 | 2738582.8651 | 1267724.3799
36 | 2738582.8651 | 1267724.3799 | 2738579.3009 | 1267717.1004 | 2738576.5266 | 1267714.6663 | 2738574.1517 | 1267712.2193 | 2738572.5944 | 1267709.5914 | 2738565.0901 | 1267693.3997 | 2738564.7723 | 1267691.8574 | 2738564.3319 | 1267686.8174
37 | 2738633.5338 | 1267737.025 | 2738645.4688 | 1267730.3207
38 | 2738660.1099 | 1267736.0031 | 2738651.44 | 1267740.9156 | 2738645.4688 | 1267730.3207
39 | 2738660.1099 | 1267736.0031 | 2738669.1879 | 1267752.1123
40 | 2738681.2157 | 1267764.615 | 2738677.4307 | 1267766.7394 | 2738669.1879 | 1267752.1123
41 | 2738681.2157 | 1267764.615 | 2738698.7098 | 1267795.6558
42 | 2738681.2157 | 1267764.615 | 2738688.4881 | 1267760.5262 | 2738708.6185 | 1267749.2321
43 | 2738698.7098 | 1267795.6558 | 2738681.2988 | 1267805.4224
44 | 2738708.6185 | 1267749.2321 | 2738715.5086 | 1267761.4552
45 | 2738708.6185 | 1267749.2321 | 2738697.0318 | 1267728.6626
46 | 2738742.1687 | 1267776.0457 | 2738754.529 | 1267765.9817 | 2738765.3493 | 1267756.7267
47 | 2738721.6814 | 1267772.4057 | 2738716.4702 | 1267775.2973 | 2738721.576 | 1267781.0561 | 2738724.3125 | 1267784.1344 | 2738740.1251 | 1267771.6824 | 2738742.1687 | 1267776.0457
48 | 2738742.1687 | 1267776.0457 | 2738743.0002 | 1267777.8336 | 2738744.4474 | 1267783.8624 | 2738747.9301 | 1267798.7789
49 | 2738765.3493 | 1267756.7267 | 2738770.2612 | 1267760.8016 | 2738780.8801 | 1267772.2843 | 2738784.8124 | 1267779.8416
50 | 2738721.6814 | 1267772.4057 | 2738732.0027 | 1267766.7536 | 2738749.8125 | 1267751.9907 | 2738742.2654 | 1267737.644
51 | 2738721.6814 | 1267772.4057 | 2738715.5086 | 1267761.4552
52 | 2738747.9301 | 1267798.7789 | 2738749.1134 | 1267803.8469 | 2738751.2704 | 1267808.1577
53 | 2738784.8124 | 1267779.8416 | 2738790.6643 | 1267791.088 | 2738796.5865 | 1267808.9852
54 | 2738662.7809 | 1267822.3497 | 2738663.5753 | 1267821.8679 | 2738671.628 | 1267816.6184 | 2738673.9811 | 1267820.3105 | 2738688.9489 | 1267810.1519
55 | 2738688.9489 | 1267810.1519 | 2738701.3628 | 1267828.5723 | 2738702.6122 | 1267829.8789
56 | 2738646.1715 | 1267791.4633 | 2738662.7809 | 1267822.3497
57 | 2738656.2644 | 1267832.4066 | 2738664.9888 | 1267826.4499 | 2738662.7809 | 1267822.3497
58 | 2738702.6782 | 1267845.3417 | 2738706.7845 | 1267841.0783 | 2738707.9843 | 1267837.4474 | 2738706.949 | 1267834.0754 | 2738704.3762 | 1267831.7238 | 2738702.6122 | 1267829.8789
59 | 2738656.2644 | 1267832.4066 | 2738596.4786 | 1267867.8275 | 2738574.1681 | 1267881.0494
60 | 2738672.6108 | 1267709.3705 | 2738682.9053 | 1267703.5843 | 2738697.0318 | 1267728.6626
61 | 2738665.7268 | 1267697.2417 | 2738672.6108 | 1267709.3705
62 | 2738665.7268 | 1267697.2417 | 2738662.8803 | 1267698.8431
63 | 2738635.3317 | 1267652.4406 | 2738641.0019 | 1267652.1288 | 2738646.9208 | 1267651.8118
64 | 2738646.9208 | 1267651.8118 | 2738661.5603 | 1267651.0115
65 | 2738634.7142 | 1267641.5377 | 2738635.0225 | 1267647.0058 | 2738635.3317 | 1267652.4406
66 | 2738635.3317 | 1267652.4406 | 2738632.0642 | 1267652.6208
67 | 2738673.8166 | 1267650.3415 | 2738661.5603 | 1267651.0115
68 | 2738673.3183 | 1267861.9911 | 2738678.3004 | 1267870.7721 | 2738683.5756 | 1267880.0715
69 | 2738673.3183 | 1267861.9911 | 2738691.8623 | 1267851.4751
70 | 2738712.4358 | 1267939.3177 | 2738708.1734 | 1267925.8712 | 2738704.3401 | 1267916.917 | 2738700.8954 | 1267910.6522 | 2738700.0794 | 1267909.165 | 2738683.5756 | 1267880.0715
71 | 2738702.6782 | 1267845.3417 | 2738691.8623 | 1267851.4751
72 | 2738562.3594 | 1267656.3775 | 2738564.9715 | 1267671.4979 | 2738560.2504 | 1267674.3677 | 2738564.2737 | 1267686.1513 | 2738564.3319 | 1267686.8174
73 | 2738562.3594 | 1267656.3775 | 2738575.4554 | 1267655.6745
74 | 2738575.4554 | 1267655.6745 | 2738600.3946 | 1267654.3359
75 | 2738634.7142 | 1267641.5377 | 2738621.4666 | 1267642.193
76 | 2738632.0642 | 1267652.6208 | 2738618.5019 | 1267653.3689 | 2738616.0435 | 1267653.4987
77 | 2738673.8166 | 1267650.3415 | 2738674.9658 | 1267670.3434
78 | 2738665.4884 | 1267639.7357 | 2738666.0563 | 1267645.3768 | 2738673.5129 | 1267644.9958 | 2738673.8166 | 1267650.3415
79 | 2738673.8166 | 1267650.3415 | 2738686.9531 | 1267649.6847
80 | 2738665.4884 | 1267639.7357 | 2738672.7802 | 1267639.3175 | 2738691.8972 | 1267638.341
81 | 2738565.2554 | 1267746.6776 | 2738572.8805 | 1267763.1724 | 2738591.4182 | 1267758.1244
82 | 2738591.4182 | 1267758.1244 | 2738600.5879 | 1267778.5876
83 | 2738577.0907 | 1267640.2628 | 2738577.3328 | 1267644.3836
84 | 2738577.3328 | 1267644.3836 | 2738578.298 | 1267644.3284 | 2738621.4666 | 1267642.193
85 | 2738590.2432 | 1267640.0822 | 2738577.0907 | 1267640.2628
86 | 2738723.6054 | 1267683.7869 | 2738721.9484 | 1267665.1047
87 | 2738837.8241 | 1267600.9296 | 2738836.1237 | 1267585.65
88 | 2738834.1234 | 1267567.6754 | 2738836.1237 | 1267585.65
89 | 2738616.0435 | 1267653.4987 | 2738612.9601 | 1267653.6615 | 2738600.3946 | 1267654.3359
90 | 2738724.2255 | 1267690.7304 | 2738723.6054 | 1267683.7869
91 | 2738724.2255 | 1267690.7304 | 2738743.2366 | 1267689.0699
92 | 2738724.2255 | 1267690.7304 | 2738721.6372 | 1267690.9588 | 2738719.5729 | 1267692.2783 | 2738718.7317 | 1267694.7498 | 2738718.8673 | 1267697.3111 | 2738719.8644 | 1267699.4254 | 2738722.0042 | 1267700.6546 | 2738724.6309 | 1267700.7163 | 2738737.0139 | 1267699.6282
93 | 2738581.9897 | 1267797.7507 | 2738589.4431 | 1267794.1464 | 2738603.1388 | 1267784.2803 | 2738600.5879 | 1267778.5876
94 | 2738721.083 | 1267877.7635 | 2738732.6509 | 1267898.1413
95 | 2738754.6344 | 1267898.0562 | 2738750.0048 | 1267900.1726 | 2738737.6035 | 1267906.8658 | 2738732.6509 | 1267898.1413
96 | 2738721.083 | 1267877.7635 | 2738719.7882 | 1267875.4825
97 | 2738786.5879 | 1267883.4487 | 2738754.6344 | 1267898.0562
98 | 2738710.2606 | 1267858.6987 | 2738719.7882 | 1267875.4825
99 | 2738786.5879 | 1267883.4487 | 2738781.1962 | 1267871.5373
100 | 2738710.2606 | 1267858.6987 | 2738710.0089 | 1267858.2554
101 | 2738781.1962 | 1267871.5373 | 2738780.8611 | 1267870.797
102 | 2738702.6782 | 1267845.3417 | 2738710.0089 | 1267858.2554
103 | 2738712.4358 | 1267939.3177 | 2738739.6483 | 1267935.4181
104 | 2738762.6807 | 1267830.9614 | 2738764.2391 | 1267834.0759 | 2738768.8139 | 1267844.1825
105 | 2738772.0036 | 1267851.2291 | 2738768.8139 | 1267844.1825
106 | 2738762.6807 | 1267830.9614 | 2738756.8297 | 1267819.268
107 | 2738780.8611 | 1267870.797 | 2738772.0036 | 1267851.2291
108 | 2738751.2704 | 1267808.1577 | 2738756.8297 | 1267819.268
109 | 2738775.3132 | 1267930.3073 | 2738739.6483 | 1267935.4181

## bus_geodata
| x | y | coords
0 | 2738906.5798 | 1267222.5067
1 | 2738922.6964 | 1267216.6324
2 | 2738729.5441 | 1267291.9345
3 | 2738658.9416 | 1267574.4347
4 | 2738606.3817 | 1267576.8701
5 | 2738660.0877 | 1267585.8669
6 | 2738601.8685 | 1267580.3965
7 | 2738661.5838 | 1267600.7895
8 | 2738663.3975 | 1267618.8804
9 | 2738831.3351 | 1267631.7941
10 | 2738802.2078 | 1267632.8719
11 | 2738846.1339 | 1267631.2466
12 | 2738791.1739 | 1267633.2687
13 | 2738838.3178 | 1267605.3667
14 | 2738759.5153 | 1267634.8824
15 | 2738788.6612 | 1267612.66
16 | 2738797.7867 | 1267704.015
17 | 2738803.0769 | 1267686.5556
18 | 2738778.5318 | 1267745.6477
19 | 2738734.5216 | 1267636.1635
20 | 2738758.7114 | 1267619.2696
21 | 2738720.4323 | 1267648.011
22 | 2738721.7841 | 1267636.8142
23 | 2738826.7296 | 1267677.925
24 | 2738848.1895 | 1267682.8117
25 | 2738816.065 | 1267706.8705
26 | 2738776.358 | 1267747.4651
27 | 2738791.8761 | 1267734.2848
28 | 2738616.3646 | 1267703.9902
29 | 2738582.8651 | 1267724.3799
30 | 2738645.4688 | 1267730.3207
31 | 2738618.0521 | 1267697.2232
32 | 2738633.5338 | 1267737.025
33 | 2738660.1099 | 1267736.0031
34 | 2738669.1879 | 1267752.1123
35 | 2738681.2157 | 1267764.615
36 | 2738698.7098 | 1267795.6558
37 | 2738708.6185 | 1267749.2321
38 | 2738742.1687 | 1267776.0457
39 | 2738765.3493 | 1267756.7267
40 | 2738721.6814 | 1267772.4057
41 | 2738747.9301 | 1267798.7789
42 | 2738742.2654 | 1267737.644
43 | 2738715.5086 | 1267761.4552
44 | 2738784.8124 | 1267779.8416
45 | 2738688.9489 | 1267810.1519
46 | 2738662.7809 | 1267822.3497
47 | 2738702.6122 | 1267829.8789
48 | 2738681.2988 | 1267805.4224
49 | 2738646.1715 | 1267791.4633
50 | 2738656.2644 | 1267832.4066
51 | 2738697.0318 | 1267728.6625
52 | 2738672.6108 | 1267709.3705
53 | 2738665.7268 | 1267697.2417
54 | 2738646.9208 | 1267651.8118
55 | 2738635.3317 | 1267652.4406
56 | 2738661.5603 | 1267651.0115
57 | 2738574.1681 | 1267881.0494
58 | 2738673.3183 | 1267861.9911
59 | 2738683.5756 | 1267880.0715
60 | 2738691.8623 | 1267851.4751
61 | 2738562.3594 | 1267656.3775
62 | 2738564.3319 | 1267686.8174
63 | 2738575.4554 | 1267655.6745
64 | 2738634.7142 | 1267641.5377
65 | 2738632.0642 | 1267652.6208
66 | 2738673.8166 | 1267650.3415
67 | 2738674.9658 | 1267670.3434
68 | 2738665.4884 | 1267639.7357
69 | 2738686.9531 | 1267649.6847
70 | 2738565.2554 | 1267746.6776
71 | 2738591.4182 | 1267758.1244
72 | 2738577.3328 | 1267644.3836
73 | 2738577.0907 | 1267640.2628
74 | 2738621.4666 | 1267642.193
75 | 2738721.9484 | 1267665.1047
76 | 2738729.7154 | 1267646.8772
77 | 2738691.8972 | 1267638.341
78 | 2738837.8241 | 1267600.9296
79 | 2738836.1237 | 1267585.65
80 | 2738834.1234 | 1267567.6754
81 | 2738784.7721 | 1267587.4041
82 | 2738590.2432 | 1267640.0822
83 | 2738600.3946 | 1267654.3359
84 | 2738616.0435 | 1267653.4987
85 | 2738723.6054 | 1267683.7869
86 | 2738743.2366 | 1267689.0699
87 | 2738724.2255 | 1267690.7304
88 | 2738737.0139 | 1267699.6282
89 | 2738600.5879 | 1267778.5876
90 | 2738581.9897 | 1267797.7507
91 | 2738662.8803 | 1267698.8431
92 | 2738732.6509 | 1267898.1413
93 | 2738721.083 | 1267877.7635
94 | 2738754.6344 | 1267898.0562
95 | 2738719.7882 | 1267875.4825
96 | 2738786.5879 | 1267883.4487
97 | 2738710.2606 | 1267858.6987
98 | 2738781.1962 | 1267871.5373
99 | 2738702.6782 | 1267845.3417
100 | 2738710.0089 | 1267858.2554
101 | 2738712.4358 | 1267939.3177
102 | 2738796.5865 | 1267808.9852
103 | 2738768.8139 | 1267844.1825
104 | 2738762.6807 | 1267830.9614
105 | 2738772.0036 | 1267851.2291
106 | 2738756.8297 | 1267819.268
107 | 2738780.8611 | 1267870.7971
108 | 2738751.2704 | 1267808.1577
109 | 2738775.3132 | 1267930.3073
110 | 2738739.6483 | 1267935.4181
111 | 2738724.2255 | 1267690.7304

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1