## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4566-18_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4566-18_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4566-18_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4566-18_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_4566-18_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_4566-18_0_4_node_37 | 0.4 | n |  | TRUE
6 | bus_LV_4566-18_0_4_node_85 | 0.4 | n |  | TRUE
7 | bus_LV_4566-18_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_4566-18_0_4_node_86 | 0.4 | n |  | TRUE
9 | bus_LV_4566-18_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_4566-18_0_4_node_34 | 0.4 | n |  | TRUE
11 | bus_LV_4566-18_0_4_node_56 | 0.4 | n |  | TRUE
12 | bus_LV_4566-18_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_4566-18_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_4566-18_0_4_node_91 | 0.4 | n |  | TRUE
15 | bus_LV_4566-18_0_4_node_92 | 0.4 | n |  | TRUE
16 | bus_LV_4566-18_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_4566-18_0_4_node_90 | 0.4 | n |  | TRUE
18 | bus_LV_4566-18_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_4566-18_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_4566-18_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_4566-18_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_4566-18_0_4_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_4566-18_0_4_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_4566-18_0_4_node_89 | 0.4 | n |  | TRUE
25 | bus_LV_4566-18_0_4_node_87 | 0.4 | n |  | TRUE
26 | bus_LV_4566-18_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_4566-18_0_4_node_47 | 0.4 | n |  | TRUE
28 | bus_LV_4566-18_0_4_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_4566-18_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_4566-18_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_4566-18_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_4566-18_0_4_node_100 | 0.4 | n |  | TRUE
33 | bus_LV_4566-18_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_4566-18_0_4_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_4566-18_0_4_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_4566-18_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_4566-18_0_4_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_4566-18_0_4_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_4566-18_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_4566-18_0_4_node_101 | 0.4 | n |  | TRUE
41 | bus_LV_4566-18_0_4_node_53 | 0.4 | n |  | TRUE
42 | bus_LV_4566-18_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_4566-18_0_4_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_4566-18_0_4_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_4566-18_0_4_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_4566-18_0_4_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_4566-18_0_4_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_4566-18_0_4_node_102 | 0.4 | n |  | TRUE
49 | bus_LV_4566-18_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_4566-18_0_4_node_83 | 0.4 | n |  | TRUE
51 | bus_LV_4566-18_0_4_node_82 | 0.4 | n |  | TRUE
52 | bus_LV_4566-18_0_4_node_29 | 0.4 | n |  | TRUE
53 | bus_LV_4566-18_0_4_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_4566-18_0_4_node_94 | 0.4 | n |  | TRUE
55 | bus_LV_4566-18_0_4_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_4566-18_0_4_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_4566-18_0_4_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_4566-18_0_4_node_35 | 0.4 | n |  | TRUE
59 | bus_LV_4566-18_0_4_node_93 | 0.4 | n |  | TRUE
60 | bus_LV_4566-18_0_4_node_61 | 0.4 | n |  | TRUE
61 | bus_LV_4566-18_0_4_node_78 | 0.4 | n |  | TRUE
62 | bus_LV_4566-18_0_4_node_39 | 0.4 | n |  | TRUE
63 | bus_LV_4566-18_0_4_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_4566-18_0_4_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_4566-18_0_4_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_4566-18_0_4_node_88 | 0.4 | n |  | TRUE
67 | bus_LV_4566-18_0_4_node_99 | 0.4 | n |  | TRUE
68 | bus_LV_4566-18_0_4_node_98 | 0.4 | n |  | TRUE
69 | bus_LV_4566-18_0_4_node_52 | 0.4 | n |  | TRUE
70 | bus_LV_4566-18_0_4_node_95 | 0.4 | n |  | TRUE
71 | bus_LV_4566-18_0_4_node_50 | 0.4 | n |  | TRUE
72 | bus_LV_4566-18_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_4566-18_0_4_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_4566-18_0_4_node_79 | 0.4 | n |  | TRUE
75 | bus_LV_4566-18_0_4_node_81 | 0.4 | n |  | TRUE
76 | bus_LV_4566-18_0_4_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_4566-18_0_4_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_4566-18_0_4_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_4566-18_0_4_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_4566-18_0_4_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_4566-18_0_4_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_4566-18_0_4_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_4566-18_0_4_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_4566-18_0_4_node_68 | 0.4 | n |  | TRUE
85 | bus_LV_4566-18_0_4_node_80 | 0.4 | n |  | TRUE
86 | bus_LV_4566-18_0_4_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_4566-18_0_4_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_4566-18_0_4_node_75 | 0.4 | n |  | TRUE
89 | bus_LV_4566-18_0_4_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_4566-18_0_4_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_4566-18_0_4_node_70 | 0.4 | n |  | TRUE
92 | bus_LV_4566-18_0_4_node_71 | 0.4 | n |  | TRUE
93 | bus_LV_4566-18_0_4_node_84 | 0.4 | n |  | TRUE
94 | bus_LV_4566-18_0_4_node_96 | 0.4 | n |  | TRUE
95 | bus_LV_4566-18_0_4_node_97 | 0.4 | n |  | TRUE
96 | bus_MV_440_1_node_113 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4566-18_0_4_load_0 | 0 | 0.0053332 | 0.0013366 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4566-18_0_4_load_1 | 1 | 0.0013154 | 0.00032968 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4566-18_0_4_load_37 | 5 | 0.0047732 | 0.0011963 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4566-18_0_4_load_85 | 6 | 0.0083119 | 0.0020831 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4566-18_0_4_load_86 | 8 | 0.030634 | 0.0076777 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4566-18_0_4_load_56 | 11 | 0.042094 | 0.01055 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4566-18_0_4_load_91 | 14 | 0.01592 | 0.00399 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4566-18_0_4_load_92 | 15 | 0.012861 | 0.0032233 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4566-18_0_4_load_90 | 17 | 0.0092248 | 0.0023119 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4566-18_0_4_load_41 | 23 | 0.0020986 | 0.00052596 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4566-18_0_4_load_89 | 24 | 0.0040044 | 0.0010036 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4566-18_0_4_load_87 | 25 | 0.0022002 | 0.00055142 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4566-18_0_4_load_47 | 27 | 0.021076 | 0.0052821 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4566-18_0_4_load_45 | 28 | 0.01185 | 0.00297 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4566-18_0_4_load_100 | 32 | 0.0060479 | 0.0015157 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4566-18_0_4_load_51 | 35 | 0.0026018 | 0.00065208 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4566-18_0_4_load_48 | 37 | 0.017583 | 0.0044067 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4566-18_0_4_load_101 | 40 | 0.0094581 | 0.0023704 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4566-18_0_4_load_53 | 41 | 0.003072 | 0.00076993 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4566-18_0_4_load_44 | 43 | 0.0053039 | 0.0013293 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4566-18_0_4_load_42 | 44 | 0.005762 | 0.0014441 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4566-18_0_4_load_46 | 47 | 0.014339 | 0.0035938 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4566-18_0_4_load_102 | 48 | 0.0072957 | 0.0018285 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4566-18_0_4_load_83 | 50 | 0.055015 | 0.013788 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4566-18_0_4_load_82 | 51 | 0.003619 | 0.00090701 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4566-18_0_4_load_94 | 54 | 0.01405 | 0.0035213 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4566-18_0_4_load_43 | 55 | 0.0078276 | 0.0019618 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4566-18_0_4_load_93 | 59 | 0.0033611 | 0.00084238 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4566-18_0_4_load_78 | 61 | 0.0011722 | 0.00029379 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4566-18_0_4_load_57 | 64 | 0.015097 | 0.0037838 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4566-18_0_4_load_40 | 65 | 0.0015806 | 0.00039613 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4566-18_0_4_load_88 | 66 | 0.0033158 | 0.00083102 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4566-18_0_4_load_99 | 67 | 0.0052256 | 0.0013096 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4566-18_0_4_load_98 | 68 | 0.028487 | 0.0071396 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4566-18_0_4_load_52 | 69 | 0.0016745 | 0.00041967 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4566-18_0_4_load_95 | 70 | 0.013907 | 0.0034854 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4566-18_0_4_load_50 | 71 | 0.027997 | 0.0070167 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4566-18_0_4_load_63 | 72 | 0.00055524 | 0.00013916 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4566-18_0_4_load_60 | 73 | 0.003474 | 0.00087067 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4566-18_0_4_load_79 | 74 | 0.0006148 | 0.00015408 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4566-18_0_4_load_81 | 75 | 0.00028079 | 7.0374e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4566-18_0_4_load_59 | 76 | 0.0003958 | 9.9196e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4566-18_0_4_load_66 | 77 | 0.00054214 | 0.00013587 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4566-18_0_4_load_54 | 78 | 0.0082048 | 0.0020563 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4566-18_0_4_load_62 | 81 | 0.0039378 | 0.00098691 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4566-18_0_4_load_64 | 82 | 0.0035878 | 0.00089919 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4566-18_0_4_load_65 | 83 | 0.0035855 | 0.00089862 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4566-18_0_4_load_68 | 84 | 0.00071519 | 0.00017924 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4566-18_0_4_load_80 | 85 | 0.0016469 | 0.00041276 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4566-18_0_4_load_69 | 86 | 0.00044088 | 0.0001105 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4566-18_0_4_load_76 | 89 | 0.00071538 | 0.00017929 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4566-18_0_4_load_73 | 90 | 0.00077052 | 0.00019311 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4566-18_0_4_load_70 | 91 | 0.00076379 | 0.00019142 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4566-18_0_4_load_71 | 92 | 0.0019363 | 0.00048527 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4566-18_0_4_load_84 | 93 | 0.00053394 | 0.00013382 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4566-18_0_4_load_96 | 94 | 0.0088351 | 0.0022143 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4566-18_0_4_load_97 | 95 | 0.0077337 | 0.0019382 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4566-18_0_4_line_0 |  | 0 | 1 | 0.01179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4566-18_0_4_line_1 |  | 0 | 2 | 0.039608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4566-18_0_4_line_2 |  | 2 | 3 | 0.007333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4566-18_0_4_line_3 |  | 3 | 4 | 0.02624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4566-18_0_4_line_4 |  | 3 | 5 | 0.031294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4566-18_0_4_line_5 |  | 4 | 6 | 0.0049529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4566-18_0_4_line_6 |  | 5 | 22 | 0.019233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4566-18_0_4_line_7 |  | 6 | 7 | 0.023548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4566-18_0_4_line_8 |  | 7 | 8 | 0.020419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4566-18_0_4_line_9 |  | 8 | 18 | 0.022014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4566-18_0_4_line_10 |  | 9 | 10 | 0.023108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4566-18_0_4_line_11 |  | 9 | 11 | 0.024673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4566-18_0_4_line_12 |  | 10 | 59 | 0.011546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4566-18_0_4_line_13 |  | 10 | 33 | 0.007537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4566-18_0_4_line_14 |  | 11 | 12 | 0.026187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4566-18_0_4_line_15 |  | 12 | 13 | 0.027829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4566-18_0_4_line_16 |  | 13 | 14 | 0.013782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_4566-18_0_4_line_17 |  | 13 | 15 | 0.008524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_4566-18_0_4_line_18 |  | 14 | 16 | 0.0097922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_4566-18_0_4_line_19 |  | 15 | 29 | 0.013801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_4566-18_0_4_line_20 |  | 16 | 17 | 0.0080586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_4566-18_0_4_line_21 |  | 17 | 20 | 0.014102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_4566-18_0_4_line_22 |  | 18 | 19 | 0.0082317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4566-18_0_4_line_23 |  | 18 | 20 | 0.029098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4566-18_0_4_line_24 |  | 19 | 25 | 0.00026063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4566-18_0_4_line_25 |  | 20 | 24 | 0.0090864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4566-18_0_4_line_26 |  | 21 | 22 | 0.003477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4566-18_0_4_line_27 |  | 21 | 23 | 0.0039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4566-18_0_4_line_28 |  | 23 | 65 | 0.015715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4566-18_0_4_line_29 |  | 24 | 66 | 0.010251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4566-18_0_4_line_30 |  | 26 | 27 | 0.03108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_4566-18_0_4_line_31 |  | 26 | 28 | 0.016161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_4566-18_0_4_line_32 |  | 27 | 45 | 0.031026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_4566-18_0_4_line_33 |  | 28 | 30 | 0.009291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_4566-18_0_4_line_34 |  | 29 | 30 | 0.036758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_4566-18_0_4_line_35 |  | 31 | 32 | 0.015416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4566-18_0_4_line_36 |  | 31 | 33 | 0.00995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4566-18_0_4_line_37 |  | 33 | 41 | 0.012467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4566-18_0_4_line_38 |  | 34 | 35 | 0.0074661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4566-18_0_4_line_39 |  | 34 | 36 | 0.025111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4566-18_0_4_line_40 |  | 34 | 37 | 0.021254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4566-18_0_4_line_41 |  | 35 | 66 | 0.0096717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4566-18_0_4_line_42 |  | 36 | 55 | 0.012638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4566-18_0_4_line_43 |  | 36 | 44 | 0.0040152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4566-18_0_4_line_44 |  | 37 | 57 | 0.012951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4566-18_0_4_line_45 |  | 38 | 39 | 0.069483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4566-18_0_4_line_46 |  | 38 | 40 | 0.045117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4566-18_0_4_line_47 |  | 39 | 53 | 0.10063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4566-18_0_4_line_48 |  | 39 | 54 | 0.0033288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4566-18_0_4_line_49 |  | 39 | 45 | 0.050126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_4566-18_0_4_line_50 |  | 41 | 69 | 0.016425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4566-18_0_4_line_51 |  | 42 | 43 | 0.027724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4566-18_0_4_line_52 |  | 42 | 44 | 0.025673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4566-18_0_4_line_53 |  | 46 | 47 | 0.0029825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4566-18_0_4_line_54 |  | 46 | 48 | 0.014558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4566-18_0_4_line_55 |  | 48 | 56 | 0.019489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4566-18_0_4_line_56 |  | 49 | 50 | 0.015572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4566-18_0_4_line_57 |  | 49 | 51 | 0.0081508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4566-18_0_4_line_58 |  | 51 | 52 | 0.010493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4566-18_0_4_line_59 |  | 52 | 53 | 0.049247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4566-18_0_4_line_60 |  | 53 | 58 | 0.053122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4566-18_0_4_line_61 |  | 54 | 70 | 0.0063488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4566-18_0_4_line_62 |  | 56 | 57 | 0.018341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4566-18_0_4_line_63 |  | 57 | 71 | 0.015258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4566-18_0_4_line_64 |  | 58 | 60 | 0.024061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4566-18_0_4_line_65 |  | 58 | 61 | 0.029796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4566-18_0_4_line_66 |  | 60 | 72 | 0.01939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4566-18_0_4_line_67 |  | 60 | 73 | 0.051117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4566-18_0_4_line_68 |  | 61 | 74 | 0.026397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4566-18_0_4_line_69 |  | 62 | 63 | 0.011998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4566-18_0_4_line_70 |  | 62 | 64 | 0.087153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4566-18_0_4_line_71 |  | 63 | 75 | 0.03812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4566-18_0_4_line_72 |  | 67 | 68 | 0.017593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4566-18_0_4_line_73 |  | 68 | 95 | 0.025575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4566-18_0_4_line_74 |  | 69 | 78 | 0.0050863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4566-18_0_4_line_75 |  | 70 | 94 | 0.0063642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4566-18_0_4_line_76 |  | 73 | 81 | 0.027976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4566-18_0_4_line_77 |  | 75 | 79 | 0.022277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4566-18_0_4_line_78 |  | 76 | 77 | 0.015463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4566-18_0_4_line_79 |  | 77 | 80 | 0.0031141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4566-18_0_4_line_80 |  | 79 | 88 | 0.024063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4566-18_0_4_line_81 |  | 79 | 80 | 0.015381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4566-18_0_4_line_82 |  | 80 | 87 | 0.019717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4566-18_0_4_line_83 |  | 81 | 82 | 0.017871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4566-18_0_4_line_84 |  | 81 | 83 | 0.012761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4566-18_0_4_line_85 |  | 82 | 84 | 0.0060407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4566-18_0_4_line_86 |  | 83 | 85 | 0.010916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4566-18_0_4_line_87 |  | 84 | 86 | 0.012497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4566-18_0_4_line_88 |  | 86 | 89 | 0.014561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4566-18_0_4_line_89 |  | 87 | 89 | 0.013766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4566-18_0_4_line_90 |  | 87 | 90 | 0.014476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4566-18_0_4_line_91 |  | 88 | 93 | 0.011228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4566-18_0_4_line_92 |  | 90 | 92 | 0.010806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4566-18_0_4_line_93 |  | 91 | 92 | 0.0090206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4566-18_0_4_line_94 |  | 94 | 95 | 0.0036943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4566-18_0_4_trafo_47 | 0.63 MVA 20/0.4 kV | 96 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2710180.4421 | 1268626.2126 | 2710180.1066 | 1268622.5539 | 2710183.824 | 1268617.7857 | 2710185.3113 | 1268616.3456
1 | 2710184.0673 | 1268665.6543 | 2710183.7968 | 1268662.8024 | 2710180.4421 | 1268626.2126
2 | 2710184.0673 | 1268665.6543 | 2710181.7618 | 1268672.6174
3 | 2710168.8811 | 1268694.4519 | 2710172.02 | 1268691.2298 | 2710174.8355 | 1268688.8024 | 2710177.0486 | 1268686.7864 | 2710178.4598 | 1268684.1771 | 2710179.6846 | 1268681.0639 | 2710180.038 | 1268679.0687 | 2710180.2654 | 1268676.9711 | 2710181.7618 | 1268672.6174
4 | 2710181.7618 | 1268672.6174 | 2710152.9096 | 1268663.2713 | 2710152.0108 | 1268662.9173
5 | 2710168.8811 | 1268694.4519 | 2710166.0838 | 1268698.5392
6 | 2710134.1157 | 1268655.8701 | 2710152.0108 | 1268662.9173
7 | 2710152.7848 | 1268717.9724 | 2710153.2878 | 1268717.2367 | 2710166.0838 | 1268698.5392
8 | 2710152.7848 | 1268717.9724 | 2710147.9608 | 1268714.6796 | 2710135.9471 | 1268706.4209
9 | 2710117.6299 | 1268694.2186 | 2710123.9992 | 1268698.2074 | 2710135.9471 | 1268706.4209
10 | 2710095.297 | 1268820.4795 | 2710097.7326 | 1268815.009 | 2710100.5144 | 1268807.9213 | 2710105.8827 | 1268807.8546 | 2710110.0176 | 1268807.7316
11 | 2710110.0176 | 1268807.7316 | 2710112.5522 | 1268806.233 | 2710114.9308 | 1268802.6075 | 2710116.3371 | 1268797.0289 | 2710119.0347 | 1268788.8053 | 2710119.8973 | 1268785.9484
12 | 2710095.297 | 1268820.4795 | 2710105.6983 | 1268825.4927
13 | 2710095.297 | 1268820.4795 | 2710088.4933 | 1268817.1943
14 | 2710127.4371 | 1268760.8708 | 2710127.1897 | 1268761.6224 | 2710122.4205 | 1268777.5919 | 2710119.8973 | 1268785.9484
15 | 2710108.3044 | 1268749.0483 | 2710129.3037 | 1268755.234 | 2710127.4371 | 1268760.8708
16 | 2710108.3044 | 1268749.0483 | 2710115.4406 | 1268737.7381 | 2710115.6574 | 1268737.3918
17 | 2710108.3044 | 1268749.0483 | 2710101.6468 | 1268744.3757 | 2710101.3273 | 1268744.1513
18 | 2710120.8264 | 1268729.0753 | 2710119.8321 | 1268730.7249 | 2710115.6574 | 1268737.3918
19 | 2710090.0334 | 1268736.2189 | 2710101.3273 | 1268744.1513
20 | 2710120.8264 | 1268729.0753 | 2710114.8466 | 1268723.6731
21 | 2710104.4001 | 1268714.2006 | 2710105.3915 | 1268715.131 | 2710114.8466 | 1268723.6731
22 | 2710110.5416 | 1268690.0384 | 2710114.624 | 1268692.3276 | 2710117.6299 | 1268694.2186
23 | 2710104.4001 | 1268714.2006 | 2710107.7148 | 1268709.6251 | 2710106.3534 | 1268708.3541 | 2710114.624 | 1268692.3276 | 2710117.6299 | 1268694.2186
24 | 2710110.4382 | 1268690.2776 | 2710110.5416 | 1268690.0384
25 | 2710104.4001 | 1268714.2006 | 2710097.7671 | 1268707.9906
26 | 2710130.8883 | 1268654.5532 | 2710134.1157 | 1268655.8701
27 | 2710130.8883 | 1268654.5532 | 2710132.4308 | 1268650.9712
28 | 2710138.6464 | 1268636.5374 | 2710132.4308 | 1268650.9712
29 | 2710090.2837 | 1268700.9844 | 2710097.7671 | 1268707.9906
30 | 2710059.7093 | 1268790.4903 | 2710056.7428 | 1268788.9115 | 2710033.114 | 1268774.4191
31 | 2710059.7093 | 1268790.4903 | 2710062.0294 | 1268786.3632 | 2710067.6159 | 1268776.3959
32 | 2710007.3678 | 1268757.1198 | 2710019.2164 | 1268764.7804 | 2710031.5726 | 1268773.4736 | 2710033.114 | 1268774.4191
33 | 2710072.1597 | 1268768.2917 | 2710070.727 | 1268770.845 | 2710067.6159 | 1268776.3959
34 | 2710072.1597 | 1268768.2917 | 2710077.9466 | 1268757.0786 | 2710083.7336 | 1268745.8655 | 2710090.0334 | 1268736.2189
35 | 2710079.5111 | 1268812.8565 | 2710073.2265 | 1268826.9407
36 | 2710088.4933 | 1268817.1943 | 2710086.4865 | 1268816.2228 | 2710079.5111 | 1268812.8565
37 | 2710088.4933 | 1268817.1943 | 2710083.1351 | 1268828.4512
38 | 2710077.7732 | 1268689.2716 | 2710083.2234 | 1268694.3743
39 | 2710073.9841 | 1268671.6523 | 2710070.5106 | 1268673.8451 | 2710067.1663 | 1268675.9735 | 2710072.4468 | 1268683.0447 | 2710076.1011 | 1268687.7058 | 2710077.7732 | 1268689.2716
40 | 2710077.7732 | 1268689.2716 | 2710075.2893 | 1268692.0834 | 2710065.6228 | 1268703.8469 | 2710063.7137 | 1268705.0864
41 | 2710083.2234 | 1268694.3743 | 2710090.2837 | 1268700.9844
42 | 2710073.9841 | 1268671.6523 | 2710078.3992 | 1268677.4952 | 2710081.9074 | 1268681.4877
43 | 2710073.9841 | 1268671.6523 | 2710071.9194 | 1268668.2086
44 | 2710052.9106 | 1268712.2286 | 2710059.9613 | 1268707.5225 | 2710063.7137 | 1268705.0864
45 | 2709929.2132 | 1268705.9872 | 2709936.7387 | 1268698.821 | 2709939.4516 | 1268696.2358 | 2709944.5974 | 1268702.0589 | 2709949.2785 | 1268707.3729 | 2709952.427 | 1268711.713 | 2709952.3272 | 1268713.8352 | 2709952.6345 | 1268715.9317 | 2709953.3348 | 1268717.9353 | 2709954.7159 | 1268720.1741 | 2709956.5857 | 1268722.0328 | 2709958.8409 | 1268723.4093 | 2709961.3552 | 1268724.2123 | 2709963.587 | 1268724.4207 | 2709965.8273 | 1268724.1733 | 2709970.9762 | 1268729.8296 | 2709973.1999 | 1268732.4955 | 2709971.006 | 1268733.8893
46 | 2709929.2132 | 1268705.9872 | 2709922.0219 | 1268698.4357 | 2709897.8449 | 1268673.5594
47 | 2709921.05 | 1268771.6594 | 2709928.7797 | 1268771.7144 | 2709935.5667 | 1268773.887 | 2709938.2718 | 1268774.9493 | 2709937.4673 | 1268771.6648 | 2709934.1163 | 1268768.0994 | 2709927.7588 | 1268761.4531 | 2709922.6908 | 1268757.9224 | 2709944.503 | 1268744.3163 | 2709950.6266 | 1268737.2463 | 2709954.071 | 1268734.1855 | 2709954.3226 | 1268734.0122 | 2709958.798 | 1268730.9706 | 2709960.5451 | 1268730.1246 | 2709962.7671 | 1268729.6433 | 2709965.3585 | 1268729.9474 | 2709967.7729 | 1268730.8598 | 2709971.006 | 1268733.8893
48 | 2709971.006 | 1268733.8893 | 2709972.7459 | 1268736.7272
49 | 2709971.006 | 1268733.8893 | 2709973.1999 | 1268732.4955 | 2709974.1348 | 1268733.625 | 2709980.2387 | 1268741.3565 | 2709986.6822 | 1268748.2269 | 2709993.0239 | 1268752.0817 | 2710001.9527 | 1268759.2875 | 2710004.6009 | 1268760.9827 | 2710007.3678 | 1268757.1198
50 | 2710083.1351 | 1268828.4512 | 2710076.0761 | 1268843.2815
51 | 2710058.7185 | 1268646.1901 | 2710083.3237 | 1268633.4151
52 | 2710058.7185 | 1268646.1901 | 2710071.9194 | 1268668.2086
53 | 2710009.7592 | 1268720.8882 | 2710011.3692 | 1268723.3987
54 | 2710009.7592 | 1268720.8882 | 2710022.2456 | 1268713.4033
55 | 2710038.9612 | 1268703.3833 | 2710022.2456 | 1268713.4033
56 | 2709885.977 | 1268817.0801 | 2709885.4088 | 1268803.5243 | 2709883.3986 | 1268803.5425
57 | 2709883.3986 | 1268803.5425 | 2709883.3101 | 1268795.3922
58 | 2709883.1961 | 1268784.9002 | 2709883.3101 | 1268795.3922
59 | 2709883.1961 | 1268784.9002 | 2709882.9105 | 1268780.024 | 2709899.5659 | 1268769.6691 | 2709906.5209 | 1268776.1597 | 2709917.3932 | 1268772.3809 | 2709921.05 | 1268771.6594
60 | 2709965.5333 | 1268797.3429 | 2709961.573 | 1268792.9431 | 2709938.2718 | 1268774.9493 | 2709935.5667 | 1268773.887 | 2709928.7797 | 1268771.7144 | 2709921.05 | 1268771.6594
61 | 2709972.7459 | 1268736.7272 | 2709975.3236 | 1268740.9313 | 2709976.2178 | 1268742.031
62 | 2710052.9106 | 1268712.2286 | 2710046.473 | 1268711.0966 | 2710044.6364 | 1268711.4961 | 2710041.7818 | 1268708.3513 | 2710038.9612 | 1268703.3833
63 | 2710052.9106 | 1268712.2286 | 2710064.9039 | 1268721.6601
64 | 2709983.8801 | 1268812.9758 | 2709965.5333 | 1268797.3429
65 | 2709965.5333 | 1268797.3429 | 2709964.6122 | 1268827.1247
66 | 2709983.8801 | 1268812.9758 | 2709982.435 | 1268832.3123
67 | 2709983.8801 | 1268812.9758 | 2710009.3818 | 1268837.2829 | 2710013.9426 | 1268844.5964 | 2710014.9342 | 1268851.7965
68 | 2709964.6122 | 1268827.1247 | 2709963.7962 | 1268853.5088
69 | 2709926.854 | 1268951.9361 | 2709926.5629 | 1268963.9301
70 | 2709926.854 | 1268951.9361 | 2709927.146 | 1268935.8497 | 2709928.4348 | 1268864.7973
71 | 2709926.5629 | 1268963.9301 | 2709938.4778 | 1268964.3744 | 2709964.6214 | 1268962.6977
72 | 2710016.9872 | 1268775.8166 | 2710012.2679 | 1268772.8914 | 2710002.4136 | 1268765.9727
73 | 2710002.4136 | 1268765.9727 | 2710000.4388 | 1268764.5862 | 2709988.0896 | 1268754.7032 | 2709982.738 | 1268749.6728
74 | 2710071.5304 | 1268842.0111 | 2710075.8956 | 1268843.6606 | 2710076.0761 | 1268843.2815
75 | 2709976.2178 | 1268742.031 | 2709980.233 | 1268746.9687
76 | 2710013.0269 | 1268879.5989 | 2710015.5273 | 1268856.1027 | 2710014.9342 | 1268851.7965
77 | 2709986.8531 | 1268961.272 | 2709964.6214 | 1268962.6977
78 | 2709968.0178 | 1268947.7015 | 2709983.4079 | 1268946.1991
79 | 2709986.5073 | 1268945.8965 | 2709983.4079 | 1268946.1991
80 | 2709986.8531 | 1268961.272 | 2709986.2049 | 1268968.1882 | 2709995.2996 | 1268969.3029 | 2709999.8968 | 1268969.8111 | 2710003.2456 | 1268970.2628
81 | 2709986.8531 | 1268961.272 | 2709986.7856 | 1268955.1987 | 2709986.5073 | 1268945.8965
82 | 2710006.1893 | 1268943.9723 | 2709986.5073 | 1268945.8965
83 | 2710013.0269 | 1268879.5989 | 2710011.1393 | 1268897.3704
84 | 2710013.0269 | 1268879.5989 | 2710000.3377 | 1268878.2476
85 | 2710011.1393 | 1268897.3704 | 2710010.5012 | 1268903.3772
86 | 2709989.4828 | 1268877.0917 | 2710000.3377 | 1268878.2476
87 | 2710010.5012 | 1268903.3772 | 2710009.1813 | 1268915.8044
88 | 2710009.1813 | 1268915.8044 | 2710007.6433 | 1268930.2838
89 | 2710006.1893 | 1268943.9723 | 2710007.6433 | 1268930.2838
90 | 2710006.1893 | 1268943.9723 | 2710020.6629 | 1268944.2259
91 | 2710003.2456 | 1268970.2628 | 2710001.9945 | 1268981.4207
92 | 2710020.6629 | 1268944.2259 | 2710031.4671 | 1268944.4152
93 | 2710040.4863 | 1268944.5732 | 2710031.4671 | 1268944.4152
94 | 2709980.233 | 1268746.9687 | 2709981.4389 | 1268748.4517 | 2709982.738 | 1268749.6728

## bus_geodata
| x | y | coords
0 | 2710180.4421 | 1268626.2126
1 | 2710185.3113 | 1268616.3456
2 | 2710184.0673 | 1268665.6543
3 | 2710181.7618 | 1268672.6174
4 | 2710168.8811 | 1268694.4519
5 | 2710152.0108 | 1268662.9173
6 | 2710166.0838 | 1268698.5392
7 | 2710152.7848 | 1268717.9724
8 | 2710135.9471 | 1268706.4209
9 | 2710110.0176 | 1268807.7316
10 | 2710095.297 | 1268820.4795
11 | 2710119.8973 | 1268785.9484
12 | 2710127.4371 | 1268760.8708
13 | 2710108.3044 | 1268749.0483
14 | 2710115.6574 | 1268737.3918
15 | 2710101.3273 | 1268744.1513
16 | 2710120.8264 | 1268729.0753
17 | 2710114.8466 | 1268723.6731
18 | 2710117.6299 | 1268694.2186
19 | 2710110.5416 | 1268690.0384
20 | 2710104.4001 | 1268714.2006
21 | 2710130.8883 | 1268654.5532
22 | 2710134.1157 | 1268655.8701
23 | 2710132.4308 | 1268650.9712
24 | 2710097.7671 | 1268707.9906
25 | 2710110.4382 | 1268690.2776
26 | 2710059.7093 | 1268790.4903
27 | 2710033.114 | 1268774.4191
28 | 2710067.6159 | 1268776.3959
29 | 2710090.0334 | 1268736.2189
30 | 2710072.1597 | 1268768.2917
31 | 2710079.5111 | 1268812.8565
32 | 2710073.2265 | 1268826.9406
33 | 2710088.4933 | 1268817.1943
34 | 2710077.7732 | 1268689.2716
35 | 2710083.2234 | 1268694.3743
36 | 2710073.9841 | 1268671.6523
37 | 2710063.7137 | 1268705.0864
38 | 2709929.2132 | 1268705.9872
39 | 2709971.006 | 1268733.8893
40 | 2709897.8449 | 1268673.5594
41 | 2710083.1351 | 1268828.4512
42 | 2710058.7185 | 1268646.1901
43 | 2710083.3237 | 1268633.4151
44 | 2710071.9194 | 1268668.2086
45 | 2710007.3678 | 1268757.1198
46 | 2710009.7592 | 1268720.8882
47 | 2710011.3692 | 1268723.3987
48 | 2710022.2456 | 1268713.4033
49 | 2709883.3986 | 1268803.5425
50 | 2709885.977 | 1268817.0801
51 | 2709883.3101 | 1268795.3922
52 | 2709883.1961 | 1268784.9002
53 | 2709921.05 | 1268771.6594
54 | 2709972.7459 | 1268736.7272
55 | 2710081.9074 | 1268681.4877
56 | 2710038.9612 | 1268703.3833
57 | 2710052.9106 | 1268712.2286
58 | 2709965.5333 | 1268797.3429
59 | 2710105.6983 | 1268825.4927
60 | 2709983.8801 | 1268812.9758
61 | 2709964.6122 | 1268827.1247
62 | 2709926.854 | 1268951.9361
63 | 2709926.5629 | 1268963.9301
64 | 2709928.4348 | 1268864.7973
65 | 2710138.6464 | 1268636.5374
66 | 2710090.2837 | 1268700.9844
67 | 2710016.9872 | 1268775.8166
68 | 2710002.4136 | 1268765.9727
69 | 2710076.0761 | 1268843.2815
70 | 2709976.2178 | 1268742.031
71 | 2710064.9039 | 1268721.6601
72 | 2709982.435 | 1268832.3123
73 | 2710014.9342 | 1268851.7965
74 | 2709963.7962 | 1268853.5088
75 | 2709964.6214 | 1268962.6977
76 | 2709968.0178 | 1268947.7015
77 | 2709983.4079 | 1268946.1991
78 | 2710071.5304 | 1268842.0111
79 | 2709986.8531 | 1268961.272
80 | 2709986.5073 | 1268945.8965
81 | 2710013.0269 | 1268879.5989
82 | 2710011.1393 | 1268897.3704
83 | 2710000.3377 | 1268878.2476
84 | 2710010.5012 | 1268903.3772
85 | 2709989.4828 | 1268877.0917
86 | 2710009.1813 | 1268915.8044
87 | 2710006.1893 | 1268943.9723
88 | 2710003.2456 | 1268970.2628
89 | 2710007.6433 | 1268930.2838
90 | 2710020.6629 | 1268944.2259
91 | 2710040.4863 | 1268944.5732
92 | 2710031.4671 | 1268944.4152
93 | 2710001.9945 | 1268981.4207
94 | 2709980.233 | 1268746.9687
95 | 2709982.738 | 1268749.6728
96 | 2710007.3678 | 1268757.1198

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1