## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4566-34_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4566-34_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4566-34_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4566-34_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4566-34_0_8_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_4566-34_0_8_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_4566-34_0_8_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_4566-34_0_8_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_4566-34_0_8_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_4566-34_0_8_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_4566-34_0_8_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_4566-34_0_8_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_4566-34_0_8_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_4566-34_0_8_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_4566-34_0_8_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_4566-34_0_8_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_4566-34_0_8_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_4566-34_0_8_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_4566-34_0_8_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_4566-34_0_8_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_4566-34_0_8_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_4566-34_0_8_node_95 | 0.4 | n |  | TRUE
22 | bus_LV_4566-34_0_8_node_270 | 0.4 | n |  | TRUE
23 | bus_LV_4566-34_0_8_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_4566-34_0_8_node_165 | 0.4 | n |  | TRUE
25 | bus_LV_4566-34_0_8_node_174 | 0.4 | n |  | TRUE
26 | bus_LV_4566-34_0_8_node_180 | 0.4 | n |  | TRUE
27 | bus_LV_4566-34_0_8_node_55 | 0.4 | n |  | TRUE
28 | bus_LV_4566-34_0_8_node_135 | 0.4 | n |  | TRUE
29 | bus_LV_4566-34_0_8_node_56 | 0.4 | n |  | TRUE
30 | bus_LV_4566-34_0_8_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_4566-34_0_8_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_4566-34_0_8_node_185 | 0.4 | n |  | TRUE
33 | bus_LV_4566-34_0_8_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_4566-34_0_8_node_92 | 0.4 | n |  | TRUE
35 | bus_LV_4566-34_0_8_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_4566-34_0_8_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_4566-34_0_8_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_4566-34_0_8_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_4566-34_0_8_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_4566-34_0_8_node_110 | 0.4 | n |  | TRUE
41 | bus_LV_4566-34_0_8_node_94 | 0.4 | n |  | TRUE
42 | bus_LV_4566-34_0_8_node_114 | 0.4 | n |  | TRUE
43 | bus_LV_4566-34_0_8_node_167 | 0.4 | n |  | TRUE
44 | bus_LV_4566-34_0_8_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_4566-34_0_8_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_4566-34_0_8_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_4566-34_0_8_node_222 | 0.4 | n |  | TRUE
48 | bus_LV_4566-34_0_8_node_221 | 0.4 | n |  | TRUE
49 | bus_LV_4566-34_0_8_node_223 | 0.4 | n |  | TRUE
50 | bus_LV_4566-34_0_8_node_225 | 0.4 | n |  | TRUE
51 | bus_LV_4566-34_0_8_node_227 | 0.4 | n |  | TRUE
52 | bus_LV_4566-34_0_8_node_226 | 0.4 | n |  | TRUE
53 | bus_LV_4566-34_0_8_node_248 | 0.4 | n |  | TRUE
54 | bus_LV_4566-34_0_8_node_245 | 0.4 | n |  | TRUE
55 | bus_LV_4566-34_0_8_node_243 | 0.4 | n |  | TRUE
56 | bus_LV_4566-34_0_8_node_252 | 0.4 | n |  | TRUE
57 | bus_LV_4566-34_0_8_node_241 | 0.4 | n |  | TRUE
58 | bus_LV_4566-34_0_8_node_246 | 0.4 | n |  | TRUE
59 | bus_LV_4566-34_0_8_node_247 | 0.4 | n |  | TRUE
60 | bus_LV_4566-34_0_8_node_258 | 0.4 | n |  | TRUE
61 | bus_LV_4566-34_0_8_node_265 | 0.4 | n |  | TRUE
62 | bus_LV_4566-34_0_8_node_90 | 0.4 | n |  | TRUE
63 | bus_LV_4566-34_0_8_node_93 | 0.4 | n |  | TRUE
64 | bus_LV_4566-34_0_8_node_88 | 0.4 | n |  | TRUE
65 | bus_LV_4566-34_0_8_node_34 | 0.4 | n |  | TRUE
66 | bus_LV_4566-34_0_8_node_35 | 0.4 | n |  | TRUE
67 | bus_LV_4566-34_0_8_node_36 | 0.4 | n |  | TRUE
68 | bus_LV_4566-34_0_8_node_37 | 0.4 | n |  | TRUE
69 | bus_LV_4566-34_0_8_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_4566-34_0_8_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_4566-34_0_8_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_4566-34_0_8_node_186 | 0.4 | n |  | TRUE
73 | bus_LV_4566-34_0_8_node_58 | 0.4 | n |  | TRUE
74 | bus_LV_4566-34_0_8_node_203 | 0.4 | n |  | TRUE
75 | bus_LV_4566-34_0_8_node_217 | 0.4 | n |  | TRUE
76 | bus_LV_4566-34_0_8_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_4566-34_0_8_node_139 | 0.4 | n |  | TRUE
78 | bus_LV_4566-34_0_8_node_77 | 0.4 | n |  | TRUE
79 | bus_LV_4566-34_0_8_node_175 | 0.4 | n |  | TRUE
80 | bus_LV_4566-34_0_8_node_54 | 0.4 | n |  | TRUE
81 | bus_LV_4566-34_0_8_node_38 | 0.4 | n |  | TRUE
82 | bus_LV_4566-34_0_8_node_39 | 0.4 | n |  | TRUE
83 | bus_LV_4566-34_0_8_node_40 | 0.4 | n |  | TRUE
84 | bus_LV_4566-34_0_8_node_41 | 0.4 | n |  | TRUE
85 | bus_LV_4566-34_0_8_node_42 | 0.4 | n |  | TRUE
86 | bus_LV_4566-34_0_8_node_43 | 0.4 | n |  | TRUE
87 | bus_LV_4566-34_0_8_node_121 | 0.4 | n |  | TRUE
88 | bus_LV_4566-34_0_8_node_177 | 0.4 | n |  | TRUE
89 | bus_LV_4566-34_0_8_node_172 | 0.4 | n |  | TRUE
90 | bus_LV_4566-34_0_8_node_123 | 0.4 | n |  | TRUE
91 | bus_LV_4566-34_0_8_node_201 | 0.4 | n |  | TRUE
92 | bus_LV_4566-34_0_8_node_171 | 0.4 | n |  | TRUE
93 | bus_LV_4566-34_0_8_node_44 | 0.4 | n |  | TRUE
94 | bus_LV_4566-34_0_8_node_45 | 0.4 | n |  | TRUE
95 | bus_LV_4566-34_0_8_node_46 | 0.4 | n |  | TRUE
96 | bus_LV_4566-34_0_8_node_47 | 0.4 | n |  | TRUE
97 | bus_LV_4566-34_0_8_node_48 | 0.4 | n |  | TRUE
98 | bus_LV_4566-34_0_8_node_49 | 0.4 | n |  | TRUE
99 | bus_LV_4566-34_0_8_node_103 | 0.4 | n |  | TRUE
100 | bus_LV_4566-34_0_8_node_50 | 0.4 | n |  | TRUE
101 | bus_LV_4566-34_0_8_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_4566-34_0_8_node_51 | 0.4 | n |  | TRUE
103 | bus_LV_4566-34_0_8_node_109 | 0.4 | n |  | TRUE
104 | bus_LV_4566-34_0_8_node_163 | 0.4 | n |  | TRUE
105 | bus_LV_4566-34_0_8_node_75 | 0.4 | n |  | TRUE
106 | bus_LV_4566-34_0_8_node_202 | 0.4 | n |  | TRUE
107 | bus_LV_4566-34_0_8_node_216 | 0.4 | n |  | TRUE
108 | bus_LV_4566-34_0_8_node_182 | 0.4 | n |  | TRUE
109 | bus_LV_4566-34_0_8_node_187 | 0.4 | n |  | TRUE
110 | bus_LV_4566-34_0_8_node_188 | 0.4 | n |  | TRUE
111 | bus_LV_4566-34_0_8_node_61 | 0.4 | n |  | TRUE
112 | bus_LV_4566-34_0_8_node_62 | 0.4 | n |  | TRUE
113 | bus_LV_4566-34_0_8_node_64 | 0.4 | n |  | TRUE
114 | bus_LV_4566-34_0_8_node_65 | 0.4 | n |  | TRUE
115 | bus_LV_4566-34_0_8_node_66 | 0.4 | n |  | TRUE
116 | bus_LV_4566-34_0_8_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_4566-34_0_8_node_85 | 0.4 | n |  | TRUE
118 | bus_LV_4566-34_0_8_node_82 | 0.4 | n |  | TRUE
119 | bus_LV_4566-34_0_8_node_159 | 0.4 | n |  | TRUE
120 | bus_LV_4566-34_0_8_node_178 | 0.4 | n |  | TRUE
121 | bus_LV_4566-34_0_8_node_126 | 0.4 | n |  | TRUE
122 | bus_LV_4566-34_0_8_node_68 | 0.4 | n |  | TRUE
123 | bus_LV_4566-34_0_8_node_69 | 0.4 | n |  | TRUE
124 | bus_LV_4566-34_0_8_node_71 | 0.4 | n |  | TRUE
125 | bus_LV_4566-34_0_8_node_73 | 0.4 | n |  | TRUE
126 | bus_LV_4566-34_0_8_node_142 | 0.4 | n |  | TRUE
127 | bus_LV_4566-34_0_8_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_4566-34_0_8_node_74 | 0.4 | n |  | TRUE
129 | bus_LV_4566-34_0_8_node_76 | 0.4 | n |  | TRUE
130 | bus_LV_4566-34_0_8_node_78 | 0.4 | n |  | TRUE
131 | bus_LV_4566-34_0_8_node_158 | 0.4 | n |  | TRUE
132 | bus_LV_4566-34_0_8_node_156 | 0.4 | n |  | TRUE
133 | bus_LV_4566-34_0_8_node_79 | 0.4 | n |  | TRUE
134 | bus_LV_4566-34_0_8_node_120 | 0.4 | n |  | TRUE
135 | bus_LV_4566-34_0_8_node_147 | 0.4 | n |  | TRUE
136 | bus_LV_4566-34_0_8_node_173 | 0.4 | n |  | TRUE
137 | bus_LV_4566-34_0_8_node_154 | 0.4 | n |  | TRUE
138 | bus_LV_4566-34_0_8_node_152 | 0.4 | n |  | TRUE
139 | bus_LV_4566-34_0_8_node_157 | 0.4 | n |  | TRUE
140 | bus_LV_4566-34_0_8_node_122 | 0.4 | n |  | TRUE
141 | bus_LV_4566-34_0_8_node_119 | 0.4 | n |  | TRUE
142 | bus_LV_4566-34_0_8_node_145 | 0.4 | n |  | TRUE
143 | bus_LV_4566-34_0_8_node_80 | 0.4 | n |  | TRUE
144 | bus_LV_4566-34_0_8_node_81 | 0.4 | n |  | TRUE
145 | bus_LV_4566-34_0_8_node_83 | 0.4 | n |  | TRUE
146 | bus_LV_4566-34_0_8_node_84 | 0.4 | n |  | TRUE
147 | bus_LV_4566-34_0_8_node_86 | 0.4 | n |  | TRUE
148 | bus_LV_4566-34_0_8_node_124 | 0.4 | n |  | TRUE
149 | bus_LV_4566-34_0_8_node_111 | 0.4 | n |  | TRUE
150 | bus_LV_4566-34_0_8_node_153 | 0.4 | n |  | TRUE
151 | bus_LV_4566-34_0_8_node_125 | 0.4 | n |  | TRUE
152 | bus_LV_4566-34_0_8_node_112 | 0.4 | n |  | TRUE
153 | bus_LV_4566-34_0_8_node_151 | 0.4 | n |  | TRUE
154 | bus_LV_4566-34_0_8_node_91 | 0.4 | n |  | TRUE
155 | bus_LV_4566-34_0_8_node_215 | 0.4 | n |  | TRUE
156 | bus_LV_4566-34_0_8_node_214 | 0.4 | n |  | TRUE
157 | bus_LV_4566-34_0_8_node_116 | 0.4 | n |  | TRUE
158 | bus_LV_4566-34_0_8_node_113 | 0.4 | n |  | TRUE
159 | bus_LV_4566-34_0_8_node_166 | 0.4 | n |  | TRUE
160 | bus_LV_4566-34_0_8_node_96 | 0.4 | n |  | TRUE
161 | bus_LV_4566-34_0_8_node_97 | 0.4 | n |  | TRUE
162 | bus_LV_4566-34_0_8_node_98 | 0.4 | n |  | TRUE
163 | bus_LV_4566-34_0_8_node_99 | 0.4 | n |  | TRUE
164 | bus_LV_4566-34_0_8_node_100 | 0.4 | n |  | TRUE
165 | bus_LV_4566-34_0_8_node_134 | 0.4 | n |  | TRUE
166 | bus_LV_4566-34_0_8_node_133 | 0.4 | n |  | TRUE
167 | bus_LV_4566-34_0_8_node_104 | 0.4 | n |  | TRUE
168 | bus_LV_4566-34_0_8_node_105 | 0.4 | n |  | TRUE
169 | bus_LV_4566-34_0_8_node_106 | 0.4 | n |  | TRUE
170 | bus_LV_4566-34_0_8_node_107 | 0.4 | n |  | TRUE
171 | bus_LV_4566-34_0_8_node_132 | 0.4 | n |  | TRUE
172 | bus_LV_4566-34_0_8_node_115 | 0.4 | n |  | TRUE
173 | bus_LV_4566-34_0_8_node_117 | 0.4 | n |  | TRUE
174 | bus_LV_4566-34_0_8_node_118 | 0.4 | n |  | TRUE
175 | bus_LV_4566-34_0_8_node_136 | 0.4 | n |  | TRUE
176 | bus_LV_4566-34_0_8_node_137 | 0.4 | n |  | TRUE
177 | bus_LV_4566-34_0_8_node_181 | 0.4 | n |  | TRUE
178 | bus_LV_4566-34_0_8_node_183 | 0.4 | n |  | TRUE
179 | bus_LV_4566-34_0_8_node_184 | 0.4 | n |  | TRUE
180 | bus_LV_4566-34_0_8_node_199 | 0.4 | n |  | TRUE
181 | bus_LV_4566-34_0_8_node_127 | 0.4 | n |  | TRUE
182 | bus_LV_4566-34_0_8_node_128 | 0.4 | n |  | TRUE
183 | bus_LV_4566-34_0_8_node_129 | 0.4 | n |  | TRUE
184 | bus_LV_4566-34_0_8_node_130 | 0.4 | n |  | TRUE
185 | bus_LV_4566-34_0_8_node_131 | 0.4 | n |  | TRUE
186 | bus_LV_4566-34_0_8_node_164 | 0.4 | n |  | TRUE
187 | bus_LV_4566-34_0_8_node_176 | 0.4 | n |  | TRUE
188 | bus_LV_4566-34_0_8_node_162 | 0.4 | n |  | TRUE
189 | bus_LV_4566-34_0_8_node_179 | 0.4 | n |  | TRUE
190 | bus_LV_4566-34_0_8_node_138 | 0.4 | n |  | TRUE
191 | bus_LV_4566-34_0_8_node_140 | 0.4 | n |  | TRUE
192 | bus_LV_4566-34_0_8_node_141 | 0.4 | n |  | TRUE
193 | bus_LV_4566-34_0_8_node_161 | 0.4 | n |  | TRUE
194 | bus_LV_4566-34_0_8_node_148 | 0.4 | n |  | TRUE
195 | bus_LV_4566-34_0_8_node_149 | 0.4 | n |  | TRUE
196 | bus_LV_4566-34_0_8_node_143 | 0.4 | n |  | TRUE
197 | bus_LV_4566-34_0_8_node_144 | 0.4 | n |  | TRUE
198 | bus_LV_4566-34_0_8_node_146 | 0.4 | n |  | TRUE
199 | bus_LV_4566-34_0_8_node_170 | 0.4 | n |  | TRUE
200 | bus_LV_4566-34_0_8_node_155 | 0.4 | n |  | TRUE
201 | bus_LV_4566-34_0_8_node_150 | 0.4 | n |  | TRUE
202 | bus_LV_4566-34_0_8_node_160 | 0.4 | n |  | TRUE
203 | bus_LV_4566-34_0_8_node_208 | 0.4 | n |  | TRUE
204 | bus_LV_4566-34_0_8_node_212 | 0.4 | n |  | TRUE
205 | bus_LV_4566-34_0_8_node_207 | 0.4 | n |  | TRUE
206 | bus_LV_4566-34_0_8_node_213 | 0.4 | n |  | TRUE
207 | bus_LV_4566-34_0_8_node_189 | 0.4 | n |  | TRUE
208 | bus_LV_4566-34_0_8_node_190 | 0.4 | n |  | TRUE
209 | bus_LV_4566-34_0_8_node_240 | 0.4 | n |  | TRUE
210 | bus_LV_4566-34_0_8_node_191 | 0.4 | n |  | TRUE
211 | bus_LV_4566-34_0_8_node_228 | 0.4 | n |  | TRUE
212 | bus_LV_4566-34_0_8_node_229 | 0.4 | n |  | TRUE
213 | bus_LV_4566-34_0_8_node_230 | 0.4 | n |  | TRUE
214 | bus_LV_4566-34_0_8_node_231 | 0.4 | n |  | TRUE
215 | bus_LV_4566-34_0_8_node_232 | 0.4 | n |  | TRUE
216 | bus_LV_4566-34_0_8_node_249 | 0.4 | n |  | TRUE
217 | bus_LV_4566-34_0_8_node_250 | 0.4 | n |  | TRUE
218 | bus_LV_4566-34_0_8_node_251 | 0.4 | n |  | TRUE
219 | bus_LV_4566-34_0_8_node_256 | 0.4 | n |  | TRUE
220 | bus_LV_4566-34_0_8_node_233 | 0.4 | n |  | TRUE
221 | bus_LV_4566-34_0_8_node_234 | 0.4 | n |  | TRUE
222 | bus_LV_4566-34_0_8_node_235 | 0.4 | n |  | TRUE
223 | bus_LV_4566-34_0_8_node_236 | 0.4 | n |  | TRUE
224 | bus_LV_4566-34_0_8_node_237 | 0.4 | n |  | TRUE
225 | bus_LV_4566-34_0_8_node_238 | 0.4 | n |  | TRUE
226 | bus_LV_4566-34_0_8_node_262 | 0.4 | n |  | TRUE
227 | bus_LV_4566-34_0_8_node_269 | 0.4 | n |  | TRUE
228 | bus_LV_4566-34_0_8_node_264 | 0.4 | n |  | TRUE
229 | bus_LV_4566-34_0_8_node_239 | 0.4 | n |  | TRUE
230 | bus_LV_4566-34_0_8_node_242 | 0.4 | n |  | TRUE
231 | bus_LV_4566-34_0_8_node_259 | 0.4 | n |  | TRUE
232 | bus_LV_4566-34_0_8_node_261 | 0.4 | n |  | TRUE
233 | bus_LV_4566-34_0_8_node_253 | 0.4 | n |  | TRUE
234 | bus_LV_4566-34_0_8_node_254 | 0.4 | n |  | TRUE
235 | bus_LV_4566-34_0_8_node_260 | 0.4 | n |  | TRUE
236 | bus_LV_4566-34_0_8_node_263 | 0.4 | n |  | TRUE
237 | bus_LV_4566-34_0_8_node_211 | 0.4 | n |  | TRUE
238 | bus_LV_4566-34_0_8_node_195 | 0.4 | n |  | TRUE
239 | bus_LV_4566-34_0_8_node_192 | 0.4 | n |  | TRUE
240 | bus_LV_4566-34_0_8_node_193 | 0.4 | n |  | TRUE
241 | bus_LV_4566-34_0_8_node_194 | 0.4 | n |  | TRUE
242 | bus_LV_4566-34_0_8_node_196 | 0.4 | n |  | TRUE
243 | bus_LV_4566-34_0_8_node_209 | 0.4 | n |  | TRUE
244 | bus_LV_4566-34_0_8_node_210 | 0.4 | n |  | TRUE
245 | bus_LV_4566-34_0_8_node_206 | 0.4 | n |  | TRUE
246 | bus_LV_4566-34_0_8_node_200 | 0.4 | n |  | TRUE
247 | bus_LV_4566-34_0_8_node_268 | 0.4 | n |  | TRUE
248 | bus_LV_4566-34_0_8_node_197 | 0.4 | n |  | TRUE
249 | bus_LV_4566-34_0_8_node_198 | 0.4 | n |  | TRUE
250 | bus_LV_4566-34_0_8_node_204 | 0.4 | n |  | TRUE
251 | bus_LV_4566-34_0_8_node_205 | 0.4 | n |  | TRUE
252 | bus_LV_4566-34_0_8_node_218 | 0.4 | n |  | TRUE
253 | bus_LV_4566-34_0_8_node_219 | 0.4 | n |  | TRUE
254 | bus_LV_4566-34_0_8_node_267 | 0.4 | n |  | TRUE
255 | bus_LV_4566-34_0_8_node_266 | 0.4 | n |  | TRUE
256 | bus_MV_374_1_node_72 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4566-34_0_8_load_0 | 0 | 0.0012468 | 0.00031248 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4566-34_0_8_load_1 | 1 | 0.0012749 | 0.00031951 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4566-34_0_8_load_2 | 2 | 0.0014552 | 0.00036471 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4566-34_0_8_load_3 | 3 | 0.0011503 | 0.00028829 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4566-34_0_8_load_21 | 4 | 0.0017959 | 0.0004501 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4566-34_0_8_load_19 | 5 | 0.015705 | 0.0039361 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4566-34_0_8_load_4 | 6 | 0.0015462 | 0.00038752 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4566-34_0_8_load_5 | 7 | 0.0011962 | 0.00029979 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4566-34_0_8_load_6 | 8 | 0.0028049 | 0.00070299 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4566-34_0_8_load_7 | 9 | 0.0027266 | 0.00068335 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4566-34_0_8_load_8 | 10 | 0.0013252 | 0.00033212 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4566-34_0_8_load_9 | 13 | 0.00066691 | 0.00016714 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4566-34_0_8_load_10 | 14 | 0.011331 | 0.0028399 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4566-34_0_8_load_12 | 16 | 0.027331 | 0.0068497 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4566-34_0_8_load_13 | 17 | 0.0031523 | 0.00079005 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4566-34_0_8_load_95 | 21 | 0.0035029 | 0.0008779 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4566-34_0_8_load_270 | 22 | 0.0033469 | 0.00083882 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4566-34_0_8_load_165 | 24 | 0.0040934 | 0.0010259 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4566-34_0_8_load_174 | 25 | 0.0024186 | 0.00060615 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4566-34_0_8_load_180 | 26 | 0.014834 | 0.0037177 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4566-34_0_8_load_55 | 27 | 0.0032982 | 0.00082662 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4566-34_0_8_load_135 | 28 | 0.0024912 | 0.00062434 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4566-34_0_8_load_18 | 31 | 0.0019493 | 0.00048853 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4566-34_0_8_load_185 | 32 | 0.012421 | 0.0031131 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4566-34_0_8_load_92 | 34 | 0.0016522 | 0.00041409 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4566-34_0_8_load_24 | 35 | 0.0025335 | 0.00063496 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4566-34_0_8_load_25 | 36 | 0.0010432 | 0.00026145 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4566-34_0_8_load_26 | 37 | 0.0014806 | 0.00037108 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4566-34_0_8_load_27 | 38 | 0.0012535 | 0.00031417 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4566-34_0_8_load_52 | 39 | 0.0030397 | 0.00076181 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4566-34_0_8_load_110 | 40 | 0.0034882 | 0.00087423 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4566-34_0_8_load_167 | 43 | 0.0029679 | 0.00074382 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4566-34_0_8_load_29 | 44 | 0.021115 | 0.0052919 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4566-34_0_8_load_222 | 47 | 0.0039498 | 0.00098991 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4566-34_0_8_load_221 | 48 | 0.0016663 | 0.00041762 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4566-34_0_8_load_223 | 49 | 0.0014066 | 0.00035254 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4566-34_0_8_load_227 | 51 | 0.00043902 | 0.00011003 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4566-34_0_8_load_245 | 54 | 0.00041656 | 0.0001044 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4566-34_0_8_load_243 | 55 | 0.0010052 | 0.00025192 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4566-34_0_8_load_252 | 56 | 0.00070472 | 0.00017662 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4566-34_0_8_load_246 | 58 | 0.00035651 | 8.9351e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4566-34_0_8_load_247 | 59 | 0.00037429 | 9.3806e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4566-34_0_8_load_258 | 60 | 8.932e-05 | 2.2386e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4566-34_0_8_load_265 | 61 | 0.00025873 | 6.4844e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4566-34_0_8_load_88 | 64 | 0.0013981 | 0.00035039 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4566-34_0_8_load_34 | 65 | 0.0035463 | 0.00088879 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4566-34_0_8_load_35 | 66 | 0.012014 | 0.003011 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4566-34_0_8_load_36 | 67 | 0.019475 | 0.0048808 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4566-34_0_8_load_60 | 69 | 0.010647 | 0.0026683 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4566-34_0_8_load_53 | 70 | 0.003673 | 0.00092055 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4566-34_0_8_load_186 | 72 | 0.0022991 | 0.00057621 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4566-34_0_8_load_203 | 74 | 0.0012693 | 0.00031811 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4566-34_0_8_load_217 | 75 | 0.0016714 | 0.0004189 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4566-34_0_8_load_77 | 78 | 0.0017322 | 0.00043413 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4566-34_0_8_load_175 | 79 | 0.0020892 | 0.0005236 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4566-34_0_8_load_38 | 81 | 0.0015222 | 0.0003815 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4566-34_0_8_load_39 | 82 | 0.0022817 | 0.00057185 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4566-34_0_8_load_41 | 84 | 0.0020645 | 0.0005174 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4566-34_0_8_load_43 | 86 | 0.001656 | 0.00041503 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4566-34_0_8_load_177 | 88 | 0.0037459 | 0.00093881 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4566-34_0_8_load_172 | 89 | 0.003321 | 0.00083232 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4566-34_0_8_load_201 | 91 | 0.0025249 | 0.0006328 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4566-34_0_8_load_171 | 92 | 0.0027251 | 0.00068298 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4566-34_0_8_load_44 | 93 | 0.0031337 | 0.00078538 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4566-34_0_8_load_45 | 94 | 0.0024411 | 0.00061179 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4566-34_0_8_load_46 | 95 | 0.0027677 | 0.00069366 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4566-34_0_8_load_47 | 96 | 0.0024367 | 0.0006107 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4566-34_0_8_load_48 | 97 | 0.0031331 | 0.00078523 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4566-34_0_8_load_49 | 98 | 0.0025674 | 0.00064344 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4566-34_0_8_load_103 | 99 | 0.0021023 | 0.00052688 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4566-34_0_8_load_50 | 100 | 0.0035456 | 0.0008886 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4566-34_0_8_load_102 | 101 | 0.003329 | 0.00083432 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4566-34_0_8_load_51 | 102 | 0.0030699 | 0.00076939 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4566-34_0_8_load_109 | 103 | 0.0026199 | 0.00065661 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4566-34_0_8_load_163 | 104 | 0.0020267 | 0.00050794 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4566-34_0_8_load_75 | 105 | 0.0025182 | 0.00063113 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4566-34_0_8_load_202 | 106 | 0.0059319 | 0.0014867 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4566-34_0_8_load_216 | 107 | 0.0042824 | 0.0010733 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4566-34_0_8_load_188 | 110 | 0.0028755 | 0.00072066 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4566-34_0_8_load_61 | 111 | 0.004699 | 0.0011777 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4566-34_0_8_load_64 | 113 | 0.0028 | 0.00070174 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4566-34_0_8_load_65 | 114 | 0.003244 | 0.00081301 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4566-34_0_8_load_66 | 115 | 0.0034602 | 0.0008672 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4566-34_0_8_load_101 | 116 | 0.0032423 | 0.00081259 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4566-34_0_8_load_85 | 117 | 0.0032829 | 0.00082276 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4566-34_0_8_load_178 | 120 | 0.0025847 | 0.00064779 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4566-34_0_8_load_126 | 121 | 0.003153 | 0.00079023 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4566-34_0_8_load_68 | 122 | 0.0022258 | 0.00055785 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4566-34_0_8_load_69 | 123 | 0.002009 | 0.0005035 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4566-34_0_8_load_142 | 126 | 0.0022928 | 0.00057462 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4566-34_0_8_load_108 | 127 | 0.0020096 | 0.00050365 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4566-34_0_8_load_74 | 128 | 0.0038655 | 0.00096878 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4566-34_0_8_load_158 | 131 | 0.0039151 | 0.00098123 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4566-34_0_8_load_156 | 132 | 0.004515 | 0.0011316 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4566-34_0_8_load_147 | 135 | 0.0017507 | 0.00043876 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4566-34_0_8_load_154 | 137 | 0.0031599 | 0.00079195 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4566-34_0_8_load_157 | 139 | 0.0049738 | 0.0012465 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4566-34_0_8_load_122 | 140 | 0.002483 | 0.00062229 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4566-34_0_8_load_119 | 141 | 0.0019495 | 0.0004886 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4566-34_0_8_load_145 | 142 | 0.0013564 | 0.00033996 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4566-34_0_8_load_80 | 143 | 0.0032825 | 0.00082267 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4566-34_0_8_load_81 | 144 | 0.0031554 | 0.00079082 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4566-34_0_8_load_83 | 145 | 0.0032818 | 0.0008225 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4566-34_0_8_load_84 | 146 | 0.0036041 | 0.00090327 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4566-34_0_8_load_86 | 147 | 0.0031525 | 0.00079009 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4566-34_0_8_load_124 | 148 | 0.0031546 | 0.00079061 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4566-34_0_8_load_111 | 149 | 0.0037351 | 0.00093611 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4566-34_0_8_load_153 | 150 | 0.0035867 | 0.00089891 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4566-34_0_8_load_125 | 151 | 0.0032829 | 0.00082276 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4566-34_0_8_load_112 | 152 | 0.002988 | 0.00074886 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4566-34_0_8_load_151 | 153 | 0.0034377 | 0.00086157 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4566-34_0_8_load_91 | 154 | 0.0017932 | 0.00044943 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4566-34_0_8_load_215 | 155 | 0.0027731 | 0.00069499 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4566-34_0_8_load_214 | 156 | 0.001922 | 0.00048171 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4566-34_0_8_load_116 | 157 | 0.00076419 | 0.00019152 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4566-34_0_8_load_113 | 158 | 0.0020177 | 0.00050568 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4566-34_0_8_load_166 | 159 | 0.0017548 | 0.00043979 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4566-34_0_8_load_96 | 160 | 0.0022857 | 0.00057285 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4566-34_0_8_load_97 | 161 | 0.0031087 | 0.00077913 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4566-34_0_8_load_98 | 162 | 0.0039202 | 0.0009825 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4566-34_0_8_load_99 | 163 | 0.0032316 | 0.00080991 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4566-34_0_8_load_100 | 164 | 0.0022728 | 0.00056962 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4566-34_0_8_load_134 | 165 | 0.0032114 | 0.00080484 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4566-34_0_8_load_133 | 166 | 0.0027656 | 0.00069313 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4566-34_0_8_load_104 | 167 | 0.0022927 | 0.00057461 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4566-34_0_8_load_105 | 168 | 0.0020103 | 0.00050382 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4566-34_0_8_load_106 | 169 | 0.0034963 | 0.00087626 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4566-34_0_8_load_107 | 170 | 0.0069245 | 0.0017354 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4566-34_0_8_load_132 | 171 | 0.0027947 | 0.00070042 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4566-34_0_8_load_117 | 173 | 0.0014799 | 0.00037091 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4566-34_0_8_load_118 | 174 | 0.0013022 | 0.00032635 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4566-34_0_8_load_136 | 175 | 0.0013237 | 0.00033176 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4566-34_0_8_load_137 | 176 | 0.0012845 | 0.00032193 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4566-34_0_8_load_183 | 178 | 0.0021362 | 0.00053538 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4566-34_0_8_load_184 | 179 | 0.0021324 | 0.00053442 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4566-34_0_8_load_199 | 180 | 0.00074625 | 0.00018703 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4566-34_0_8_load_127 | 181 | 0.0021113 | 0.00052914 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4566-34_0_8_load_128 | 182 | 0.0035638 | 0.00089317 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4566-34_0_8_load_129 | 183 | 0.0044978 | 0.0011273 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_4566-34_0_8_load_130 | 184 | 0.0019424 | 0.00048682 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_4566-34_0_8_load_131 | 185 | 0.0017976 | 0.00045053 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_4566-34_0_8_load_164 | 186 | 0.0020503 | 0.00051385 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_4566-34_0_8_load_176 | 187 | 0.0019293 | 0.00048353 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_4566-34_0_8_load_162 | 188 | 0.0021467 | 0.000538 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_4566-34_0_8_load_179 | 189 | 0.0022068 | 0.00055306 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_4566-34_0_8_load_138 | 190 | 0.0038635 | 0.00096827 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_4566-34_0_8_load_140 | 191 | 0.0024049 | 0.00060272 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_4566-34_0_8_load_141 | 192 | 0.0051125 | 0.0012813 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_4566-34_0_8_load_161 | 193 | 0.0019658 | 0.00049269 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_4566-34_0_8_load_148 | 194 | 0.0029095 | 0.00072919 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_4566-34_0_8_load_149 | 195 | 0.0030104 | 0.00075448 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_4566-34_0_8_load_143 | 196 | 0.0024476 | 0.00061343 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_4566-34_0_8_load_144 | 197 | 0.0034876 | 0.00087408 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_4566-34_0_8_load_146 | 198 | 0.0044132 | 0.0011061 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_4566-34_0_8_load_170 | 199 | 0.0027451 | 0.00068798 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_4566-34_0_8_load_155 | 200 | 0.0046711 | 0.0011707 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_4566-34_0_8_load_150 | 201 | 0.0026494 | 0.00066401 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_4566-34_0_8_load_160 | 202 | 0.0035638 | 0.00089318 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_4566-34_0_8_load_208 | 203 | 0.00116 | 0.00029073 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_4566-34_0_8_load_212 | 204 | 0.0028951 | 0.00072558 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_4566-34_0_8_load_207 | 205 | 0.00095422 | 0.00023915 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_4566-34_0_8_load_213 | 206 | 0.0044245 | 0.0011089 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_4566-34_0_8_load_189 | 207 | 0.00095384 | 0.00023906 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_4566-34_0_8_load_190 | 208 | 0.00098357 | 0.00024651 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_4566-34_0_8_load_191 | 210 | 0.00095477 | 0.00023929 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_4566-34_0_8_load_228 | 211 | 0.0012093 | 0.00030308 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_4566-34_0_8_load_229 | 212 | 0.00035871 | 8.9901e-05 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_4566-34_0_8_load_230 | 213 | 0.0021375 | 0.0005357 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_4566-34_0_8_load_232 | 215 | 0.0013833 | 0.0003467 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_4566-34_0_8_load_249 | 216 | 0.0010955 | 0.00027456 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_4566-34_0_8_load_250 | 217 | 0.0010119 | 0.00025359 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_4566-34_0_8_load_251 | 218 | 0.00021054 | 5.2766e-05 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_4566-34_0_8_load_256 | 219 | 0.0031816 | 0.00079738 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_4566-34_0_8_load_233 | 220 | 0.0015063 | 0.00037751 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_4566-34_0_8_load_234 | 221 | 0.0013693 | 0.00034317 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_4566-34_0_8_load_237 | 224 | 0.00037726 | 9.4549e-05 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_4566-34_0_8_load_238 | 225 | 0.0006594 | 0.00016526 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_4566-34_0_8_load_262 | 226 | 0.0038224 | 0.00095799 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_4566-34_0_8_load_269 | 227 | 0.0011469 | 0.00028745 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_4566-34_0_8_load_264 | 228 | 0.00052506 | 0.00013159 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_4566-34_0_8_load_239 | 229 | 0.00068216 | 0.00017097 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_4566-34_0_8_load_259 | 231 | 0.0010056 | 0.00025202 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_4566-34_0_8_load_261 | 232 | 0.0018547 | 0.00046484 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_4566-34_0_8_load_253 | 233 | 0.00038057 | 9.5379e-05 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_4566-34_0_8_load_254 | 234 | 0.00052245 | 0.00013094 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_4566-34_0_8_load_260 | 235 | 0.0030182 | 0.00075642 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_4566-34_0_8_load_263 | 236 | 0.00037574 | 9.4169e-05 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_4566-34_0_8_load_211 | 237 | 0.0009846 | 0.00024676 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_4566-34_0_8_load_195 | 238 | 0.00059972 | 0.0001503 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_4566-34_0_8_load_192 | 239 | 0.00095401 | 0.0002391 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_4566-34_0_8_load_193 | 240 | 0.00060851 | 0.00015251 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_4566-34_0_8_load_194 | 241 | 0.0005789 | 0.00014509 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_4566-34_0_8_load_209 | 243 | 0.00095383 | 0.00023905 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_4566-34_0_8_load_210 | 244 | 0.00098385 | 0.00024658 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_4566-34_0_8_load_206 | 245 | 0.00095401 | 0.0002391 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_4566-34_0_8_load_200 | 246 | 0.0011648 | 0.00029193 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_4566-34_0_8_load_268 | 247 | 0.0009841 | 0.00024664 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_4566-34_0_8_load_197 | 248 | 0.0011648 | 0.00029193 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_4566-34_0_8_load_198 | 249 | 0.0020849 | 0.00052253 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_4566-34_0_8_load_204 | 250 | 0.0014725 | 0.00036904 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_4566-34_0_8_load_205 | 251 | 0.0013729 | 0.00034408 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_4566-34_0_8_load_218 | 252 | 0.0015699 | 0.00039347 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_4566-34_0_8_load_219 | 253 | 0.0045766 | 0.001147 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_4566-34_0_8_load_267 | 254 | 0.0011397 | 0.00028563 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_4566-34_0_8_load_266 | 255 | 0.0013934 | 0.00034921 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 105 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4566-34_0_8_line_0 |  | 0 | 1 | 0.0016652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4566-34_0_8_line_1 |  | 0 | 2 | 0.0077667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4566-34_0_8_line_2 |  | 2 | 3 | 0.0090015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4566-34_0_8_line_3 |  | 3 | 4 | 0.0030946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4566-34_0_8_line_4 |  | 4 | 5 | 0.016288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4566-34_0_8_line_5 |  | 5 | 31 | 0.0071018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4566-34_0_8_line_6 |  | 6 | 7 | 0.01598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4566-34_0_8_line_7 |  | 6 | 8 | 0.011255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4566-34_0_8_line_8 |  | 7 | 9 | 0.022097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4566-34_0_8_line_9 |  | 8 | 10 | 0.007378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4566-34_0_8_line_10 |  | 9 | 11 | 0.020073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4566-34_0_8_line_11 |  | 11 | 12 | 0.027038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4566-34_0_8_line_12 |  | 12 | 30 | 0.045612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4566-34_0_8_line_13 |  | 12 | 31 | 0.013331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4566-34_0_8_line_14 |  | 12 | 19 | 0.040843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4566-34_0_8_line_15 |  | 13 | 14 | 0.014903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4566-34_0_8_line_16 |  | 13 | 15 | 0.01459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4566-34_0_8_line_17 |  | 14 | 16 | 0.027271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4566-34_0_8_line_18 |  | 15 | 17 | 0.03596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4566-34_0_8_line_19 |  | 15 | 18 | 0.024425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4566-34_0_8_line_20 |  | 16 | 19 | 0.04044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4566-34_0_8_line_21 |  | 18 | 20 | 0.029096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4566-34_0_8_line_22 |  | 18 | 21 | 0.03571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_4566-34_0_8_line_23 |  | 19 | 26 | 0.062426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4566-34_0_8_line_24 |  | 20 | 22 | 0.0064316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4566-34_0_8_line_25 |  | 21 | 27 | 0.0093356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_4566-34_0_8_line_26 |  | 23 | 24 | 0.014224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4566-34_0_8_line_27 |  | 23 | 25 | 0.022271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4566-34_0_8_line_28 |  | 24 | 28 | 0.005719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4566-34_0_8_line_29 |  | 25 | 29 | 0.011282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4566-34_0_8_line_30 |  | 26 | 34 | 0.01838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4566-34_0_8_line_31 |  | 27 | 80 | 0.025378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_4566-34_0_8_line_32 |  | 28 | 170 | 0.0085535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4566-34_0_8_line_33 |  | 29 | 79 | 0.018568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_4566-34_0_8_line_34 |  | 29 | 80 | 0.01699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_4566-34_0_8_line_35 |  | 30 | 32 | 0.036648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4566-34_0_8_line_36 |  | 32 | 33 | 0.038605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4566-34_0_8_line_37 |  | 33 | 45 | 0.041254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4566-34_0_8_line_38 |  | 34 | 62 | 0.023661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4566-34_0_8_line_39 |  | 35 | 36 | 0.00016037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4566-34_0_8_line_40 |  | 35 | 37 | 0.017771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4566-34_0_8_line_41 |  | 36 | 38 | 0.018776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4566-34_0_8_line_42 |  | 38 | 39 | 0.00031039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4566-34_0_8_line_43 |  | 39 | 40 | 0.016707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4566-34_0_8_line_44 |  | 40 | 103 | 0.0040534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4566-34_0_8_line_45 |  | 41 | 42 | 0.027073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4566-34_0_8_line_46 |  | 41 | 43 | 0.034413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4566-34_0_8_line_47 |  | 42 | 157 | 0.0049217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4566-34_0_8_line_48 |  | 42 | 158 | 0.020462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4566-34_0_8_line_49 |  | 43 | 159 | 0.028079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4566-34_0_8_line_50 |  | 44 | 45 | 0.020253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4566-34_0_8_line_51 |  | 46 | 47 | 0.008454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4566-34_0_8_line_52 |  | 46 | 48 | 0.040205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4566-34_0_8_line_53 |  | 48 | 63 | 0.024925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4566-34_0_8_line_54 |  | 49 | 50 | 0.015458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4566-34_0_8_line_55 |  | 50 | 51 | 0.010427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4566-34_0_8_line_56 |  | 51 | 53 | 0.058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4566-34_0_8_line_57 |  | 52 | 53 | 0.012235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4566-34_0_8_line_58 |  | 52 | 54 | 0.015487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4566-34_0_8_line_59 |  | 53 | 60 | 0.0089582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4566-34_0_8_line_60 |  | 54 | 58 | 0.028676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4566-34_0_8_line_61 |  | 55 | 56 | 0.0030705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4566-34_0_8_line_62 |  | 55 | 57 | 0.026059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4566-34_0_8_line_63 |  | 57 | 229 | 0.022202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4566-34_0_8_line_64 |  | 58 | 59 | 0.02126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4566-34_0_8_line_65 |  | 59 | 227 | 0.0053995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4566-34_0_8_line_66 |  | 60 | 61 | 0.021018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4566-34_0_8_line_67 |  | 62 | 63 | 0.059986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4566-34_0_8_line_68 |  | 62 | 64 | 0.013901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4566-34_0_8_line_69 |  | 65 | 66 | 0.013424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4566-34_0_8_line_70 |  | 65 | 67 | 0.0093472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4566-34_0_8_line_71 |  | 66 | 68 | 0.032368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4566-34_0_8_line_72 |  | 68 | 69 | 0.014917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4566-34_0_8_line_73 |  | 68 | 70 | 0.045886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4566-34_0_8_line_74 |  | 69 | 71 | 0.016008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4566-34_0_8_line_75 |  | 70 | 80 | 0.016605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4566-34_0_8_line_76 |  | 71 | 72 | 0.0034827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4566-34_0_8_line_77 |  | 71 | 73 | 0.003156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4566-34_0_8_line_78 |  | 73 | 74 | 0.019853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4566-34_0_8_line_79 |  | 73 | 75 | 0.016863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4566-34_0_8_line_80 |  | 74 | 106 | 0.0043952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4566-34_0_8_line_81 |  | 75 | 107 | 0.023736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4566-34_0_8_line_82 |  | 76 | 77 | 0.004284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_4566-34_0_8_line_83 |  | 76 | 78 | 0.010727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_4566-34_0_8_line_84 |  | 77 | 104 | 0.016989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_4566-34_0_8_line_85 |  | 77 | 79 | 0.014891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_4566-34_0_8_line_86 |  | 78 | 105 | 0.023204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_4566-34_0_8_line_87 |  | 81 | 82 | 0.024897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4566-34_0_8_line_88 |  | 81 | 83 | 0.01015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4566-34_0_8_line_89 |  | 82 | 84 | 0.018631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4566-34_0_8_line_90 |  | 83 | 85 | 0.003113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4566-34_0_8_line_91 |  | 83 | 86 | 0.0125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4566-34_0_8_line_92 |  | 85 | 87 | 0.011384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4566-34_0_8_line_93 |  | 85 | 88 | 0.011399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4566-34_0_8_line_94 |  | 86 | 89 | 0.025709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4566-34_0_8_line_95 |  | 87 | 90 | 0.007372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4566-34_0_8_line_96 |  | 89 | 92 | 0.029429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4566-34_0_8_line_97 |  | 90 | 91 | 0.014388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4566-34_0_8_line_98 |  | 91 | 180 | 0.017093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4566-34_0_8_line_99 |  | 92 | 136 | 0.018748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4566-34_0_8_line_100 |  | 93 | 94 | 0.017695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4566-34_0_8_line_101 |  | 93 | 95 | 0.0040996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4566-34_0_8_line_102 |  | 94 | 96 | 0.0014996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4566-34_0_8_line_103 |  | 95 | 97 | 0.014471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4566-34_0_8_line_104 |  | 96 | 98 | 0.016838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4566-34_0_8_line_105 |  | 97 | 99 | 0.0022298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4566-34_0_8_line_106 |  | 98 | 100 | 0.0032693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4566-34_0_8_line_107 |  | 99 | 101 | 0.024921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4566-34_0_8_line_108 |  | 100 | 102 | 0.015671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4566-34_0_8_line_109 |  | 101 | 116 | 0.00026638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4566-34_0_8_line_110 |  | 103 | 163 | 0.015229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4566-34_0_8_line_111 |  | 104 | 193 | 0.0061682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_4566-34_0_8_line_112 |  | 105 | 128 | 0.024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_4566-34_0_8_line_113 |  | 106 | 250 | 0.0015844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4566-34_0_8_line_114 |  | 107 | 109 | 0.0024092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4566-34_0_8_line_115 |  | 108 | 109 | 0.003617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4566-34_0_8_line_116 |  | 108 | 110 | 0.015354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4566-34_0_8_line_117 |  | 109 | 198 | 0.019901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4566-34_0_8_line_118 |  | 110 | 204 | 0.0020374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4566-34_0_8_line_119 |  | 111 | 112 | 0.01551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4566-34_0_8_line_120 |  | 112 | 113 | 0.028423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4566-34_0_8_line_121 |  | 112 | 114 | 0.010187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4566-34_0_8_line_122 |  | 112 | 115 | 0.021976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4566-34_0_8_line_123 |  | 113 | 116 | 0.00052388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4566-34_0_8_line_124 |  | 114 | 117 | 0.029826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4566-34_0_8_line_125 |  | 117 | 118 | 0.013046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4566-34_0_8_line_126 |  | 118 | 146 | 0.013266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4566-34_0_8_line_127 |  | 118 | 147 | 0.010366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4566-34_0_8_line_128 |  | 118 | 143 | 0.021435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
129 | LV_4566-34_0_8_line_129 |  | 119 | 120 | 0.0057721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_4566-34_0_8_line_130 |  | 119 | 121 | 0.014807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_4566-34_0_8_line_131 |  | 120 | 189 | 0.0071133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_4566-34_0_8_line_132 |  | 121 | 151 | 0.00034253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_4566-34_0_8_line_133 |  | 122 | 123 | 0.002753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4566-34_0_8_line_134 |  | 123 | 124 | 0.008312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4566-34_0_8_line_135 |  | 124 | 125 | 0.009753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4566-34_0_8_line_136 |  | 125 | 126 | 0.0050353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4566-34_0_8_line_137 |  | 126 | 127 | 0.0066818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4566-34_0_8_line_138 |  | 127 | 169 | 0.0004559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4566-34_0_8_line_139 |  | 128 | 129 | 0.010889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
140 | LV_4566-34_0_8_line_140 |  | 129 | 130 | 0.004491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
141 | LV_4566-34_0_8_line_141 |  | 130 | 131 | 0.019059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4566-34_0_8_line_142 |  | 130 | 132 | 0.017356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4566-34_0_8_line_143 |  | 131 | 136 | 0.0039865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4566-34_0_8_line_144 |  | 132 | 139 | 0.025566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4566-34_0_8_line_145 |  | 133 | 134 | 0.012173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4566-34_0_8_line_146 |  | 133 | 135 | 0.0043026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4566-34_0_8_line_147 |  | 133 | 136 | 0.003905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4566-34_0_8_line_148 |  | 134 | 140 | 0.04156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4566-34_0_8_line_149 |  | 134 | 141 | 0.020946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4566-34_0_8_line_150 |  | 135 | 142 | 0.021932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4566-34_0_8_line_151 |  | 137 | 138 | 0.020715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4566-34_0_8_line_152 |  | 138 | 200 | 0.0178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4566-34_0_8_line_153 |  | 138 | 201 | 0.0059179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4566-34_0_8_line_154 |  | 142 | 196 | 0.019373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4566-34_0_8_line_155 |  | 143 | 144 | 2.6807e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
156 | LV_4566-34_0_8_line_156 |  | 144 | 145 | 0.013642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
157 | LV_4566-34_0_8_line_157 |  | 145 | 148 | 0.00029986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
158 | LV_4566-34_0_8_line_158 |  | 146 | 149 | 0.014786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4566-34_0_8_line_159 |  | 147 | 150 | 0.026966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4566-34_0_8_line_160 |  | 148 | 151 | 0.013667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
161 | LV_4566-34_0_8_line_161 |  | 149 | 152 | 0.00022765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4566-34_0_8_line_162 |  | 150 | 153 | 0.0074233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4566-34_0_8_line_163 |  | 152 | 171 | 0.0005524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4566-34_0_8_line_164 |  | 153 | 201 | 0.015771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4566-34_0_8_line_165 |  | 154 | 155 | 0.0085732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4566-34_0_8_line_166 |  | 155 | 156 | 0.027058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4566-34_0_8_line_167 |  | 156 | 179 | 0.0047138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4566-34_0_8_line_168 |  | 158 | 172 | 0.010167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4566-34_0_8_line_169 |  | 160 | 161 | 0.010515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4566-34_0_8_line_170 |  | 160 | 162 | 0.011397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4566-34_0_8_line_171 |  | 161 | 163 | 0.0060776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_4566-34_0_8_line_172 |  | 162 | 164 | 0.0072366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_4566-34_0_8_line_173 |  | 164 | 165 | 0.011849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_4566-34_0_8_line_174 |  | 165 | 166 | 0.0038597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_4566-34_0_8_line_175 |  | 166 | 171 | 0.020291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_4566-34_0_8_line_176 |  | 167 | 168 | 0.0058466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_4566-34_0_8_line_177 |  | 167 | 169 | 0.0067147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_4566-34_0_8_line_178 |  | 168 | 170 | 0.0070099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_4566-34_0_8_line_179 |  | 172 | 173 | 0.021968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_4566-34_0_8_line_180 |  | 172 | 174 | 0.005299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_4566-34_0_8_line_181 |  | 173 | 175 | 0.017132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_4566-34_0_8_line_182 |  | 175 | 176 | 0.0062992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_4566-34_0_8_line_183 |  | 176 | 190 | 0.015684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_4566-34_0_8_line_184 |  | 177 | 178 | 0.020391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_4566-34_0_8_line_185 |  | 177 | 179 | 0.045198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_4566-34_0_8_line_186 |  | 178 | 203 | 0.0027884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_4566-34_0_8_line_187 |  | 180 | 248 | 0.0028471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_4566-34_0_8_line_188 |  | 181 | 182 | 0.013498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
189 | LV_4566-34_0_8_line_189 |  | 181 | 183 | 0.007749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
190 | LV_4566-34_0_8_line_190 |  | 182 | 184 | 0.0026775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
191 | LV_4566-34_0_8_line_191 |  | 183 | 185 | 0.00067932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
192 | LV_4566-34_0_8_line_192 |  | 184 | 186 | 0.0059432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
193 | LV_4566-34_0_8_line_193 |  | 185 | 187 | 0.0056362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
194 | LV_4566-34_0_8_line_194 |  | 186 | 188 | 0.0064368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
195 | LV_4566-34_0_8_line_195 |  | 187 | 189 | 0.019389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
196 | LV_4566-34_0_8_line_196 |  | 188 | 202 | 0.0032003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
197 | LV_4566-34_0_8_line_197 |  | 190 | 191 | 0.021557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_4566-34_0_8_line_198 |  | 191 | 192 | 0.010797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_4566-34_0_8_line_199 |  | 192 | 194 | 0.012786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_4566-34_0_8_line_200 |  | 193 | 202 | 0.017396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
201 | LV_4566-34_0_8_line_201 |  | 194 | 195 | 0.012799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_4566-34_0_8_line_202 |  | 195 | 199 | 0.0091677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_4566-34_0_8_line_203 |  | 196 | 197 | 0.028008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_4566-34_0_8_line_204 |  | 199 | 200 | 0.018068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_4566-34_0_8_line_205 |  | 203 | 205 | 0.031744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_4566-34_0_8_line_206 |  | 204 | 206 | 0.02491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_4566-34_0_8_line_207 |  | 205 | 245 | 8.7558e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_4566-34_0_8_line_208 |  | 207 | 208 | 0.0020758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_4566-34_0_8_line_209 |  | 207 | 209 | 0.27968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_4566-34_0_8_line_210 |  | 208 | 210 | 0.013048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_4566-34_0_8_line_211 |  | 209 | 230 | 0.026257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_4566-34_0_8_line_212 |  | 209 | 229 | 0.014117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_4566-34_0_8_line_213 |  | 210 | 237 | 0.0008734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_4566-34_0_8_line_214 |  | 211 | 212 | 0.009813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_4566-34_0_8_line_215 |  | 211 | 213 | 0.0094661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_4566-34_0_8_line_216 |  | 212 | 214 | 0.011924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_4566-34_0_8_line_217 |  | 213 | 215 | 0.016239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_4566-34_0_8_line_218 |  | 214 | 216 | 0.020302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_4566-34_0_8_line_219 |  | 214 | 217 | 0.011588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_4566-34_0_8_line_220 |  | 214 | 218 | 0.030235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_4566-34_0_8_line_221 |  | 215 | 219 | 0.043964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_4566-34_0_8_line_222 |  | 216 | 231 | 0.015501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_4566-34_0_8_line_223 |  | 217 | 232 | 0.011999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_4566-34_0_8_line_224 |  | 218 | 223 | 0.0038018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_4566-34_0_8_line_225 |  | 219 | 234 | 0.02859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_4566-34_0_8_line_226 |  | 220 | 221 | 0.006522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_4566-34_0_8_line_227 |  | 220 | 222 | 0.016683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_4566-34_0_8_line_228 |  | 221 | 223 | 0.015374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_4566-34_0_8_line_229 |  | 222 | 224 | 0.0046744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_4566-34_0_8_line_230 |  | 222 | 225 | 0.011392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_4566-34_0_8_line_231 |  | 223 | 226 | 0.042259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_4566-34_0_8_line_232 |  | 224 | 227 | 0.0047299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_4566-34_0_8_line_233 |  | 225 | 228 | 0.0066434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_4566-34_0_8_line_234 |  | 226 | 230 | 0.015139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_4566-34_0_8_line_235 |  | 228 | 236 | 0.035652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_4566-34_0_8_line_236 |  | 231 | 235 | 0.027299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_4566-34_0_8_line_237 |  | 233 | 234 | 0.015994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_4566-34_0_8_line_238 |  | 237 | 238 | 0.0020585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_4566-34_0_8_line_239 |  | 238 | 240 | 0.011471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_4566-34_0_8_line_240 |  | 239 | 240 | 0.00097852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_4566-34_0_8_line_241 |  | 239 | 241 | 0.017185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_4566-34_0_8_line_242 |  | 241 | 242 | 0.006918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_4566-34_0_8_line_243 |  | 242 | 243 | 0.023038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_4566-34_0_8_line_244 |  | 242 | 244 | 0.022884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_4566-34_0_8_line_245 |  | 242 | 245 | 0.01139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_4566-34_0_8_line_246 |  | 243 | 246 | 0.014494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_4566-34_0_8_line_247 |  | 244 | 247 | 0.00049841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_4566-34_0_8_line_248 |  | 246 | 249 | 0.012691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
249 | LV_4566-34_0_8_line_249 |  | 247 | 254 | 0.00012755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_4566-34_0_8_line_250 |  | 248 | 249 | 0.0024358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_4566-34_0_8_line_251 |  | 250 | 251 | 0.0061154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_4566-34_0_8_line_252 |  | 251 | 252 | 0.0062784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_4566-34_0_8_line_253 |  | 252 | 253 | 0.001921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_4566-34_0_8_line_254 |  | 254 | 255 | 0.00025039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4566-34_0_8_trafo_75 | 0.63 MVA 20/0.4 kV | 256 | 105 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2710973.9171 | 1267058.1657 | 2710972.727 | 1267059.3305
1 | 2710973.9171 | 1267058.1657 | 2710979.4678 | 1267052.7333
2 | 2710985.9009 | 1267046.4371 | 2710979.4678 | 1267052.7333
3 | 2710988.1125 | 1267044.2726 | 2710985.9009 | 1267046.4371
4 | 2710999.753 | 1267032.8801 | 2710988.1125 | 1267044.2726
5 | 2710999.753 | 1267032.8801 | 2711004.8285 | 1267027.9126
6 | 2710956.3319 | 1267038.4365 | 2710968.0035 | 1267027.5222
7 | 2710956.3319 | 1267038.4365 | 2710948.1109 | 1267046.124
8 | 2710984.1437 | 1267012.4294 | 2710968.0035 | 1267027.5222
9 | 2710952.9853 | 1267051.6626 | 2710948.1109 | 1267046.124 | 2710948.1109 | 1267046.124
10 | 2710997.5242 | 1266997.4872 | 2710986.5481 | 1267010.181 | 2710984.1437 | 1267012.4294
11 | 2710997.5242 | 1266997.4872 | 2711004.9618 | 1267005.2002 | 2711014.3558 | 1267018.5883
12 | 2711014.3558 | 1267018.5883 | 2711024.6923 | 1267033.5066 | 2711042.8949 | 1267021.7272 | 2711046.7483 | 1267017.4181
13 | 2711014.3558 | 1267018.5883 | 2711004.8285 | 1267027.9126
14 | 2711014.3558 | 1267018.5883 | 2711024.6923 | 1267033.5066 | 2711037.0446 | 1267052.5441
15 | 2710985.6485 | 1267096.3874 | 2710984.2396 | 1267097.7584 | 2710975.2169 | 1267107.0296
16 | 2710965.5405 | 1267117.9472 | 2710974.6421 | 1267107.6202 | 2710975.2169 | 1267107.0296
17 | 2710985.6485 | 1267096.3874 | 2710992.5922 | 1267089.6304 | 2711005.1996 | 1267077.3758
18 | 2710965.5405 | 1267117.9472 | 2710946.8624 | 1267104.963 | 2710935.5527 | 1267098.1332
19 | 2710965.5405 | 1267117.9472 | 2710976.8413 | 1267124.4206 | 2710986.3691 | 1267130.6827
20 | 2711037.0446 | 1267052.5441 | 2711010.8311 | 1267071.902 | 2711005.1996 | 1267077.3758
21 | 2710967.1748 | 1267152.3857 | 2710970.5876 | 1267149.4805 | 2710980.7349 | 1267138.8062 | 2710983.9312 | 1267134.1955 | 2710986.3691 | 1267130.6827
22 | 2710986.3691 | 1267130.6827 | 2711015.9152 | 1267150.7379
23 | 2711037.0446 | 1267052.5441 | 2711063.864 | 1267037.4126 | 2711092.0459 | 1267029.1128 | 2711094.288 | 1267028.8803
24 | 2710967.1748 | 1267152.3857 | 2710969.3217 | 1267155.1395 | 2710971.4488 | 1267157.1688
25 | 2711023.6395 | 1267155.9809 | 2711015.9152 | 1267150.7379
26 | 2711025.2895 | 1267161.9409 | 2711019.1176 | 1267171.8225 | 2711017.5833 | 1267173.8886
27 | 2711025.2895 | 1267161.9409 | 2711042.5689 | 1267173.2087 | 2711043.9442 | 1267174.1065
28 | 2711017.5833 | 1267173.8886 | 2711014.1736 | 1267178.4799
29 | 2711053.3915 | 1267180.2738 | 2711043.9442 | 1267174.1065
30 | 2711094.288 | 1267028.8803 | 2711108.5684 | 1267027.3997 | 2711112.5909 | 1267027.33
31 | 2711044.8133 | 1267169.9703 | 2711027.4164 | 1267158.5446 | 2711023.6395 | 1267155.9809
32 | 2711007.8318 | 1267184.1965 | 2711008.018 | 1267183.8912 | 2711014.1736 | 1267178.4799 | 2711014.1736 | 1267178.4799
33 | 2711053.3915 | 1267180.2738 | 2711069.2531 | 1267189.9263
34 | 2711044.8133 | 1267169.9703 | 2711055.6987 | 1267176.9031 | 2711053.3915 | 1267180.2738
35 | 2711046.7483 | 1267017.4181 | 2711052.5488 | 1267012.0779 | 2711061.5176 | 1267000.4252 | 2711069.3124 | 1266988.7253
36 | 2711092.4529 | 1266957.8472 | 2711085.2066 | 1266967.1858 | 2711074.2717 | 1266981.2815 | 2711069.3124 | 1266988.7253
37 | 2711092.4529 | 1266957.8472 | 2711102.7073 | 1266947.9091 | 2711114.2884 | 1266932.6913 | 2711117.5486 | 1266925.5019
38 | 2711136.233 | 1267027.7868 | 2711123.6479 | 1267027.1385 | 2711112.5909 | 1267027.33
39 | 2711222.7619 | 1267399.1644 | 2711222.9097 | 1267399.2266
40 | 2711222.9097 | 1267399.2266 | 2711238.3256 | 1267405.7151 | 2711239.2818 | 1267406.1382
41 | 2711222.7619 | 1267399.1644 | 2711205.4563 | 1267391.8805
42 | 2711205.1702 | 1267391.7601 | 2711205.4563 | 1267391.8805
43 | 2711189.7711 | 1267385.2786 | 2711205.1702 | 1267391.7601
44 | 2711189.7711 | 1267385.2786 | 2711186.0351 | 1267383.7062
45 | 2711280.5232 | 1267363.1834 | 2711279.7693 | 1267368.8297 | 2711279.8688 | 1267373.1353 | 2711282.5455 | 1267376.1328 | 2711294.7676 | 1267380.8226
46 | 2711294.7676 | 1267380.8226 | 2711304.7922 | 1267368.6785 | 2711312.0192 | 1267351.4683
47 | 2711280.5232 | 1267363.1834 | 2711282.4906 | 1267358.6721
48 | 2711280.5232 | 1267363.1834 | 2711277.0107 | 1267364.5852 | 2711272.9095 | 1267364.4634 | 2711268.606 | 1267361.8912 | 2711265.6735 | 1267356.0865 | 2711265.3985 | 1267355.0631
49 | 2711312.0192 | 1267351.4683 | 2711322.8909 | 1267325.5792
50 | 2711117.5486 | 1266925.5019 | 2711126.2958 | 1266932.0387 | 2711131.8739 | 1266933.3225 | 2711135.256 | 1266932.0627
51 | 2711208.6633 | 1266974.9364 | 2711215.8063 | 1266972.6911 | 2711216.7177 | 1266973.0752
52 | 2711208.6633 | 1266974.9364 | 2711206.8483 | 1266980.5516 | 2711203.3538 | 1266988.9821 | 2711196.4783 | 1267005.823 | 2711193.2719 | 1267012.0313
53 | 2711178.2733 | 1267024.9083 | 2711179.4446 | 1267025.4863 | 2711181.4449 | 1267026.4248 | 2711184.3512 | 1267027.6361 | 2711185.5198 | 1267027.1576 | 2711186.2566 | 1267025.6146 | 2711193.2719 | 1267012.0313
54 | 2711568.5964 | 1266776.1461 | 2711574.9354 | 1266777.8116 | 2711580.796 | 1266776.8992 | 2711583.6196 | 1266775.9699
55 | 2711568.5964 | 1266776.1461 | 2711566.1027 | 1266786.2703
56 | 2711575.5663 | 1266842.0685 | 2711564.5334 | 1266809.454 | 2711563.2575 | 1266799.6658 | 2711564.8774 | 1266791.2446 | 2711566.1027 | 1266786.2703
57 | 2711579.4812 | 1266853.6636 | 2711575.5663 | 1266842.0685
58 | 2711579.4812 | 1266853.6636 | 2711584.1178 | 1266866.1176 | 2711584.7353 | 1266868.2273
59 | 2711575.5663 | 1266842.0685 | 2711571.4111 | 1266842.3903 | 2711566.8106 | 1266843.5712 | 2711566.779 | 1266843.5972
60 | 2711584.7353 | 1266868.2273 | 2711585.3486 | 1266870.3223 | 2711590.8099 | 1266888.9416 | 2711592.1735 | 1266895.8982
61 | 2711518.4536 | 1266903.1453 | 2711520.2073 | 1266905.6658
62 | 2711535.091 | 1266927.0565 | 2711520.2073 | 1266905.6658
63 | 2711535.091 | 1266927.0565 | 2711522.0591 | 1266945.0315
64 | 2711592.1735 | 1266895.8982 | 2711595.2122 | 1266911.3999 | 2711595.6449 | 1266914.7999 | 2711595.7491 | 1266916.8326
65 | 2711595.9509 | 1266922.2269 | 2711595.953 | 1266920.811 | 2711595.7491 | 1266916.8326
66 | 2711566.779 | 1266843.5972 | 2711564.1334 | 1266845.7781 | 2711563.0619 | 1266849.4834 | 2711563.4317 | 1266863.2103
67 | 2711136.233 | 1267027.7868 | 2711137.3628 | 1267021.3691 | 2711143.8072 | 1267007.8229 | 2711156.6836 | 1267014.204 | 2711178.2733 | 1267024.9083
68 | 2711136.233 | 1267027.7868 | 2711141.5139 | 1267028.053 | 2711150.0065 | 1267029.4911
69 | 2711051.3896 | 1267086.9325 | 2711061.7985 | 1267090.787 | 2711063.4937 | 1267092.3776
70 | 2711046.7533 | 1267078.8161 | 2711051.3896 | 1267086.9325 | 2711051.3896 | 1267086.9325
71 | 2711081.1121 | 1267119.2081 | 2711075.6218 | 1267108.8626 | 2711068.8498 | 1267097.4031 | 2711063.4937 | 1267092.3776
72 | 2711081.1121 | 1267119.2081 | 2711084.6256 | 1267116.9611 | 2711089.4598 | 1267115.7509 | 2711095.2225 | 1267115.7726
73 | 2711081.1121 | 1267119.2081 | 2711078.1308 | 1267121.9878 | 2711054.2843 | 1267156.3306
74 | 2711110.3012 | 1267120.5913 | 2711098.3291 | 1267115.7843 | 2711095.2225 | 1267115.7726
75 | 2711044.8133 | 1267169.9703 | 2711054.2843 | 1267156.3306
76 | 2711110.3012 | 1267120.5913 | 2711113.5478 | 1267121.8516
77 | 2711110.3012 | 1267120.5913 | 2711109.3411 | 1267123.5981
78 | 2711109.3411 | 1267123.5981 | 2711103.3255 | 1267142.5179
79 | 2711109.3411 | 1267123.5981 | 2711124.0559 | 1267129.5021 | 2711124.9927 | 1267129.8753
80 | 2711101.9937 | 1267146.7065 | 2711103.3255 | 1267142.5179
81 | 2711147.0286 | 1267138.6961 | 2711137.2991 | 1267134.7779 | 2711124.9927 | 1267129.8753
82 | 2711083.8406 | 1267193.9134 | 2711081.9237 | 1267197.7474
83 | 2711083.8406 | 1267193.9134 | 2711093.3042 | 1267198.9639
84 | 2711081.9237 | 1267197.7474 | 2711073.986 | 1267212.7682
85 | 2711081.9237 | 1267197.7474 | 2711077.623 | 1267195.0198 | 2711069.2531 | 1267189.9263
86 | 2711093.3042 | 1267198.9639 | 2711113.7756 | 1267209.8889
87 | 2711276.4426 | 1267285.5822 | 2711265.9751 | 1267281.338 | 2711253.459 | 1267276.0138
88 | 2711244.119 | 1267272.0407 | 2711253.459 | 1267276.0138
89 | 2711276.4426 | 1267285.5822 | 2711285.6499 | 1267289.3154 | 2711290.2225 | 1267291.5924 | 2711293.4915 | 1267293.07
90 | 2711245.213 | 1267269.1254 | 2711244.119 | 1267272.0407
91 | 2711244.119 | 1267272.0407 | 2711232.5209 | 1267267.378
92 | 2711235.5818 | 1267263.1834 | 2711238.6778 | 1267265.9107 | 2711245.213 | 1267269.1254
93 | 2711245.213 | 1267269.1254 | 2711255.7558 | 1267273.4593
94 | 2711208.6661 | 1267257.7904 | 2711209.2057 | 1267258.0047 | 2711232.5209 | 1267267.378
95 | 2711235.5818 | 1267263.1834 | 2711238.2712 | 1267256.3169
96 | 2711208.6661 | 1267257.7904 | 2711203.0923 | 1267255.5765 | 2711186.6392 | 1267248.0381 | 2711181.7339 | 1267245.9432
97 | 2711238.2712 | 1267256.3169 | 2711243.5722 | 1267242.9409
98 | 2711243.5722 | 1267242.9409 | 2711249.8696 | 1267227.0507
99 | 2711164.4923 | 1267238.5799 | 2711181.7339 | 1267245.9432
100 | 2711119.2734 | 1267421.034 | 2711133.5923 | 1267431.4304
101 | 2711119.2734 | 1267421.034 | 2711115.956 | 1267418.6254
102 | 2711134.8058 | 1267432.3115 | 2711133.5923 | 1267431.4304
103 | 2711115.956 | 1267418.6254 | 2711104.2461 | 1267410.1233
104 | 2711134.8058 | 1267432.3115 | 2711148.431 | 1267442.2042
105 | 2711102.4417 | 1267408.8132 | 2711104.2461 | 1267410.1233
106 | 2711148.431 | 1267442.2042 | 2711151.0765 | 1267444.125
107 | 2711102.4417 | 1267408.8132 | 2711085.3398 | 1267396.3961 | 2711082.0479 | 1267394.5248
108 | 2711163.7114 | 1267453.3903 | 2711162.923 | 1267452.7263 | 2711151.0765 | 1267444.125
109 | 2711081.8164 | 1267394.3931 | 2711082.0479 | 1267394.5248
110 | 2711171.9988 | 1267377.7983 | 2711186.0351 | 1267383.7062
111 | 2711073.986 | 1267212.7682 | 2711071.104 | 1267218.2218
112 | 2711135.2426 | 1267220.8663 | 2711128.5092 | 1267217.7517 | 2711113.7756 | 1267209.8889
113 | 2711101.9937 | 1267146.7065 | 2711101.5136 | 1267148.2164
114 | 2711149.2634 | 1267139.596 | 2711147.0286 | 1267138.6961
115 | 2711150.4945 | 1267136.194 | 2711149.2634 | 1267139.596
116 | 2711150.4945 | 1267136.194 | 2711155.686 | 1267121.7441
117 | 2711149.2634 | 1267139.596 | 2711153.2541 | 1267141.1947 | 2711167.7788 | 1267146.8909
118 | 2711155.686 | 1267121.7441 | 2711156.3749 | 1267119.8267
119 | 2711056.6512 | 1267380.0872 | 2711048.5573 | 1267393.3181
120 | 2711056.6512 | 1267380.0872 | 2711081.3609 | 1267394.1342
121 | 2711056.6512 | 1267380.0872 | 2711061.5878 | 1267371.1762
122 | 2711056.6512 | 1267380.0872 | 2711037.4372 | 1267369.4219
123 | 2711081.3609 | 1267394.1342 | 2711081.8164 | 1267394.3931
124 | 2711061.5878 | 1267371.1762 | 2711076.0414 | 1267345.0862
125 | 2711082.3635 | 1267333.6743 | 2711076.0414 | 1267345.0862
126 | 2711082.3635 | 1267333.6743 | 2711093.9527 | 1267340.1309
127 | 2711082.3635 | 1267333.6743 | 2711084.6347 | 1267329.4133 | 2711087.242 | 1267324.5276
128 | 2711082.3635 | 1267333.6743 | 2711063.6227 | 1267323.2702
129 | 2711026.2157 | 1267302.5032 | 2711028.9412 | 1267297.4152
130 | 2711026.2157 | 1267302.5032 | 2711039.1618 | 1267309.6904
131 | 2711032.3001 | 1267291.1449 | 2711028.9412 | 1267297.4152
132 | 2711039.1618 | 1267309.6904 | 2711039.4613 | 1267309.8567
133 | 2710975.7046 | 1267225.0692 | 2710976.4616 | 1267223.9558 | 2710977.0631 | 1267222.6843
134 | 2710980.6174 | 1267215.1706 | 2710977.0631 | 1267222.6843
135 | 2710980.6174 | 1267215.1706 | 2710986.9909 | 1267207.7727
136 | 2710986.9909 | 1267207.7727 | 2710990.7515 | 1267204.4244
137 | 2710990.7515 | 1267204.4244 | 2710995.7419 | 1267199.9811
138 | 2710996.0824 | 1267199.678 | 2710995.7419 | 1267199.9811
139 | 2711145.1253 | 1267225.4376 | 2711135.2426 | 1267220.8663
140 | 2711145.1253 | 1267225.4376 | 2711143.2937 | 1267229.54
141 | 2711143.2937 | 1267229.54 | 2711147.3797 | 1267231.2739 | 2711160.826 | 1267237.0146
142 | 2711143.2937 | 1267229.54 | 2711139.3822 | 1267227.7316 | 2711132.8094 | 1267224.5052 | 2711127.6896 | 1267221.9434
143 | 2711164.4923 | 1267238.5799 | 2711160.826 | 1267237.0146
144 | 2711127.6896 | 1267221.9434 | 2711110.6852 | 1267213.4351 | 2711104.9208 | 1267210.322
145 | 2711177.032 | 1267240.0171 | 2711165.931 | 1267234.9483
146 | 2711165.931 | 1267234.9483 | 2711167.4973 | 1267230.9409
147 | 2711165.931 | 1267234.9483 | 2711164.4923 | 1267238.5799
148 | 2711177.032 | 1267240.0171 | 2711192.0967 | 1267201.2839
149 | 2711177.032 | 1267240.0171 | 2711196.5091 | 1267247.7235
150 | 2711181.1209 | 1267219.5294 | 2711178.3355 | 1267226.3741 | 2711176.5128 | 1267230.3989 | 2711175.1046 | 1267232.0071 | 2711173.326 | 1267232.4963 | 2711171.3004 | 1267232.5027 | 2711169.2063 | 1267231.7515 | 2711167.4973 | 1267230.9409
151 | 2711115.7326 | 1267276.9187 | 2711125.2264 | 1267258.5068
152 | 2711115.7326 | 1267276.9187 | 2711116.6205 | 1267279.3486 | 2711119.4319 | 1267281.9927 | 2711129.5727 | 1267287.0972
153 | 2711115.7326 | 1267276.9187 | 2711110.8581 | 1267280.2744
154 | 2711181.1209 | 1267219.5294 | 2711182.3776 | 1267216.4415 | 2711188.2671 | 1267201.5231
155 | 2711063.5993 | 1267323.2571 | 2711063.6227 | 1267323.2702
156 | 2711063.5993 | 1267323.2571 | 2711051.6723 | 1267316.6358
157 | 2711051.4102 | 1267316.4902 | 2711051.6723 | 1267316.6358
158 | 2711106.8691 | 1267347.3268 | 2711093.9527 | 1267340.1309
159 | 2711099.9377 | 1267300.7376 | 2711087.242 | 1267324.5276
160 | 2711051.4102 | 1267316.4902 | 2711039.4613 | 1267309.8567
161 | 2711106.8691 | 1267347.3268 | 2711107.0679 | 1267347.4376
162 | 2711103.4327 | 1267294.1886 | 2711099.9377 | 1267300.7376
163 | 2711107.0679 | 1267347.4376 | 2711107.5505 | 1267347.7065
164 | 2711103.4327 | 1267294.1886 | 2711110.8581 | 1267280.2744
165 | 2711240.2921 | 1267080.0214 | 2711237.0878 | 1267087.9733
166 | 2711237.0878 | 1267087.9733 | 2711232.7617 | 1267098.709 | 2711226.9913 | 1267113.0766
167 | 2711225.2345 | 1267117.4508 | 2711226.9913 | 1267113.0766
168 | 2711262.7606 | 1267345.2444 | 2711265.3985 | 1267355.0631
169 | 2711156.7058 | 1267371.3615 | 2711166.3971 | 1267375.4406
170 | 2711156.7058 | 1267371.3615 | 2711146.2015 | 1267366.9403
171 | 2711171.9988 | 1267377.7983 | 2711166.3971 | 1267375.4406
172 | 2711139.5317 | 1267364.133 | 2711146.2015 | 1267366.9403
173 | 2711128.648 | 1267359.4603 | 2711129.3214 | 1267359.8355 | 2711139.5317 | 1267364.133
174 | 2711125.2763 | 1267357.5819 | 2711128.648 | 1267359.4603
175 | 2711107.5505 | 1267347.7065 | 2711125.2763 | 1267357.5819
176 | 2711000.8159 | 1267194.9618 | 2711004.1802 | 1267190.1802 | 2711004.1802 | 1267190.1802
177 | 2711000.8159 | 1267194.9618 | 2710999.8711 | 1267196.3046 | 2710996.0824 | 1267199.678
178 | 2711007.8318 | 1267184.1965 | 2711004.1802 | 1267190.1802
179 | 2711262.7606 | 1267345.2444 | 2711242.5967 | 1267336.5263
180 | 2711262.7606 | 1267345.2444 | 2711267.7129 | 1267347.1299
181 | 2711226.1821 | 1267332.0446 | 2711236.2174 | 1267333.7681 | 2711242.5967 | 1267336.5263
182 | 2711226.1821 | 1267332.0446 | 2711225.1623 | 1267331.8695 | 2711220.3214 | 1267329.8006
183 | 2711205.8997 | 1267323.6372 | 2711220.3214 | 1267329.8006
184 | 2711208.3898 | 1267159.3922 | 2711227.3964 | 1267166.7778
185 | 2711208.3898 | 1267159.3922 | 2711225.2345 | 1267117.4508
186 | 2711229.9955 | 1267167.7877 | 2711227.3964 | 1267166.7778
187 | 2711250.9186 | 1267224.4039 | 2711249.8696 | 1267227.0507
188 | 2711048.097 | 1267261.6559 | 2711052.1073 | 1267254.1697 | 2711054.4458 | 1267249.7444
189 | 2711048.097 | 1267261.6559 | 2711044.4379 | 1267268.4865
190 | 2711055.6968 | 1267247.3772 | 2711054.4458 | 1267249.7444
191 | 2711044.4379 | 1267268.4865 | 2711044.1171 | 1267269.0854
192 | 2711055.6968 | 1267247.3772 | 2711058.4736 | 1267242.1226
193 | 2711044.1171 | 1267269.0854 | 2711041.4557 | 1267274.0536
194 | 2711061.481 | 1267236.4315 | 2711058.4736 | 1267242.1226
195 | 2711032.3001 | 1267291.1449 | 2711041.4557 | 1267274.0536
196 | 2711061.481 | 1267236.4315 | 2711062.9763 | 1267233.602
197 | 2711205.8997 | 1267323.6372 | 2711193.3955 | 1267318.2932 | 2711187.6872 | 1267312.7477
198 | 2711177.9092 | 1267308.1694 | 2711187.6872 | 1267312.7477 | 2711187.6872 | 1267312.7477
199 | 2711177.9092 | 1267308.1694 | 2711166.3298 | 1267302.7475
200 | 2711062.9763 | 1267233.602 | 2711071.104 | 1267218.2218
201 | 2711166.3298 | 1267302.7475 | 2711154.7389 | 1267297.3203
202 | 2711146.2216 | 1267293.978 | 2711150.6675 | 1267295.414 | 2711154.7389 | 1267297.3203
203 | 2711198.5518 | 1267175.4715 | 2711188.2671 | 1267201.5231
204 | 2711129.5727 | 1267287.0972 | 2711137.9074 | 1267291.2926 | 2711146.2216 | 1267293.978
205 | 2711259.6611 | 1267171.1905 | 2711247.0999 | 1267166.171 | 2711245.0013 | 1267166.454 | 2711238.33 | 1267169.6535 | 2711235.0079 | 1267169.7354 | 2711229.9955 | 1267167.7877
206 | 2711164.7973 | 1267096.3838 | 2711156.3749 | 1267119.8267
207 | 2711259.7424 | 1267171.2229 | 2711259.6611 | 1267171.1905
208 | 2711290.2915 | 1267124.6239 | 2711289.5323 | 1267126.5559
209 | 2711290.2915 | 1267124.6239 | 2711513.7683 | 1266956.4577
210 | 2711284.7602 | 1267138.7001 | 2711289.5323 | 1267126.5559
211 | 2711513.7683 | 1266956.4577 | 2711528.6162 | 1266959.307 | 2711534.202 | 1266961.7701 | 2711538.2547 | 1266964.8715
212 | 2711513.7683 | 1266956.4577 | 2711521.2675 | 1266946.1235 | 2711522.0591 | 1266945.0315
213 | 2711284.7602 | 1267138.7001 | 2711284.4408 | 1267139.513
214 | 2711615.7525 | 1267010.3316 | 2711614.0939 | 1267009.987 | 2711606.7507 | 1267006.5238
215 | 2711615.7525 | 1267010.3316 | 2711624.6919 | 1267012.1891 | 2711625.0272 | 1267012.2084
216 | 2711595.9655 | 1267001.4372 | 2711606.7507 | 1267006.5238
217 | 2711641.2393 | 1267013.1461 | 2711625.0272 | 1267012.2084
218 | 2711595.9655 | 1267001.4372 | 2711588.5972 | 1267020.3544
219 | 2711595.9655 | 1267001.4372 | 2711585.3165 | 1266996.8671
220 | 2711595.9655 | 1267001.4372 | 2711599.8302 | 1266993.3698 | 2711601.2388 | 1266988.5589 | 2711601.3658 | 1266985.4252 | 2711599.9673 | 1266981.7289 | 2711597.7497 | 1266977.9504 | 2711595.7256 | 1266973.5902
221 | 2711685.0843 | 1267012.5255 | 2711683.8659 | 1267012.7407 | 2711667.7102 | 1267014.1589 | 2711661.4495 | 1267014.3408 | 2711648.4 | 1267013.5603 | 2711641.2393 | 1267013.1461
222 | 2711582.9711 | 1267034.7988 | 2711582.9711 | 1267034.7988 | 2711588.5972 | 1267020.3544
223 | 2711585.3165 | 1266996.8671 | 2711580.1082 | 1266994.6319 | 2711574.4645 | 1266991.7631
224 | 2711594.1248 | 1266970.1418 | 2711595.7256 | 1266973.5902
225 | 2711713.182 | 1267007.2869 | 2711709.2887 | 1267008.2506 | 2711685.0843 | 1267012.5255
226 | 2711594.6203 | 1266948.2619 | 2711594.2157 | 1266953.3733 | 2711594.2082 | 1266954.768
227 | 2711595.9368 | 1266931.6313 | 2711594.6203 | 1266948.2619
228 | 2711594.1248 | 1266970.1418 | 2711594.2082 | 1266954.768
229 | 2711595.9368 | 1266931.6313 | 2711595.9438 | 1266926.9569
230 | 2711595.9368 | 1266931.6313 | 2711607.2919 | 1266930.7105
231 | 2711594.1248 | 1266970.1418 | 2711576.4069 | 1266968.15 | 2711554.0794 | 1266963.0463 | 2711552.5674 | 1266962.8415
232 | 2711595.9509 | 1266922.2269 | 2711595.9438 | 1266926.9569
233 | 2711607.2919 | 1266930.7105 | 2711611.3968 | 1266930.3776 | 2711613.724 | 1266931.3573
234 | 2711538.2547 | 1266964.8715 | 2711541.211 | 1266962.6364 | 2711547.0193 | 1266962.09 | 2711552.5674 | 1266962.8415
235 | 2711640.2886 | 1266954.0896 | 2711634.3024 | 1266947.136 | 2711623.2077 | 1266935.3495 | 2711613.724 | 1266931.3573
236 | 2711582.9711 | 1267034.7988 | 2711580.288 | 1267046.4917 | 2711580.2862 | 1267056.5449 | 2711581.5603 | 1267061.6365
237 | 2711728.7072 | 1267003.4439 | 2711713.182 | 1267007.2869
238 | 2711284.4408 | 1267139.513 | 2711283.6879 | 1267141.429
239 | 2711283.6879 | 1267141.429 | 2711279.4926 | 1267152.1054
240 | 2711279.4926 | 1267152.1054 | 2711279.1348 | 1267153.0161
241 | 2711279.1348 | 1267153.0161 | 2711272.8496 | 1267169.0108
242 | 2711270.3195 | 1267175.4496 | 2711272.8496 | 1267169.0108
243 | 2711270.3195 | 1267175.4496 | 2711261.8317 | 1267196.8668
244 | 2711270.3195 | 1267175.4496 | 2711291.5531 | 1267183.9832
245 | 2711270.3195 | 1267175.4496 | 2711259.7424 | 1267171.2229
246 | 2711261.8317 | 1267196.8668 | 2711256.4919 | 1267210.3408
247 | 2711292.0155 | 1267184.1691 | 2711291.5531 | 1267183.9832
248 | 2711251.816 | 1267222.1395 | 2711256.4919 | 1267210.3408
249 | 2711292.1339 | 1267184.2167 | 2711292.0155 | 1267184.1691
250 | 2711250.9186 | 1267224.4039 | 2711251.816 | 1267222.1395
251 | 2711101.5136 | 1267148.2164 | 2711099.6606 | 1267154.0444
252 | 2711099.6606 | 1267154.0444 | 2711097.7583 | 1267160.0276
253 | 2711097.1762 | 1267161.8584 | 2711097.7583 | 1267160.0276
254 | 2711292.3662 | 1267184.31 | 2711292.1339 | 1267184.2167

## bus_geodata
| x | y | coords
0 | 2710973.9171 | 1267058.1658
1 | 2710972.727 | 1267059.3305
2 | 2710979.4678 | 1267052.7333
3 | 2710985.9009 | 1267046.4371
4 | 2710988.1125 | 1267044.2726
5 | 2710999.753 | 1267032.8801
6 | 2710956.3319 | 1267038.4365
7 | 2710968.0035 | 1267027.5222
8 | 2710948.1109 | 1267046.124
9 | 2710984.1437 | 1267012.4294
10 | 2710952.9853 | 1267051.6626
11 | 2710997.5242 | 1266997.4872
12 | 2711014.3558 | 1267018.5883
13 | 2710975.2169 | 1267107.0296
14 | 2710985.6485 | 1267096.3874
15 | 2710965.5405 | 1267117.9472
16 | 2711005.1996 | 1267077.3758
17 | 2710935.5527 | 1267098.1332
18 | 2710986.3691 | 1267130.6827
19 | 2711037.0446 | 1267052.5441
20 | 2710967.1748 | 1267152.3857
21 | 2711015.9152 | 1267150.7379
22 | 2710971.4488 | 1267157.1688
23 | 2711025.2895 | 1267161.9409
24 | 2711017.5833 | 1267173.8886
25 | 2711043.9442 | 1267174.1065
26 | 2711094.288 | 1267028.8803
27 | 2711023.6395 | 1267155.9809
28 | 2711014.1736 | 1267178.4799
29 | 2711053.3915 | 1267180.2738
30 | 2711046.7483 | 1267017.4181
31 | 2711004.8285 | 1267027.9126
32 | 2711069.3124 | 1266988.7253
33 | 2711092.4529 | 1266957.8472
34 | 2711112.5909 | 1267027.33
35 | 2711222.9097 | 1267399.2266
36 | 2711222.7619 | 1267399.1644
37 | 2711239.2818 | 1267406.1382
38 | 2711205.4563 | 1267391.8805
39 | 2711205.1702 | 1267391.7601
40 | 2711189.7711 | 1267385.2786
41 | 2711294.7676 | 1267380.8226
42 | 2711280.5232 | 1267363.1834
43 | 2711312.0192 | 1267351.4683
44 | 2711135.256 | 1266932.0627
45 | 2711117.5486 | 1266925.5019
46 | 2711208.6633 | 1266974.9364
47 | 2711216.7177 | 1266973.0752
48 | 2711193.2719 | 1267012.0313
49 | 2711583.6196 | 1266775.9699
50 | 2711568.5964 | 1266776.1461
51 | 2711566.1027 | 1266786.2703
52 | 2711579.4812 | 1266853.6636
53 | 2711575.5663 | 1266842.0685
54 | 2711584.7353 | 1266868.2273
55 | 2711520.2073 | 1266905.6658
56 | 2711518.4536 | 1266903.1453
57 | 2711535.091 | 1266927.0565
58 | 2711592.1735 | 1266895.8982
59 | 2711595.7491 | 1266916.8326
60 | 2711566.779 | 1266843.5972
61 | 2711563.4317 | 1266863.2103
62 | 2711136.233 | 1267027.7868
63 | 2711178.2733 | 1267024.9083
64 | 2711150.0065 | 1267029.4911
65 | 2711051.3896 | 1267086.9325
66 | 2711063.4937 | 1267092.3776
67 | 2711046.7533 | 1267078.8161
68 | 2711081.1121 | 1267119.2081
69 | 2711095.2225 | 1267115.7726
70 | 2711054.2843 | 1267156.3306
71 | 2711110.3012 | 1267120.5913
72 | 2711113.5478 | 1267121.8516
73 | 2711109.3411 | 1267123.5981
74 | 2711103.3255 | 1267142.5179
75 | 2711124.9927 | 1267129.8753
76 | 2711083.8406 | 1267193.9134
77 | 2711081.9237 | 1267197.7474
78 | 2711093.3042 | 1267198.9639
79 | 2711069.2531 | 1267189.9263
80 | 2711044.8133 | 1267169.9703
81 | 2711253.459 | 1267276.0138
82 | 2711276.4426 | 1267285.5822
83 | 2711244.119 | 1267272.0407
84 | 2711293.4915 | 1267293.07
85 | 2711245.213 | 1267269.1254
86 | 2711232.5209 | 1267267.378
87 | 2711235.5818 | 1267263.1834
88 | 2711255.7558 | 1267273.4593
89 | 2711208.6661 | 1267257.7904
90 | 2711238.2712 | 1267256.3169
91 | 2711243.5722 | 1267242.9409
92 | 2711181.7339 | 1267245.9432
93 | 2711119.2734 | 1267421.034
94 | 2711133.5923 | 1267431.4304
95 | 2711115.956 | 1267418.6254
96 | 2711134.8058 | 1267432.3115
97 | 2711104.2461 | 1267410.1233
98 | 2711148.431 | 1267442.2042
99 | 2711102.4417 | 1267408.8132
100 | 2711151.0765 | 1267444.125
101 | 2711082.0479 | 1267394.5248
102 | 2711163.7114 | 1267453.3903
103 | 2711186.0351 | 1267383.7062
104 | 2711073.986 | 1267212.7682
105 | 2711113.7756 | 1267209.8889
106 | 2711101.9937 | 1267146.7065
107 | 2711147.0286 | 1267138.6961
108 | 2711150.4945 | 1267136.194
109 | 2711149.2634 | 1267139.596
110 | 2711155.686 | 1267121.7441
111 | 2711048.5573 | 1267393.3181
112 | 2711056.6512 | 1267380.0872
113 | 2711081.3609 | 1267394.1342
114 | 2711061.5878 | 1267371.1762
115 | 2711037.4372 | 1267369.4219
116 | 2711081.8164 | 1267394.3931
117 | 2711076.0414 | 1267345.0862
118 | 2711082.3635 | 1267333.6743
119 | 2711026.2157 | 1267302.5032
120 | 2711028.9412 | 1267297.4152
121 | 2711039.1618 | 1267309.6904
122 | 2710975.7046 | 1267225.0692
123 | 2710977.0631 | 1267222.6843
124 | 2710980.6174 | 1267215.1706
125 | 2710986.9909 | 1267207.7727
126 | 2710990.7515 | 1267204.4244
127 | 2710995.7419 | 1267199.9811
128 | 2711135.2426 | 1267220.8663
129 | 2711145.1253 | 1267225.4376
130 | 2711143.2937 | 1267229.54
131 | 2711160.826 | 1267237.0146
132 | 2711127.6896 | 1267221.9434
133 | 2711165.931 | 1267234.9483
134 | 2711177.032 | 1267240.0171
135 | 2711167.4973 | 1267230.9409
136 | 2711164.4923 | 1267238.5799
137 | 2711125.2264 | 1267258.5068
138 | 2711115.7326 | 1267276.9187
139 | 2711104.9208 | 1267210.322
140 | 2711192.0967 | 1267201.2839
141 | 2711196.5091 | 1267247.7235
142 | 2711181.1209 | 1267219.5294
143 | 2711063.6227 | 1267323.2702
144 | 2711063.5993 | 1267323.2571
145 | 2711051.6723 | 1267316.6358
146 | 2711093.9527 | 1267340.1309
147 | 2711087.242 | 1267324.5276
148 | 2711051.4102 | 1267316.4902
149 | 2711106.8691 | 1267347.3268
150 | 2711099.9377 | 1267300.7376
151 | 2711039.4613 | 1267309.8567
152 | 2711107.0679 | 1267347.4376
153 | 2711103.4327 | 1267294.1886
154 | 2711240.2921 | 1267080.0214
155 | 2711237.0878 | 1267087.9733
156 | 2711226.9913 | 1267113.0766
157 | 2711282.4906 | 1267358.6721
158 | 2711265.3985 | 1267355.0631
159 | 2711322.8909 | 1267325.5792
160 | 2711156.7058 | 1267371.3615
161 | 2711166.3971 | 1267375.4406
162 | 2711146.2015 | 1267366.9403
163 | 2711171.9988 | 1267377.7983
164 | 2711139.5317 | 1267364.133
165 | 2711128.648 | 1267359.4603
166 | 2711125.2763 | 1267357.5819
167 | 2711000.8159 | 1267194.9618
168 | 2711004.1802 | 1267190.1802
169 | 2710996.0824 | 1267199.678
170 | 2711007.8318 | 1267184.1965
171 | 2711107.5505 | 1267347.7065
172 | 2711262.7606 | 1267345.2444
173 | 2711242.5967 | 1267336.5263
174 | 2711267.7129 | 1267347.1299
175 | 2711226.1821 | 1267332.0446
176 | 2711220.3214 | 1267329.8006
177 | 2711208.3898 | 1267159.3922
178 | 2711227.3964 | 1267166.7778
179 | 2711225.2345 | 1267117.4508
180 | 2711249.8696 | 1267227.0507
181 | 2711048.097 | 1267261.6559
182 | 2711054.4458 | 1267249.7444
183 | 2711044.4379 | 1267268.4865
184 | 2711055.6968 | 1267247.3772
185 | 2711044.1171 | 1267269.0854
186 | 2711058.4736 | 1267242.1226
187 | 2711041.4557 | 1267274.0536
188 | 2711061.481 | 1267236.4315
189 | 2711032.3001 | 1267291.1449
190 | 2711205.8997 | 1267323.6372
191 | 2711187.6872 | 1267312.7477
192 | 2711177.9092 | 1267308.1694
193 | 2711071.104 | 1267218.2218
194 | 2711166.3298 | 1267302.7475
195 | 2711154.7389 | 1267297.3203
196 | 2711188.2671 | 1267201.5231
197 | 2711198.5518 | 1267175.4715
198 | 2711167.7788 | 1267146.8909
199 | 2711146.2216 | 1267293.978
200 | 2711129.5727 | 1267287.0972
201 | 2711110.8581 | 1267280.2744
202 | 2711062.9763 | 1267233.602
203 | 2711229.9955 | 1267167.7877
204 | 2711156.3749 | 1267119.8267
205 | 2711259.6611 | 1267171.1905
206 | 2711164.7973 | 1267096.3838
207 | 2711290.2915 | 1267124.6239
208 | 2711289.5323 | 1267126.5559
209 | 2711513.7683 | 1266956.4577
210 | 2711284.7602 | 1267138.7001
211 | 2711615.7525 | 1267010.3316
212 | 2711606.7507 | 1267006.5238
213 | 2711625.0272 | 1267012.2084
214 | 2711595.9655 | 1267001.4372
215 | 2711641.2393 | 1267013.1461
216 | 2711588.5972 | 1267020.3544
217 | 2711585.3165 | 1266996.8671
218 | 2711595.7256 | 1266973.5902
219 | 2711685.0843 | 1267012.5255
220 | 2711594.6203 | 1266948.2619
221 | 2711594.2082 | 1266954.768
222 | 2711595.9368 | 1266931.6313
223 | 2711594.1248 | 1266970.1418
224 | 2711595.9438 | 1266926.9569
225 | 2711607.2919 | 1266930.7105
226 | 2711552.5674 | 1266962.8415
227 | 2711595.9509 | 1266922.2269
228 | 2711613.724 | 1266931.3573
229 | 2711522.0591 | 1266945.0315
230 | 2711538.2547 | 1266964.8715
231 | 2711582.9711 | 1267034.7988
232 | 2711574.4645 | 1266991.7631
233 | 2711728.7072 | 1267003.4439
234 | 2711713.182 | 1267007.2869
235 | 2711581.5603 | 1267061.6365
236 | 2711640.2886 | 1266954.0896
237 | 2711284.4408 | 1267139.513
238 | 2711283.6879 | 1267141.429
239 | 2711279.1348 | 1267153.0161
240 | 2711279.4926 | 1267152.1054
241 | 2711272.8496 | 1267169.0108
242 | 2711270.3195 | 1267175.4496
243 | 2711261.8317 | 1267196.8668
244 | 2711291.5531 | 1267183.9832
245 | 2711259.7424 | 1267171.2229
246 | 2711256.4919 | 1267210.3408
247 | 2711292.0155 | 1267184.1691
248 | 2711250.9186 | 1267224.4039
249 | 2711251.816 | 1267222.1395
250 | 2711101.5136 | 1267148.2164
251 | 2711099.6606 | 1267154.0443
252 | 2711097.7583 | 1267160.0276
253 | 2711097.1762 | 1267161.8584
254 | 2711292.1339 | 1267184.2167
255 | 2711292.3662 | 1267184.31
256 | 2711113.7756 | 1267209.8889

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1