## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4746-3_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4746-3_0_6_node_26 | 0.4 | n |  | TRUE
2 | bus_LV_4746-3_0_6_node_29 | 0.4 | n |  | TRUE
3 | bus_LV_4746-3_0_6_node_25 | 0.4 | n |  | TRUE
4 | bus_LV_4746-3_0_6_node_27 | 0.4 | n |  | TRUE
5 | bus_LV_4746-3_0_6_node_1 | 0.4 | n |  | TRUE
6 | bus_LV_4746-3_0_6_node_2 | 0.4 | n |  | TRUE
7 | bus_LV_4746-3_0_6_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_4746-3_0_6_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_4746-3_0_6_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_4746-3_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_4746-3_0_6_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_4746-3_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_4746-3_0_6_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_4746-3_0_6_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_4746-3_0_6_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_4746-3_0_6_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_4746-3_0_6_node_74 | 0.4 | n |  | TRUE
18 | bus_LV_4746-3_0_6_node_76 | 0.4 | n |  | TRUE
19 | bus_LV_4746-3_0_6_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_4746-3_0_6_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_4746-3_0_6_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_4746-3_0_6_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_4746-3_0_6_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_4746-3_0_6_node_75 | 0.4 | n |  | TRUE
25 | bus_LV_4746-3_0_6_node_73 | 0.4 | n |  | TRUE
26 | bus_LV_4746-3_0_6_node_77 | 0.4 | n |  | TRUE
27 | bus_LV_4746-3_0_6_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_4746-3_0_6_node_10 | 0.4 | n |  | TRUE
29 | bus_LV_4746-3_0_6_node_11 | 0.4 | n |  | TRUE
30 | bus_LV_4746-3_0_6_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_4746-3_0_6_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_4746-3_0_6_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_4746-3_0_6_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_4746-3_0_6_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_4746-3_0_6_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_4746-3_0_6_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_4746-3_0_6_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_4746-3_0_6_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_4746-3_0_6_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_4746-3_0_6_node_43 | 0.4 | n |  | TRUE
41 | bus_LV_4746-3_0_6_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_4746-3_0_6_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_4746-3_0_6_node_125 | 0.4 | n |  | TRUE
44 | bus_LV_4746-3_0_6_node_157 | 0.4 | n |  | TRUE
45 | bus_LV_4746-3_0_6_node_126 | 0.4 | n |  | TRUE
46 | bus_LV_4746-3_0_6_node_124 | 0.4 | n |  | TRUE
47 | bus_LV_4746-3_0_6_node_155 | 0.4 | n |  | TRUE
48 | bus_LV_4746-3_0_6_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_4746-3_0_6_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_4746-3_0_6_node_151 | 0.4 | n |  | TRUE
51 | bus_LV_4746-3_0_6_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_4746-3_0_6_node_152 | 0.4 | n |  | TRUE
53 | bus_LV_4746-3_0_6_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_4746-3_0_6_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_4746-3_0_6_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_4746-3_0_6_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_4746-3_0_6_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_4746-3_0_6_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_4746-3_0_6_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_4746-3_0_6_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_4746-3_0_6_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_4746-3_0_6_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_4746-3_0_6_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_4746-3_0_6_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_4746-3_0_6_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_4746-3_0_6_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_4746-3_0_6_node_55 | 0.4 | n |  | TRUE
68 | bus_LV_4746-3_0_6_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_4746-3_0_6_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_4746-3_0_6_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_4746-3_0_6_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_4746-3_0_6_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_4746-3_0_6_node_104 | 0.4 | n |  | TRUE
74 | bus_LV_4746-3_0_6_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_4746-3_0_6_node_62 | 0.4 | n |  | TRUE
76 | bus_LV_4746-3_0_6_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_4746-3_0_6_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_4746-3_0_6_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_4746-3_0_6_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_4746-3_0_6_node_95 | 0.4 | n |  | TRUE
81 | bus_LV_4746-3_0_6_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_4746-3_0_6_node_67 | 0.4 | n |  | TRUE
83 | bus_LV_4746-3_0_6_node_96 | 0.4 | n |  | TRUE
84 | bus_LV_4746-3_0_6_node_93 | 0.4 | n |  | TRUE
85 | bus_LV_4746-3_0_6_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_4746-3_0_6_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_4746-3_0_6_node_71 | 0.4 | n |  | TRUE
88 | bus_LV_4746-3_0_6_node_72 | 0.4 | n |  | TRUE
89 | bus_LV_4746-3_0_6_node_94 | 0.4 | n |  | TRUE
90 | bus_LV_4746-3_0_6_node_78 | 0.4 | n |  | TRUE
91 | bus_LV_4746-3_0_6_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_4746-3_0_6_node_80 | 0.4 | n |  | TRUE
93 | bus_LV_4746-3_0_6_node_81 | 0.4 | n |  | TRUE
94 | bus_LV_4746-3_0_6_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_4746-3_0_6_node_170 | 0.4 | n |  | TRUE
96 | bus_LV_4746-3_0_6_node_169 | 0.4 | n |  | TRUE
97 | bus_LV_4746-3_0_6_node_83 | 0.4 | n |  | TRUE
98 | bus_LV_4746-3_0_6_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_4746-3_0_6_node_85 | 0.4 | n |  | TRUE
100 | bus_LV_4746-3_0_6_node_86 | 0.4 | n |  | TRUE
101 | bus_LV_4746-3_0_6_node_87 | 0.4 | n |  | TRUE
102 | bus_LV_4746-3_0_6_node_88 | 0.4 | n |  | TRUE
103 | bus_LV_4746-3_0_6_node_89 | 0.4 | n |  | TRUE
104 | bus_LV_4746-3_0_6_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_4746-3_0_6_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_4746-3_0_6_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_4746-3_0_6_node_98 | 0.4 | n |  | TRUE
108 | bus_LV_4746-3_0_6_node_171 | 0.4 | n |  | TRUE
109 | bus_LV_4746-3_0_6_node_97 | 0.4 | n |  | TRUE
110 | bus_LV_4746-3_0_6_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_4746-3_0_6_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_4746-3_0_6_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_4746-3_0_6_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_4746-3_0_6_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_4746-3_0_6_node_105 | 0.4 | n |  | TRUE
116 | bus_LV_4746-3_0_6_node_107 | 0.4 | n |  | TRUE
117 | bus_LV_4746-3_0_6_node_106 | 0.4 | n |  | TRUE
118 | bus_LV_4746-3_0_6_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_4746-3_0_6_node_110 | 0.4 | n |  | TRUE
120 | bus_LV_4746-3_0_6_node_144 | 0.4 | n |  | TRUE
121 | bus_LV_4746-3_0_6_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_4746-3_0_6_node_131 | 0.4 | n |  | TRUE
123 | bus_LV_4746-3_0_6_node_132 | 0.4 | n |  | TRUE
124 | bus_LV_4746-3_0_6_node_133 | 0.4 | n |  | TRUE
125 | bus_LV_4746-3_0_6_node_134 | 0.4 | n |  | TRUE
126 | bus_LV_4746-3_0_6_node_135 | 0.4 | n |  | TRUE
127 | bus_LV_4746-3_0_6_node_136 | 0.4 | n |  | TRUE
128 | bus_LV_4746-3_0_6_node_137 | 0.4 | n |  | TRUE
129 | bus_LV_4746-3_0_6_node_138 | 0.4 | n |  | TRUE
130 | bus_LV_4746-3_0_6_node_139 | 0.4 | n |  | TRUE
131 | bus_LV_4746-3_0_6_node_149 | 0.4 | n |  | TRUE
132 | bus_LV_4746-3_0_6_node_147 | 0.4 | n |  | TRUE
133 | bus_LV_4746-3_0_6_node_142 | 0.4 | n |  | TRUE
134 | bus_LV_4746-3_0_6_node_143 | 0.4 | n |  | TRUE
135 | bus_LV_4746-3_0_6_node_148 | 0.4 | n |  | TRUE
136 | bus_LV_4746-3_0_6_node_112 | 0.4 | n |  | TRUE
137 | bus_LV_4746-3_0_6_node_113 | 0.4 | n |  | TRUE
138 | bus_LV_4746-3_0_6_node_114 | 0.4 | n |  | TRUE
139 | bus_LV_4746-3_0_6_node_115 | 0.4 | n |  | TRUE
140 | bus_LV_4746-3_0_6_node_116 | 0.4 | n |  | TRUE
141 | bus_LV_4746-3_0_6_node_118 | 0.4 | n |  | TRUE
142 | bus_LV_4746-3_0_6_node_117 | 0.4 | n |  | TRUE
143 | bus_LV_4746-3_0_6_node_119 | 0.4 | n |  | TRUE
144 | bus_LV_4746-3_0_6_node_120 | 0.4 | n |  | TRUE
145 | bus_LV_4746-3_0_6_node_121 | 0.4 | n |  | TRUE
146 | bus_LV_4746-3_0_6_node_122 | 0.4 | n |  | TRUE
147 | bus_LV_4746-3_0_6_node_140 | 0.4 | n |  | TRUE
148 | bus_LV_4746-3_0_6_node_141 | 0.4 | n |  | TRUE
149 | bus_LV_4746-3_0_6_node_150 | 0.4 | n |  | TRUE
150 | bus_LV_4746-3_0_6_node_123 | 0.4 | n |  | TRUE
151 | bus_LV_4746-3_0_6_node_130 | 0.4 | n |  | TRUE
152 | bus_LV_4746-3_0_6_node_128 | 0.4 | n |  | TRUE
153 | bus_LV_4746-3_0_6_node_127 | 0.4 | n |  | TRUE
154 | bus_LV_4746-3_0_6_node_129 | 0.4 | n |  | TRUE
155 | bus_LV_4746-3_0_6_node_145 | 0.4 | n |  | TRUE
156 | bus_LV_4746-3_0_6_node_146 | 0.4 | n |  | TRUE
157 | bus_LV_4746-3_0_6_node_153 | 0.4 | n |  | TRUE
158 | bus_LV_4746-3_0_6_node_154 | 0.4 | n |  | TRUE
159 | bus_LV_4746-3_0_6_node_156 | 0.4 | n |  | TRUE
160 | bus_LV_4746-3_0_6_node_158 | 0.4 | n |  | TRUE
161 | bus_LV_4746-3_0_6_node_161 | 0.4 | n |  | TRUE
162 | bus_LV_4746-3_0_6_node_159 | 0.4 | n |  | TRUE
163 | bus_LV_4746-3_0_6_node_162 | 0.4 | n |  | TRUE
164 | bus_LV_4746-3_0_6_node_160 | 0.4 | n |  | TRUE
165 | bus_LV_4746-3_0_6_node_167 | 0.4 | n |  | TRUE
166 | bus_LV_4746-3_0_6_node_168 | 0.4 | n |  | TRUE
167 | bus_LV_4746-3_0_6_node_163 | 0.4 | n |  | TRUE
168 | bus_LV_4746-3_0_6_node_164 | 0.4 | n |  | TRUE
169 | bus_LV_4746-3_0_6_node_165 | 0.4 | n |  | TRUE
170 | bus_LV_4746-3_0_6_node_166 | 0.4 | n |  | TRUE
171 | bus_MV_443_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4746-3_0_6_load_0 | 0 | 0.0026204 | 0.00065673 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4746-3_0_6_load_26 | 1 | 0.0088271 | 0.0022123 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4746-3_0_6_load_29 | 2 | 0.013352 | 0.0033463 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4746-3_0_6_load_25 | 3 | 0.047585 | 0.011926 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4746-3_0_6_load_27 | 4 | 0.0074838 | 0.0018756 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4746-3_0_6_load_1 | 5 | 0.005948 | 0.0014907 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4746-3_0_6_load_4 | 8 | 0.0064335 | 0.0016124 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4746-3_0_6_load_8 | 10 | 0.011284 | 0.0028282 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4746-3_0_6_load_32 | 13 | 0.0025021 | 0.00062708 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4746-3_0_6_load_31 | 14 | 0.0066336 | 0.0016625 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4746-3_0_6_load_21 | 16 | 0.0032091 | 0.00080429 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4746-3_0_6_load_76 | 18 | 0.011602 | 0.0029077 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4746-3_0_6_load_23 | 19 | 0.0028647 | 0.00071797 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4746-3_0_6_load_14 | 20 | 0.01167 | 0.0029248 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4746-3_0_6_load_33 | 21 | 0.0028627 | 0.00071745 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4746-3_0_6_load_30 | 22 | 0.010855 | 0.0027206 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4746-3_0_6_load_75 | 24 | 0.0030801 | 0.00077194 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4746-3_0_6_load_73 | 25 | 0.0071392 | 0.0017893 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4746-3_0_6_load_77 | 26 | 0.011339 | 0.0028418 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4746-3_0_6_load_12 | 27 | 0.0017214 | 0.00043141 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4746-3_0_6_load_10 | 28 | 0.003579 | 0.00089697 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4746-3_0_6_load_11 | 29 | 0.0033636 | 0.00084299 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4746-3_0_6_load_15 | 31 | 0.0035483 | 0.00088928 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4746-3_0_6_load_16 | 32 | 0.0041016 | 0.001028 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4746-3_0_6_load_17 | 33 | 0.0094151 | 0.0023596 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4746-3_0_6_load_24 | 34 | 0.014664 | 0.0036751 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4746-3_0_6_load_18 | 35 | 0.0058143 | 0.0014572 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4746-3_0_6_load_19 | 36 | 0.0065299 | 0.0016366 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4746-3_0_6_load_22 | 37 | 0.0046006 | 0.001153 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4746-3_0_6_load_47 | 39 | 0.013564 | 0.0033994 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4746-3_0_6_load_28 | 41 | 0.0071468 | 0.0017912 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4746-3_0_6_load_157 | 44 | 0.0016114 | 0.00040387 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4746-3_0_6_load_126 | 45 | 0.0014352 | 0.0003597 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4746-3_0_6_load_124 | 46 | 0.00073037 | 0.00018305 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4746-3_0_6_load_35 | 48 | 0.0027799 | 0.00069672 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4746-3_0_6_load_36 | 49 | 0.00088911 | 0.00022283 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4746-3_0_6_load_151 | 50 | 0.001958 | 0.00049072 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4746-3_0_6_load_37 | 51 | 0.0037561 | 0.00094137 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4746-3_0_6_load_152 | 52 | 0.0011417 | 0.00028614 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4746-3_0_6_load_38 | 53 | 0.0027215 | 0.00068206 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4746-3_0_6_load_39 | 54 | 0.0012578 | 0.00031523 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4746-3_0_6_load_40 | 55 | 0.0017971 | 0.0004504 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4746-3_0_6_load_45 | 56 | 0.014403 | 0.0036097 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4746-3_0_6_load_41 | 57 | 0.008548 | 0.0021423 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4746-3_0_6_load_42 | 58 | 0.0019606 | 0.00049137 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4746-3_0_6_load_44 | 59 | 0.0036444 | 0.00091337 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4746-3_0_6_load_50 | 60 | 0.0034468 | 0.00086385 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4746-3_0_6_load_48 | 61 | 0.0027098 | 0.00067914 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4746-3_0_6_load_53 | 63 | 0.0013516 | 0.00033874 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4746-3_0_6_load_51 | 64 | 0.00062107 | 0.00015565 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4746-3_0_6_load_52 | 65 | 0.0012131 | 0.00030403 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4746-3_0_6_load_54 | 66 | 0.0004191 | 0.00010504 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4746-3_0_6_load_55 | 67 | 0.0010063 | 0.00025221 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4746-3_0_6_load_56 | 68 | 0.00069548 | 0.0001743 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4746-3_0_6_load_57 | 69 | 0.0012966 | 0.00032496 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4746-3_0_6_load_58 | 70 | 0.0010309 | 0.00025838 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4746-3_0_6_load_59 | 71 | 0.00033652 | 8.434e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4746-3_0_6_load_60 | 72 | 0.0001348 | 3.3785e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4746-3_0_6_load_104 | 73 | 0.00023474 | 5.8831e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4746-3_0_6_load_61 | 74 | 0.0009992 | 0.00025042 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4746-3_0_6_load_62 | 75 | 0.0010983 | 0.00027525 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4746-3_0_6_load_63 | 76 | 0.0010959 | 0.00027466 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4746-3_0_6_load_64 | 77 | 0.0015565 | 0.0003901 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4746-3_0_6_load_65 | 78 | 0.0020977 | 0.00052574 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4746-3_0_6_load_95 | 80 | 0.0007741 | 0.00019401 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4746-3_0_6_load_70 | 81 | 0.00090409 | 0.00022659 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4746-3_0_6_load_67 | 82 | 0.0012458 | 0.00031222 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4746-3_0_6_load_96 | 83 | 0.00050418 | 0.00012636 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4746-3_0_6_load_93 | 84 | 0.0020924 | 0.00052441 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4746-3_0_6_load_68 | 85 | 0.0024761 | 0.00062056 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4746-3_0_6_load_69 | 86 | 0.0012956 | 0.00032472 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4746-3_0_6_load_71 | 87 | 0.0022127 | 0.00055454 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4746-3_0_6_load_72 | 88 | 0.0016497 | 0.00041346 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4746-3_0_6_load_94 | 89 | 0.0020343 | 0.00050985 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4746-3_0_6_load_78 | 90 | 0.002249 | 0.00056366 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4746-3_0_6_load_79 | 91 | 0.0028395 | 0.00071166 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4746-3_0_6_load_81 | 93 | 0.00051717 | 0.00012961 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4746-3_0_6_load_82 | 94 | 0.0021946 | 0.00055003 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4746-3_0_6_load_170 | 95 | 0.00052728 | 0.00013215 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4746-3_0_6_load_169 | 96 | 0.00051187 | 0.00012829 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4746-3_0_6_load_83 | 97 | 0.00066142 | 0.00016577 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4746-3_0_6_load_84 | 98 | 0.0012479 | 0.00031276 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4746-3_0_6_load_85 | 99 | 0.0015262 | 0.0003825 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4746-3_0_6_load_86 | 100 | 0.00061307 | 0.00015365 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4746-3_0_6_load_87 | 101 | 0.00069457 | 0.00017408 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4746-3_0_6_load_88 | 102 | 0.000684 | 0.00017143 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4746-3_0_6_load_89 | 103 | 0.0010148 | 0.00025433 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4746-3_0_6_load_90 | 104 | 0.00067145 | 0.00016828 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4746-3_0_6_load_91 | 105 | 0.0002455 | 6.1528e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4746-3_0_6_load_98 | 107 | 0.0001695 | 4.248e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4746-3_0_6_load_171 | 108 | 0.00015883 | 3.9806e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4746-3_0_6_load_97 | 109 | 0.00032125 | 8.0514e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4746-3_0_6_load_99 | 110 | 0.00031797 | 7.9692e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4746-3_0_6_load_100 | 111 | 0.0021531 | 0.00053961 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4746-3_0_6_load_101 | 112 | 0.00018526 | 4.643e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4746-3_0_6_load_102 | 113 | 0.00016512 | 4.1383e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4746-3_0_6_load_107 | 116 | 0.0031605 | 0.00079209 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4746-3_0_6_load_106 | 117 | 0.0012715 | 0.00031868 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4746-3_0_6_load_109 | 118 | 0.0027434 | 0.00068755 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4746-3_0_6_load_110 | 119 | 0.0013315 | 0.0003337 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4746-3_0_6_load_144 | 120 | 0.0018662 | 0.00046771 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4746-3_0_6_load_111 | 121 | 0.0016474 | 0.00041287 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4746-3_0_6_load_131 | 122 | 0.003675 | 0.00092104 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4746-3_0_6_load_134 | 125 | 0.0026382 | 0.0006612 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4746-3_0_6_load_135 | 126 | 0.002329 | 0.0005837 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4746-3_0_6_load_136 | 127 | 0.0027522 | 0.00068976 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4746-3_0_6_load_137 | 128 | 0.00061337 | 0.00015372 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4746-3_0_6_load_138 | 129 | 0.0025096 | 0.00062896 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4746-3_0_6_load_139 | 130 | 0.0027592 | 0.00069153 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4746-3_0_6_load_149 | 131 | 0.00096264 | 0.00024126 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4746-3_0_6_load_142 | 133 | 0.0031507 | 0.00078963 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4746-3_0_6_load_143 | 134 | 0.00076352 | 0.00019136 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4746-3_0_6_load_112 | 136 | 0.0016209 | 0.00040624 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4746-3_0_6_load_113 | 137 | 0.0013674 | 0.00034269 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4746-3_0_6_load_114 | 138 | 0.0012947 | 0.00032447 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4746-3_0_6_load_115 | 139 | 0.0011099 | 0.00027817 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4746-3_0_6_load_116 | 140 | 0.0013411 | 0.00033611 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4746-3_0_6_load_118 | 141 | 0.0010361 | 0.00025968 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4746-3_0_6_load_117 | 142 | 0.0022526 | 0.00056456 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4746-3_0_6_load_120 | 144 | 0.0010591 | 0.00026544 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4746-3_0_6_load_121 | 145 | 0.00062713 | 0.00015717 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4746-3_0_6_load_122 | 146 | 0.0014559 | 0.00036488 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4746-3_0_6_load_140 | 147 | 0.0015008 | 0.00037612 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4746-3_0_6_load_141 | 148 | 0.00078734 | 0.00019733 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4746-3_0_6_load_150 | 149 | 0.0020557 | 0.0005152 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4746-3_0_6_load_123 | 150 | 0.00068501 | 0.00017168 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4746-3_0_6_load_128 | 152 | 0.0018584 | 0.00046576 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4746-3_0_6_load_127 | 153 | 0.00080529 | 0.00020182 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4746-3_0_6_load_129 | 154 | 0.0014586 | 0.00036555 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4746-3_0_6_load_145 | 155 | 0.006687 | 0.0016759 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4746-3_0_6_load_146 | 156 | 0.0032117 | 0.00080493 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4746-3_0_6_load_153 | 157 | 0.0030619 | 0.00076739 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4746-3_0_6_load_154 | 158 | 0.0013267 | 0.0003325 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4746-3_0_6_load_156 | 159 | 0.00086885 | 0.00021775 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4746-3_0_6_load_158 | 160 | 0.00086853 | 0.00021767 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4746-3_0_6_load_161 | 161 | 0.00094357 | 0.00023648 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4746-3_0_6_load_159 | 162 | 0.0035546 | 0.00089087 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4746-3_0_6_load_162 | 163 | 0.00048149 | 0.00012067 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4746-3_0_6_load_160 | 164 | 0.002106 | 0.00052782 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_4746-3_0_6_load_167 | 165 | 0.00090877 | 0.00022776 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_4746-3_0_6_load_168 | 166 | 0.00040409 | 0.00010128 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_4746-3_0_6_load_163 | 167 | 0.0015688 | 0.00039319 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_4746-3_0_6_load_164 | 168 | 0.00050223 | 0.00012587 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_4746-3_0_6_load_165 | 169 | 0.0018486 | 0.00046331 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_4746-3_0_6_load_166 | 170 | 0.00097338 | 0.00024395 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4746-3_0_6_line_0 |  | 0 | 1 | 0.16961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4746-3_0_6_line_1 |  | 1 | 2 | 0.15924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4746-3_0_6_line_2 |  | 1 | 3 | 0.064686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4746-3_0_6_line_3 |  | 2 | 4 | 0.0039479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4746-3_0_6_line_4 |  | 4 | 41 | 0.026771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4746-3_0_6_line_5 |  | 5 | 6 | 0.03422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_4746-3_0_6_line_6 |  | 5 | 7 | 0.053872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_4746-3_0_6_line_7 |  | 6 | 8 | 0.014373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_4746-3_0_6_line_8 |  | 7 | 9 | 0.039944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4746-3_0_6_line_9 |  | 7 | 10 | 0.050026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_4746-3_0_6_line_10 |  | 8 | 11 | 0.027385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_4746-3_0_6_line_11 |  | 9 | 13 | 0.0093487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4746-3_0_6_line_12 |  | 9 | 14 | 0.018974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4746-3_0_6_line_13 |  | 10 | 18 | 0.026958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_4746-3_0_6_line_14 |  | 11 | 12 | 0.014909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_4746-3_0_6_line_15 |  | 12 | 19 | 0.030697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4746-3_0_6_line_16 |  | 12 | 20 | 0.027857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_4746-3_0_6_line_17 |  | 13 | 21 | 0.03609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4746-3_0_6_line_18 |  | 14 | 22 | 0.0087877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4746-3_0_6_line_19 |  | 15 | 16 | 0.016157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_4746-3_0_6_line_20 |  | 15 | 17 | 0.026902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_4746-3_0_6_line_21 |  | 16 | 23 | 0.013354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_4746-3_0_6_line_22 |  | 17 | 24 | 0.01794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_4746-3_0_6_line_23 |  | 17 | 25 | 0.017866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_4746-3_0_6_line_24 |  | 18 | 26 | 0.031755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_4746-3_0_6_line_25 |  | 20 | 27 | 0.012913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_4746-3_0_6_line_26 |  | 22 | 41 | 0.027689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4746-3_0_6_line_27 |  | 23 | 37 | 0.017726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4746-3_0_6_line_28 |  | 23 | 36 | 0.0033827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_4746-3_0_6_line_29 |  | 24 | 62 | 0.0017815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_4746-3_0_6_line_30 |  | 25 | 88 | 0.028914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_4746-3_0_6_line_31 |  | 26 | 90 | 0.02749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_4746-3_0_6_line_32 |  | 27 | 28 | 0.027952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_4746-3_0_6_line_33 |  | 28 | 29 | 0.014138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_4746-3_0_6_line_34 |  | 29 | 30 | 0.012797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_4746-3_0_6_line_35 |  | 30 | 31 | 0.017602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_4746-3_0_6_line_36 |  | 30 | 32 | 0.033095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4746-3_0_6_line_37 |  | 31 | 33 | 0.0095751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_4746-3_0_6_line_38 |  | 32 | 34 | 0.027447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4746-3_0_6_line_39 |  | 33 | 35 | 0.013036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_4746-3_0_6_line_40 |  | 35 | 36 | 0.037524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_4746-3_0_6_line_41 |  | 38 | 39 | 0.01666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_4746-3_0_6_line_42 |  | 38 | 40 | 0.015092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_4746-3_0_6_line_43 |  | 39 | 61 | 0.0102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_4746-3_0_6_line_44 |  | 40 | 56 | 0.01232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4746-3_0_6_line_45 |  | 40 | 57 | 0.026266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4746-3_0_6_line_46 |  | 42 | 43 | 0.012164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_4746-3_0_6_line_47 |  | 42 | 44 | 0.038459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_4746-3_0_6_line_48 |  | 43 | 45 | 0.066349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4746-3_0_6_line_49 |  | 43 | 46 | 0.076832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_4746-3_0_6_line_50 |  | 44 | 47 | 0.011997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_4746-3_0_6_line_51 |  | 45 | 151 | 0.0043582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4746-3_0_6_line_52 |  | 46 | 150 | 0.016846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_4746-3_0_6_line_53 |  | 47 | 160 | 0.0066703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_4746-3_0_6_line_54 |  | 47 | 157 | 0.029581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4746-3_0_6_line_55 |  | 48 | 49 | 0.011792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4746-3_0_6_line_56 |  | 48 | 50 | 0.078541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4746-3_0_6_line_57 |  | 49 | 51 | 0.026019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4746-3_0_6_line_58 |  | 50 | 52 | 0.0012431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4746-3_0_6_line_59 |  | 51 | 53 | 0.0031984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4746-3_0_6_line_60 |  | 53 | 54 | 0.029113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4746-3_0_6_line_61 |  | 54 | 55 | 0.0035225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4746-3_0_6_line_62 |  | 55 | 56 | 0.0077132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4746-3_0_6_line_63 |  | 57 | 58 | 0.040537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4746-3_0_6_line_64 |  | 58 | 59 | 0.011056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4746-3_0_6_line_65 |  | 59 | 60 | 0.068072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4746-3_0_6_line_66 |  | 61 | 62 | 0.026491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_4746-3_0_6_line_67 |  | 62 | 63 | 0.024803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4746-3_0_6_line_68 |  | 63 | 64 | 0.012834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4746-3_0_6_line_69 |  | 64 | 65 | 0.017295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4746-3_0_6_line_70 |  | 65 | 66 | 0.012107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4746-3_0_6_line_71 |  | 66 | 67 | 0.011405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4746-3_0_6_line_72 |  | 67 | 68 | 0.004784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4746-3_0_6_line_73 |  | 68 | 69 | 0.023897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4746-3_0_6_line_74 |  | 69 | 70 | 0.0043879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4746-3_0_6_line_75 |  | 70 | 71 | 0.028157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4746-3_0_6_line_76 |  | 71 | 72 | 0.012083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4746-3_0_6_line_77 |  | 72 | 73 | 0.0032623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4746-3_0_6_line_78 |  | 74 | 75 | 0.010108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4746-3_0_6_line_79 |  | 74 | 76 | 0.022256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4746-3_0_6_line_80 |  | 75 | 77 | 0.015346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_4746-3_0_6_line_81 |  | 76 | 78 | 0.0034202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4746-3_0_6_line_82 |  | 77 | 79 | 0.014309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_4746-3_0_6_line_83 |  | 78 | 80 | 0.010272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4746-3_0_6_line_84 |  | 79 | 81 | 0.01299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4746-3_0_6_line_85 |  | 79 | 82 | 0.018274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_4746-3_0_6_line_86 |  | 80 | 83 | 0.014474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4746-3_0_6_line_87 |  | 81 | 84 | 0.025496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4746-3_0_6_line_88 |  | 82 | 85 | 0.0040589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_4746-3_0_6_line_89 |  | 83 | 109 | 0.0026007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4746-3_0_6_line_90 |  | 84 | 89 | 0.026306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4746-3_0_6_line_91 |  | 85 | 86 | 0.020857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_4746-3_0_6_line_92 |  | 86 | 87 | 0.01092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_4746-3_0_6_line_93 |  | 87 | 88 | 0.012645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_4746-3_0_6_line_94 |  | 89 | 106 | 0.043016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4746-3_0_6_line_95 |  | 90 | 91 | 0.027576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_4746-3_0_6_line_96 |  | 91 | 92 | 0.020699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_4746-3_0_6_line_97 |  | 92 | 93 | 0.013798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_4746-3_0_6_line_98 |  | 92 | 94 | 0.052089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4746-3_0_6_line_99 |  | 93 | 95 | 0.015729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_4746-3_0_6_line_100 |  | 95 | 96 | 0.023791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_4746-3_0_6_line_101 |  | 96 | 166 | 0.026666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_4746-3_0_6_line_102 |  | 97 | 98 | 0.0094543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4746-3_0_6_line_103 |  | 97 | 99 | 0.009853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4746-3_0_6_line_104 |  | 98 | 100 | 0.01334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4746-3_0_6_line_105 |  | 99 | 101 | 0.004973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4746-3_0_6_line_106 |  | 100 | 102 | 0.017805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4746-3_0_6_line_107 |  | 102 | 103 | 0.0026554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4746-3_0_6_line_108 |  | 103 | 104 | 0.012822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4746-3_0_6_line_109 |  | 104 | 105 | 0.017669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4746-3_0_6_line_110 |  | 105 | 106 | 0.022367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4746-3_0_6_line_111 |  | 106 | 107 | 0.065124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4746-3_0_6_line_112 |  | 107 | 108 | 0.035605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4746-3_0_6_line_113 |  | 109 | 110 | 0.017455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4746-3_0_6_line_114 |  | 110 | 111 | 0.032452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4746-3_0_6_line_115 |  | 111 | 112 | 0.015993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4746-3_0_6_line_116 |  | 112 | 113 | 0.011108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4746-3_0_6_line_117 |  | 113 | 114 | 0.015808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4746-3_0_6_line_118 |  | 114 | 115 | 0.091113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4746-3_0_6_line_119 |  | 115 | 116 | 0.062162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4746-3_0_6_line_120 |  | 115 | 117 | 0.040516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4746-3_0_6_line_121 |  | 118 | 119 | 0.017378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4746-3_0_6_line_122 |  | 118 | 120 | 0.26583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4746-3_0_6_line_123 |  | 119 | 121 | 0.017786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4746-3_0_6_line_124 |  | 120 | 129 | 0.009105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4746-3_0_6_line_125 |  | 121 | 136 | 0.003551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4746-3_0_6_line_126 |  | 122 | 123 | 0.056832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4746-3_0_6_line_127 |  | 122 | 124 | 0.016495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4746-3_0_6_line_128 |  | 123 | 125 | 0.019013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4746-3_0_6_line_129 |  | 123 | 126 | 0.023805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4746-3_0_6_line_130 |  | 123 | 127 | 0.039292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4746-3_0_6_line_131 |  | 124 | 128 | 0.02461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4746-3_0_6_line_132 |  | 124 | 129 | 0.022654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4746-3_0_6_line_133 |  | 125 | 130 | 0.022482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4746-3_0_6_line_134 |  | 126 | 131 | 0.029464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4746-3_0_6_line_135 |  | 127 | 132 | 0.039792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4746-3_0_6_line_136 |  | 128 | 133 | 0.018226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4746-3_0_6_line_137 |  | 130 | 147 | 0.031642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4746-3_0_6_line_138 |  | 131 | 135 | 0.018336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4746-3_0_6_line_139 |  | 132 | 155 | 0.016588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4746-3_0_6_line_140 |  | 133 | 134 | 0.011671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4746-3_0_6_line_141 |  | 135 | 149 | 0.021239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4746-3_0_6_line_142 |  | 136 | 137 | 0.021647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4746-3_0_6_line_143 |  | 137 | 138 | 0.0088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4746-3_0_6_line_144 |  | 138 | 139 | 0.021468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
145 | LV_4746-3_0_6_line_145 |  | 139 | 140 | 0.0050562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
146 | LV_4746-3_0_6_line_146 |  | 140 | 141 | 0.014517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
147 | LV_4746-3_0_6_line_147 |  | 141 | 142 | 0.0099825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
148 | LV_4746-3_0_6_line_148 |  | 142 | 143 | 0.02057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
149 | LV_4746-3_0_6_line_149 |  | 143 | 144 | 0.050268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4746-3_0_6_line_150 |  | 143 | 145 | 0.020863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
151 | LV_4746-3_0_6_line_151 |  | 145 | 146 | 0.018082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
152 | LV_4746-3_0_6_line_152 |  | 146 | 150 | 0.0042311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
153 | LV_4746-3_0_6_line_153 |  | 147 | 148 | 0.0048186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4746-3_0_6_line_154 |  | 151 | 152 | 0.015263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4746-3_0_6_line_155 |  | 152 | 153 | 0.01326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4746-3_0_6_line_156 |  | 153 | 154 | 0.0060584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4746-3_0_6_line_157 |  | 155 | 156 | 0.036913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4746-3_0_6_line_158 |  | 157 | 158 | 0.0162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4746-3_0_6_line_159 |  | 158 | 159 | 0.00051201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4746-3_0_6_line_160 |  | 159 | 161 | 0.024546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4746-3_0_6_line_161 |  | 160 | 162 | 0.0078185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
162 | LV_4746-3_0_6_line_162 |  | 161 | 163 | 0.025192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4746-3_0_6_line_163 |  | 162 | 164 | 0.035473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
164 | LV_4746-3_0_6_line_164 |  | 163 | 167 | 0.024937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4746-3_0_6_line_165 |  | 164 | 165 | 6.7351e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
166 | LV_4746-3_0_6_line_166 |  | 165 | 166 | 0.02145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
167 | LV_4746-3_0_6_line_167 |  | 167 | 168 | 9.412e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4746-3_0_6_line_168 |  | 168 | 169 | 0.026145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4746-3_0_6_line_169 |  | 169 | 170 | 0.016683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4746-3_0_6_trafo_8 | 0.63 MVA 20/0.4 kV | 171 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2716831.3213 | 1259812.1127 | 2716736.0334 | 1259952.4274
1 | 2716814.2893 | 1259653.7817 | 2716831.3213 | 1259812.1127
2 | 2716894.274 | 1259826.0637 | 2716842.7523 | 1259812.6346 | 2716831.3213 | 1259812.1127
3 | 2716815.3686 | 1259649.9842 | 2716814.2893 | 1259653.7817
4 | 2716815.3686 | 1259649.9842 | 2716822.6874 | 1259624.2326
5 | 2716938.155 | 1259603.3152 | 2716910.4811 | 1259583.1858
6 | 2716869.8268 | 1259547.8729 | 2716889.6668 | 1259566.0138 | 2716908.4987 | 1259581.7439 | 2716910.4811 | 1259583.1858
7 | 2716938.155 | 1259603.3152 | 2716950.2988 | 1259611.0045
8 | 2716869.8268 | 1259547.8729 | 2716849.7089 | 1259564.0119 | 2716837.1514 | 1259570.7031
9 | 2716869.8268 | 1259547.8729 | 2716845.6351 | 1259519.4929 | 2716837.6889 | 1259509.5419
10 | 2716973.4353 | 1259625.6541 | 2716950.2988 | 1259611.0045
11 | 2716837.1514 | 1259570.7031 | 2716827.8191 | 1259570.1503
12 | 2716837.1514 | 1259570.7031 | 2716832.2632 | 1259589.0365
13 | 2716820.8668 | 1259488.4762 | 2716837.6889 | 1259509.5419
14 | 2716986.4385 | 1259633.0175 | 2716973.4353 | 1259625.6541
15 | 2716986.4385 | 1259633.0175 | 2717006.2583 | 1259643.385 | 2717013.4193 | 1259647.6402
16 | 2716986.4385 | 1259633.0175 | 2716991.6089 | 1259623.2001 | 2716992.7185 | 1259617.417 | 2716988.599 | 1259607.3553
17 | 2716791.8879 | 1259570.8071 | 2716806.7272 | 1259568.9009 | 2716827.8191 | 1259570.1503
18 | 2716829.9993 | 1259597.5275 | 2716832.2632 | 1259589.0365
19 | 2716897.3184 | 1259461.5745 | 2716910.7722 | 1259465.6215 | 2716912.43 | 1259466.9232
20 | 2716900.9743 | 1259434.9236 | 2716897.3184 | 1259461.5745
21 | 2716922.9334 | 1259475.1701 | 2716912.43 | 1259466.9232
22 | 2716900.9743 | 1259434.9236 | 2716903.4723 | 1259417.1584
23 | 2716900.9743 | 1259434.9236 | 2716890.7125 | 1259432.263 | 2716884.0159 | 1259429.446
24 | 2716820.8668 | 1259488.4762 | 2716801.0515 | 1259463.662
25 | 2716983.7064 | 1259595.4054 | 2716988.599 | 1259607.3553
26 | 2716829.9993 | 1259597.5275 | 2716825.7838 | 1259613.3378 | 2716822.6874 | 1259624.2326
27 | 2716922.9334 | 1259475.1701 | 2716928.4087 | 1259464.0352 | 2716931.1824 | 1259459.498
28 | 2716922.9334 | 1259475.1701 | 2716924.8707 | 1259477.9431
29 | 2716903.7203 | 1259415.3942 | 2716903.4723 | 1259417.1584
30 | 2716863.8843 | 1259408.8458 | 2716882.7788 | 1259428.9257 | 2716884.0159 | 1259429.446
31 | 2716783.8977 | 1259442.1808 | 2716801.0515 | 1259463.662
32 | 2716983.7064 | 1259595.4054 | 2716980.6 | 1259587.8185 | 2716972.4946 | 1259569.8047
33 | 2716972.4946 | 1259569.8047 | 2716969.0231 | 1259562.0895 | 2716967.5048 | 1259556.6188
34 | 2716964.0825 | 1259544.2876 | 2716967.5048 | 1259556.6188
35 | 2716964.0825 | 1259544.2876 | 2716958.7744 | 1259527.5047
36 | 2716964.0825 | 1259544.2876 | 2716995.1409 | 1259532.856
37 | 2716953.8264 | 1259519.3913 | 2716958.1787 | 1259525.6214 | 2716958.7744 | 1259527.5047
38 | 2716995.1409 | 1259532.856 | 2717015.2344 | 1259525.4602 | 2717021.2694 | 1259525.4039
39 | 2716946.3606 | 1259508.7045 | 2716953.8264 | 1259519.3913
40 | 2716946.3606 | 1259508.7045 | 2716924.8707 | 1259477.9431
41 | 2716955.0986 | 1259429.7663 | 2716939.0549 | 1259425.2784
42 | 2716955.0986 | 1259429.7663 | 2716969.6348 | 1259433.9795
43 | 2716939.0549 | 1259425.2784 | 2716929.2325 | 1259422.5307
44 | 2716969.6348 | 1259433.9795 | 2716981.4701 | 1259437.4005
45 | 2716969.6348 | 1259433.9795 | 2716970.7982 | 1259428.9092 | 2716972.0718 | 1259407.884
46 | 2716713.1706 | 1259582.9339 | 2716725.2978 | 1259581.6052
47 | 2716725.2978 | 1259581.6052 | 2716724.8335 | 1259577.626 | 2716726.2963 | 1259575.3306 | 2716737.2858 | 1259568.9974 | 2716738.3256 | 1259567.5055 | 2716737.9131 | 1259565.4845 | 2716736.9322 | 1259563.9972 | 2716729.285 | 1259559.5203 | 2716727.2394 | 1259558.1121 | 2716726.1653 | 1259556.3783
48 | 2716713.1706 | 1259582.9339 | 2716705.4316 | 1259599.9182 | 2716692.9777 | 1259617.7992 | 2716684.2963 | 1259623.3217 | 2716671.2797 | 1259626.9348 | 2716669.1854 | 1259626.8393
49 | 2716713.1706 | 1259582.9339 | 2716692.4442 | 1259579.8892 | 2716672.2946 | 1259573.2083 | 2716641.0785 | 1259558.1572
50 | 2716726.3267 | 1259544.3822 | 2716726.1653 | 1259556.3783
51 | 2716664.8317 | 1259626.6408 | 2716669.1854 | 1259626.8393
52 | 2716627.8142 | 1259548.0219 | 2716636.4382 | 1259555.9198 | 2716641.0785 | 1259558.1572
53 | 2716726.3267 | 1259544.3822 | 2716728.9943 | 1259543.6897 | 2716732.1417 | 1259541.3626
54 | 2716726.3267 | 1259544.3822 | 2716719.5971 | 1259546.1287 | 2716707.211 | 1259545.6729 | 2716697.4635 | 1259542.5558
55 | 2717062.0585 | 1259441.5495 | 2717050.2686 | 1259441.7783
56 | 2717062.0585 | 1259441.5495 | 2717074.2773 | 1259363.9653
57 | 2717024.2543 | 1259442.283 | 2717050.2686 | 1259441.7783
58 | 2717074.2773 | 1259363.9653 | 2717075.5162 | 1259364.0678
59 | 2717021.0565 | 1259442.345 | 2717024.2543 | 1259442.283
60 | 2717021.0565 | 1259442.345 | 2716999.9897 | 1259442.7538 | 2716992.2639 | 1259440.5206
61 | 2716988.8799 | 1259439.5424 | 2716992.2639 | 1259440.5206
62 | 2716988.8799 | 1259439.5424 | 2716981.4701 | 1259437.4005
63 | 2716972.0718 | 1259407.884 | 2716972.2986 | 1259404.1396 | 2716966.829 | 1259384.4811 | 2716967.3521 | 1259368.1088
64 | 2716967.3521 | 1259368.1088 | 2716967.6209 | 1259359.6975 | 2716968.0936 | 1259357.0998
65 | 2716990.8331 | 1259293.5041 | 2716972.6119 | 1259332.2724 | 2716968.0936 | 1259357.0998
66 | 2716903.7203 | 1259415.3942 | 2716929.2325 | 1259422.5307
67 | 2716903.7203 | 1259415.3942 | 2716906.6112 | 1259390.7607
68 | 2716907.9574 | 1259378.0079 | 2716907.9911 | 1259379.0026 | 2716906.6112 | 1259390.7607
69 | 2716907.9574 | 1259378.0079 | 2716907.371 | 1259360.7225
70 | 2716906.9606 | 1259348.6222 | 2716907.371 | 1259360.7225
71 | 2716906.9606 | 1259348.6222 | 2716906.8146 | 1259344.316 | 2716905.5556 | 1259337.3327
72 | 2716904.7068 | 1259332.6246 | 2716905.5556 | 1259337.3327
73 | 2716904.7068 | 1259332.6246 | 2716900.4671 | 1259309.1069
74 | 2716899.6886 | 1259304.7886 | 2716900.4671 | 1259309.1069
75 | 2716899.6886 | 1259304.7886 | 2716898.2192 | 1259296.6382 | 2716893.0059 | 1259277.4593
76 | 2716889.8366 | 1259265.7997 | 2716893.0059 | 1259277.4593
77 | 2716888.9809 | 1259262.6516 | 2716889.8366 | 1259265.7997
78 | 2716840.5735 | 1259327.3153 | 2716840.5735 | 1259327.3153 | 2716841.3015 | 1259332.0671 | 2716839.2244 | 1259336.9437
79 | 2716840.5735 | 1259327.3153 | 2716832.2526 | 1259306.6735
80 | 2716839.2244 | 1259336.9437 | 2716839.0797 | 1259337.2834 | 2716829.1476 | 1259348.4934
81 | 2716830.9739 | 1259303.5013 | 2716832.2526 | 1259306.6735
82 | 2716819.476 | 1259359.0374 | 2716825.823 | 1259352.2457 | 2716829.1476 | 1259348.4934
83 | 2716830.9739 | 1259303.5013 | 2716830.8128 | 1259303.1017 | 2716827.1268 | 1259293.9768
84 | 2716819.476 | 1259359.0374 | 2716810.396 | 1259349.7482
85 | 2716819.476 | 1259359.0374 | 2716831.2718 | 1259372.9943
86 | 2716827.1268 | 1259293.9768 | 2716821.7054 | 1259280.556
87 | 2716810.396 | 1259349.7482 | 2716792.5739 | 1259331.5154
88 | 2716831.2718 | 1259372.9943 | 2716833.8918 | 1259376.0943
89 | 2716820.7313 | 1259278.1447 | 2716821.7054 | 1259280.556
90 | 2716792.5739 | 1259331.5154 | 2716791.5769 | 1259330.4954 | 2716772.8754 | 1259314.0865
91 | 2716847.7361 | 1259391.6845 | 2716841.1735 | 1259384.7102 | 2716833.8918 | 1259376.0943
92 | 2716847.7361 | 1259391.6845 | 2716855.2192 | 1259399.6371
93 | 2716863.8843 | 1259408.8458 | 2716855.2192 | 1259399.6371
94 | 2716740.5414 | 1259285.7163 | 2716772.8754 | 1259314.0865
95 | 2716783.8977 | 1259442.1808 | 2716766.6903 | 1259420.6323
96 | 2716753.7743 | 1259404.458 | 2716766.6903 | 1259420.6323
97 | 2716753.7743 | 1259404.458 | 2716745.63 | 1259415.5958
98 | 2716753.7743 | 1259404.458 | 2716723.05 | 1259362.3955
99 | 2716742.1477 | 1259430.6878 | 2716742.2216 | 1259424.4029 | 2716745.63 | 1259415.5958 | 2716745.63 | 1259415.5958
100 | 2716740.7557 | 1259454.4126 | 2716742.0108 | 1259442.3365 | 2716742.1477 | 1259430.6878
101 | 2716739.392 | 1259481.0267 | 2716739.3992 | 1259480.2845 | 2716739.8886 | 1259462.7568 | 2716740.7557 | 1259454.4126
102 | 2716763.5708 | 1259359.5703 | 2716762.7967 | 1259357.6288 | 2716757.8901 | 1259352.1373
103 | 2716763.5708 | 1259359.5703 | 2716766.4031 | 1259366.6744 | 2716767.2103 | 1259368.7264
104 | 2716748.8346 | 1259342.3443 | 2716753.8855 | 1259347.6554 | 2716757.8901 | 1259352.1373
105 | 2716769.0308 | 1259373.3543 | 2716767.2103 | 1259368.7264
106 | 2716748.8346 | 1259342.3443 | 2716740.154 | 1259333.2165 | 2716736.304 | 1259329.7089
107 | 2716736.304 | 1259329.7089 | 2716734.3411 | 1259327.9207
108 | 2716725.0051 | 1259319.1723 | 2716725.2814 | 1259319.667 | 2716734.3411 | 1259327.9207
109 | 2716727.0253 | 1259303.5377 | 2716723.5645 | 1259308.1009 | 2716722.2228 | 1259314.1908 | 2716725.0051 | 1259319.1723
110 | 2716740.5414 | 1259285.7163 | 2716727.0253 | 1259303.5377
111 | 2716740.5414 | 1259285.7163 | 2716719.1775 | 1259265.255 | 2716707.9931 | 1259250.1102 | 2716694.9108 | 1259239.7062
112 | 2716694.9108 | 1259239.7062 | 2716676.9695 | 1259270.4603
113 | 2716820.7313 | 1259278.1447 | 2716815.1853 | 1259264.4152 | 2716815.0162 | 1259261.7726
114 | 2716815.0162 | 1259261.7726 | 2716814.782 | 1259258.1129 | 2716821.7845 | 1259253.2581 | 2716840.2535 | 1259244.919
115 | 2716854.8293 | 1259238.3378 | 2716840.2535 | 1259244.919
116 | 2716854.8293 | 1259238.3378 | 2716864.9533 | 1259233.7666
117 | 2716879.3609 | 1259227.2613 | 2716864.9533 | 1259233.7666
118 | 2716856.1295 | 1259139.1596 | 2716863.8442 | 1259168.8598 | 2716865.8231 | 1259176.3165 | 2716879.3609 | 1259227.2613
119 | 2716856.1295 | 1259139.1596 | 2716832.3629 | 1259144.128 | 2716798.6728 | 1259161.4482
120 | 2716856.1295 | 1259139.1596 | 2716859.8841 | 1259139.1782 | 2716887.4612 | 1259128.7359 | 2716894.4166 | 1259126.608
121 | 2716625.2272 | 1259380.4261 | 2716625.98 | 1259397.7876
122 | 2716625.2272 | 1259380.4261 | 2716381.8518 | 1259273.4856
123 | 2716625.98 | 1259397.7876 | 2716626.7506 | 1259415.5569
124 | 2716381.8518 | 1259273.4856 | 2716373.354 | 1259270.2163
125 | 2716626.7506 | 1259415.5569 | 2716626.9044 | 1259419.1046
126 | 2716283.6355 | 1259237.8909 | 2716301.7037 | 1259240.07 | 2716319.276 | 1259246.7545 | 2716337.2561 | 1259255.1222
127 | 2716352.2106 | 1259262.0818 | 2716337.2561 | 1259255.1222
128 | 2716283.6355 | 1259237.8909 | 2716277.6791 | 1259255.9471
129 | 2716283.6355 | 1259237.8909 | 2716259.9045 | 1259239.7611
130 | 2716283.6355 | 1259237.8909 | 2716270.9758 | 1259217.1909 | 2716261.29 | 1259205.7014
131 | 2716352.2106 | 1259262.0818 | 2716344.4027 | 1259285.4208
132 | 2716352.2106 | 1259262.0818 | 2716373.354 | 1259270.2163
133 | 2716277.6791 | 1259255.9471 | 2716277.1731 | 1259257.4808 | 2716265.8631 | 1259275.0174
134 | 2716230.5319 | 1259242.076 | 2716259.9045 | 1259239.7611
135 | 2716232.8545 | 1259178.0194 | 2716252.0912 | 1259194.7895 | 2716261.29 | 1259205.7014
136 | 2716338.6202 | 1259302.7055 | 2716344.4027 | 1259285.4208
137 | 2716243.854 | 1259297.4622 | 2716261.7123 | 1259281.4533 | 2716265.8631 | 1259275.0174
138 | 2716212.2326 | 1259242.4701 | 2716220.9567 | 1259242.8306 | 2716230.5319 | 1259242.076
139 | 2716232.8545 | 1259178.0194 | 2716219.8413 | 1259167.7323
140 | 2716338.6202 | 1259302.7055 | 2716334.9175 | 1259313.7735
141 | 2716212.2326 | 1259242.4701 | 2716191.0116 | 1259241.5984
142 | 2716626.9044 | 1259419.1046 | 2716627.0414 | 1259422.2634 | 2716627.3464 | 1259440.7463
143 | 2716627.3464 | 1259440.7463 | 2716627.4916 | 1259449.5451
144 | 2716627.8459 | 1259471.0105 | 2716627.4916 | 1259449.5451
145 | 2716627.8459 | 1259471.0105 | 2716627.9293 | 1259476.066
146 | 2716627.9293 | 1259476.066 | 2716627.9585 | 1259477.8295 | 2716626.0444 | 1259487.3334 | 2716624.1459 | 1259489.7308
147 | 2716617.9487 | 1259497.5567 | 2716624.1459 | 1259489.7308
148 | 2716604.1823 | 1259512.8024 | 2716612.83 | 1259504.0208 | 2716617.9487 | 1259497.5567
149 | 2716604.1823 | 1259512.8024 | 2716585.0903 | 1259505.62 | 2716555.3792 | 1259508.6899
150 | 2716604.1823 | 1259512.8024 | 2716613.1127 | 1259531.6575
151 | 2716613.1127 | 1259531.6575 | 2716615.539 | 1259536.7803 | 2716624.6939 | 1259545.1643
152 | 2716624.6939 | 1259545.1643 | 2716627.8142 | 1259548.0219
153 | 2716240.266 | 1259300.6785 | 2716243.854 | 1259297.4622
154 | 2716664.8317 | 1259626.6408 | 2716664.319 | 1259611.74 | 2716664.2664 | 1259611.3902
155 | 2716660.7373 | 1259598.7693 | 2716663.0726 | 1259603.4527 | 2716664.2664 | 1259611.3902
156 | 2716655.9552 | 1259595.0495 | 2716660.7373 | 1259598.7693
157 | 2716219.8413 | 1259167.7323 | 2716215.1244 | 1259164.0035 | 2716198.7021 | 1259144.0527 | 2716195.3526 | 1259140.2598
158 | 2716697.4635 | 1259542.5558 | 2716692.0629 | 1259537.3225 | 2716691.8581 | 1259528.6456
159 | 2716691.8581 | 1259528.6456 | 2716691.846 | 1259528.1337
160 | 2716691.846 | 1259528.1337 | 2716691.2669 | 1259503.5943
161 | 2716732.1417 | 1259541.3626 | 2716738.4284 | 1259536.7142
162 | 2716691.2669 | 1259503.5943 | 2716690.6726 | 1259478.4098
163 | 2716740.6796 | 1259502.4137 | 2716743.9158 | 1259519.9858 | 2716738.4284 | 1259536.7142 | 2716738.4284 | 1259536.7142
164 | 2716690.6726 | 1259478.4098 | 2716690.0843 | 1259453.4792
165 | 2716740.6796 | 1259502.4137 | 2716740.6674 | 1259502.3475
166 | 2716740.6674 | 1259502.3475 | 2716739.258 | 1259494.6942 | 2716739.392 | 1259481.0267
167 | 2716690.0843 | 1259453.4792 | 2716690.082 | 1259453.3851
168 | 2716690.082 | 1259453.3851 | 2716689.4652 | 1259427.2474
169 | 2716689.4652 | 1259427.2474 | 2716689.4186 | 1259425.2734 | 2716687.7927 | 1259417.8793 | 2716684.7196 | 1259411.4365

## bus_geodata
| x | y | coords
0 | 2716736.0334 | 1259952.4274
1 | 2716831.3213 | 1259812.1127
2 | 2716814.2893 | 1259653.7817
3 | 2716894.274 | 1259826.0637
4 | 2716815.3686 | 1259649.9842
5 | 2716910.4811 | 1259583.1858
6 | 2716938.155 | 1259603.3152
7 | 2716869.8268 | 1259547.8729
8 | 2716950.2988 | 1259611.0045
9 | 2716837.1514 | 1259570.7031
10 | 2716837.6889 | 1259509.5419
11 | 2716973.4353 | 1259625.6541
12 | 2716986.4385 | 1259633.0175
13 | 2716827.8191 | 1259570.1503
14 | 2716832.2632 | 1259589.0365
15 | 2716897.3184 | 1259461.5745
16 | 2716912.43 | 1259466.9232
17 | 2716900.9743 | 1259434.9236
18 | 2716820.8668 | 1259488.4762
19 | 2717013.4193 | 1259647.6402
20 | 2716988.599 | 1259607.3553
21 | 2716791.8879 | 1259570.8071
22 | 2716829.9993 | 1259597.5275
23 | 2716922.9334 | 1259475.1701
24 | 2716903.4723 | 1259417.1584
25 | 2716884.0159 | 1259429.446
26 | 2716801.0515 | 1259463.662
27 | 2716983.7064 | 1259595.4054
28 | 2716972.4946 | 1259569.8047
29 | 2716967.5048 | 1259556.6188
30 | 2716964.0825 | 1259544.2876
31 | 2716958.7744 | 1259527.5047
32 | 2716995.1409 | 1259532.856
33 | 2716953.8264 | 1259519.3913
34 | 2717021.2694 | 1259525.4039
35 | 2716946.3606 | 1259508.7045
36 | 2716924.8707 | 1259477.9431
37 | 2716931.1824 | 1259459.498
38 | 2716955.0986 | 1259429.7663
39 | 2716939.0549 | 1259425.2784
40 | 2716969.6348 | 1259433.9795
41 | 2716822.6874 | 1259624.2326
42 | 2716725.2978 | 1259581.6052
43 | 2716713.1706 | 1259582.9339
44 | 2716726.1653 | 1259556.3783
45 | 2716669.1854 | 1259626.8393
46 | 2716641.0785 | 1259558.1572
47 | 2716726.3267 | 1259544.3822
48 | 2717062.0585 | 1259441.5495
49 | 2717050.2686 | 1259441.7783
50 | 2717074.2773 | 1259363.9653
51 | 2717024.2543 | 1259442.283
52 | 2717075.5162 | 1259364.0678
53 | 2717021.0565 | 1259442.345
54 | 2716992.2639 | 1259440.5206
55 | 2716988.8799 | 1259439.5424
56 | 2716981.4701 | 1259437.4005
57 | 2716972.0718 | 1259407.884
58 | 2716967.3521 | 1259368.1088
59 | 2716968.0936 | 1259357.0998
60 | 2716990.8331 | 1259293.5041
61 | 2716929.2325 | 1259422.5307
62 | 2716903.7203 | 1259415.3942
63 | 2716906.6112 | 1259390.7607
64 | 2716907.9574 | 1259378.0079
65 | 2716907.371 | 1259360.7225
66 | 2716906.9606 | 1259348.6222
67 | 2716905.5556 | 1259337.3327
68 | 2716904.7068 | 1259332.6246
69 | 2716900.4671 | 1259309.1069
70 | 2716899.6886 | 1259304.7886
71 | 2716893.0059 | 1259277.4593
72 | 2716889.8366 | 1259265.7997
73 | 2716888.9809 | 1259262.6516
74 | 2716840.5735 | 1259327.3153
75 | 2716839.2244 | 1259336.9437
76 | 2716832.2526 | 1259306.6735
77 | 2716829.1476 | 1259348.4934
78 | 2716830.9739 | 1259303.5013
79 | 2716819.476 | 1259359.0374
80 | 2716827.1268 | 1259293.9768
81 | 2716810.396 | 1259349.7482
82 | 2716831.2718 | 1259372.9943
83 | 2716821.7054 | 1259280.556
84 | 2716792.5739 | 1259331.5154
85 | 2716833.8918 | 1259376.0943
86 | 2716847.7361 | 1259391.6845
87 | 2716855.2192 | 1259399.6371
88 | 2716863.8843 | 1259408.8458
89 | 2716772.8754 | 1259314.0865
90 | 2716783.8977 | 1259442.1807
91 | 2716766.6903 | 1259420.6323
92 | 2716753.7743 | 1259404.458
93 | 2716745.63 | 1259415.5958
94 | 2716723.05 | 1259362.3955
95 | 2716742.1477 | 1259430.6878
96 | 2716740.7557 | 1259454.4126
97 | 2716763.5708 | 1259359.5703
98 | 2716757.8901 | 1259352.1373
99 | 2716767.2103 | 1259368.7264
100 | 2716748.8346 | 1259342.3443
101 | 2716769.0308 | 1259373.3543
102 | 2716736.304 | 1259329.7089
103 | 2716734.3411 | 1259327.9207
104 | 2716725.0051 | 1259319.1723
105 | 2716727.0253 | 1259303.5377
106 | 2716740.5414 | 1259285.7163
107 | 2716694.9108 | 1259239.7062
108 | 2716676.9695 | 1259270.4603
109 | 2716820.7313 | 1259278.1447
110 | 2716815.0162 | 1259261.7726
111 | 2716840.2535 | 1259244.919
112 | 2716854.8293 | 1259238.3378
113 | 2716864.9533 | 1259233.7666
114 | 2716879.3609 | 1259227.2613
115 | 2716856.1295 | 1259139.1596
116 | 2716798.6728 | 1259161.4482
117 | 2716894.4166 | 1259126.608
118 | 2716625.2272 | 1259380.4261
119 | 2716625.98 | 1259397.7876
120 | 2716381.8518 | 1259273.4856
121 | 2716626.7506 | 1259415.5569
122 | 2716337.2561 | 1259255.1222
123 | 2716283.6355 | 1259237.8909
124 | 2716352.2106 | 1259262.0818
125 | 2716277.6791 | 1259255.9471
126 | 2716259.9045 | 1259239.7611
127 | 2716261.29 | 1259205.7014
128 | 2716344.4027 | 1259285.4208
129 | 2716373.354 | 1259270.2163
130 | 2716265.8631 | 1259275.0174
131 | 2716230.5319 | 1259242.076
132 | 2716232.8545 | 1259178.0194
133 | 2716338.6202 | 1259302.7055
134 | 2716334.9175 | 1259313.7735
135 | 2716212.2326 | 1259242.4701
136 | 2716626.9044 | 1259419.1046
137 | 2716627.3464 | 1259440.7463
138 | 2716627.4916 | 1259449.5451
139 | 2716627.8459 | 1259471.0105
140 | 2716627.9293 | 1259476.066
141 | 2716624.1459 | 1259489.7308
142 | 2716617.9487 | 1259497.5567
143 | 2716604.1823 | 1259512.8024
144 | 2716555.3792 | 1259508.6899
145 | 2716613.1127 | 1259531.6575
146 | 2716624.6939 | 1259545.1643
147 | 2716243.854 | 1259297.4622
148 | 2716240.266 | 1259300.6785
149 | 2716191.0116 | 1259241.5984
150 | 2716627.8142 | 1259548.0219
151 | 2716664.8317 | 1259626.6408
152 | 2716664.2664 | 1259611.3902
153 | 2716660.7373 | 1259598.7693
154 | 2716655.9552 | 1259595.0495
155 | 2716219.8413 | 1259167.7323
156 | 2716195.3526 | 1259140.2598
157 | 2716697.4635 | 1259542.5558
158 | 2716691.8581 | 1259528.6456
159 | 2716691.846 | 1259528.1337
160 | 2716732.1417 | 1259541.3626
161 | 2716691.2669 | 1259503.5943
162 | 2716738.4284 | 1259536.7142
163 | 2716690.6726 | 1259478.4098
164 | 2716740.6796 | 1259502.4137
165 | 2716740.6674 | 1259502.3475
166 | 2716739.392 | 1259481.0267
167 | 2716690.0843 | 1259453.4792
168 | 2716690.082 | 1259453.3851
169 | 2716689.4652 | 1259427.2474
170 | 2716684.7196 | 1259411.4365
171 | 2716869.8268 | 1259547.8729

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1