## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4761-11_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4761-11_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4761-11_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4761-11_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4761-11_0_6_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_4761-11_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_4761-11_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_4761-11_0_6_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_4761-11_0_6_node_39 | 0.4 | n |  | TRUE
9 | bus_LV_4761-11_0_6_node_37 | 0.4 | n |  | TRUE
10 | bus_LV_4761-11_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_4761-11_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_4761-11_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_4761-11_0_6_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_4761-11_0_6_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_4761-11_0_6_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_4761-11_0_6_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_4761-11_0_6_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_4761-11_0_6_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_4761-11_0_6_node_139 | 0.4 | n |  | TRUE
20 | bus_LV_4761-11_0_6_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_4761-11_0_6_node_140 | 0.4 | n |  | TRUE
22 | bus_LV_4761-11_0_6_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_4761-11_0_6_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_4761-11_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_4761-11_0_6_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_4761-11_0_6_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_4761-11_0_6_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_4761-11_0_6_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_4761-11_0_6_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_4761-11_0_6_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_4761-11_0_6_node_83 | 0.4 | n |  | TRUE
32 | bus_LV_4761-11_0_6_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_4761-11_0_6_node_79 | 0.4 | n |  | TRUE
34 | bus_LV_4761-11_0_6_node_138 | 0.4 | n |  | TRUE
35 | bus_LV_4761-11_0_6_node_81 | 0.4 | n |  | TRUE
36 | bus_LV_4761-11_0_6_node_77 | 0.4 | n |  | TRUE
37 | bus_LV_4761-11_0_6_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_4761-11_0_6_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_4761-11_0_6_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_4761-11_0_6_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_4761-11_0_6_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_4761-11_0_6_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_4761-11_0_6_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_4761-11_0_6_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_4761-11_0_6_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_4761-11_0_6_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_4761-11_0_6_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_4761-11_0_6_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_4761-11_0_6_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_4761-11_0_6_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_4761-11_0_6_node_82 | 0.4 | n |  | TRUE
52 | bus_LV_4761-11_0_6_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_4761-11_0_6_node_80 | 0.4 | n |  | TRUE
54 | bus_LV_4761-11_0_6_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_4761-11_0_6_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_4761-11_0_6_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_4761-11_0_6_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_4761-11_0_6_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_4761-11_0_6_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_4761-11_0_6_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_4761-11_0_6_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_4761-11_0_6_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_4761-11_0_6_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_4761-11_0_6_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_4761-11_0_6_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_4761-11_0_6_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_4761-11_0_6_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_4761-11_0_6_node_60 | 0.4 | n |  | TRUE
69 | bus_LV_4761-11_0_6_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_4761-11_0_6_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_4761-11_0_6_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_4761-11_0_6_node_64 | 0.4 | n |  | TRUE
73 | bus_LV_4761-11_0_6_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_4761-11_0_6_node_66 | 0.4 | n |  | TRUE
75 | bus_LV_4761-11_0_6_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_4761-11_0_6_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_4761-11_0_6_node_71 | 0.4 | n |  | TRUE
78 | bus_LV_4761-11_0_6_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_4761-11_0_6_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_4761-11_0_6_node_134 | 0.4 | n |  | TRUE
81 | bus_LV_4761-11_0_6_node_133 | 0.4 | n |  | TRUE
82 | bus_LV_4761-11_0_6_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_4761-11_0_6_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_4761-11_0_6_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_4761-11_0_6_node_84 | 0.4 | n |  | TRUE
86 | bus_LV_4761-11_0_6_node_85 | 0.4 | n |  | TRUE
87 | bus_LV_4761-11_0_6_node_75 | 0.4 | n |  | TRUE
88 | bus_LV_4761-11_0_6_node_76 | 0.4 | n |  | TRUE
89 | bus_LV_4761-11_0_6_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_4761-11_0_6_node_86 | 0.4 | n |  | TRUE
91 | bus_LV_4761-11_0_6_node_89 | 0.4 | n |  | TRUE
92 | bus_LV_4761-11_0_6_node_137 | 0.4 | n |  | TRUE
93 | bus_LV_4761-11_0_6_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_4761-11_0_6_node_88 | 0.4 | n |  | TRUE
95 | bus_LV_4761-11_0_6_node_90 | 0.4 | n |  | TRUE
96 | bus_LV_4761-11_0_6_node_91 | 0.4 | n |  | TRUE
97 | bus_LV_4761-11_0_6_node_92 | 0.4 | n |  | TRUE
98 | bus_LV_4761-11_0_6_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_4761-11_0_6_node_94 | 0.4 | n |  | TRUE
100 | bus_LV_4761-11_0_6_node_95 | 0.4 | n |  | TRUE
101 | bus_LV_4761-11_0_6_node_96 | 0.4 | n |  | TRUE
102 | bus_LV_4761-11_0_6_node_99 | 0.4 | n |  | TRUE
103 | bus_LV_4761-11_0_6_node_97 | 0.4 | n |  | TRUE
104 | bus_LV_4761-11_0_6_node_102 | 0.4 | n |  | TRUE
105 | bus_LV_4761-11_0_6_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_4761-11_0_6_node_98 | 0.4 | n |  | TRUE
107 | bus_LV_4761-11_0_6_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_4761-11_0_6_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_4761-11_0_6_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_4761-11_0_6_node_108 | 0.4 | n |  | TRUE
111 | bus_LV_4761-11_0_6_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_4761-11_0_6_node_104 | 0.4 | n |  | TRUE
113 | bus_LV_4761-11_0_6_node_105 | 0.4 | n |  | TRUE
114 | bus_LV_4761-11_0_6_node_106 | 0.4 | n |  | TRUE
115 | bus_LV_4761-11_0_6_node_123 | 0.4 | n |  | TRUE
116 | bus_LV_4761-11_0_6_node_124 | 0.4 | n |  | TRUE
117 | bus_LV_4761-11_0_6_node_110 | 0.4 | n |  | TRUE
118 | bus_LV_4761-11_0_6_node_114 | 0.4 | n |  | TRUE
119 | bus_LV_4761-11_0_6_node_111 | 0.4 | n |  | TRUE
120 | bus_LV_4761-11_0_6_node_117 | 0.4 | n |  | TRUE
121 | bus_LV_4761-11_0_6_node_112 | 0.4 | n |  | TRUE
122 | bus_LV_4761-11_0_6_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_4761-11_0_6_node_115 | 0.4 | n |  | TRUE
124 | bus_LV_4761-11_0_6_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_4761-11_0_6_node_121 | 0.4 | n |  | TRUE
126 | bus_LV_4761-11_0_6_node_122 | 0.4 | n |  | TRUE
127 | bus_LV_4761-11_0_6_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_4761-11_0_6_node_119 | 0.4 | n |  | TRUE
129 | bus_LV_4761-11_0_6_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_4761-11_0_6_node_135 | 0.4 | n |  | TRUE
131 | bus_LV_4761-11_0_6_node_149 | 0.4 | n |  | TRUE
132 | bus_LV_4761-11_0_6_node_136 | 0.4 | n |  | TRUE
133 | bus_LV_4761-11_0_6_node_150 | 0.4 | n |  | TRUE
134 | bus_LV_4761-11_0_6_node_125 | 0.4 | n |  | TRUE
135 | bus_LV_4761-11_0_6_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_4761-11_0_6_node_127 | 0.4 | n |  | TRUE
137 | bus_LV_4761-11_0_6_node_128 | 0.4 | n |  | TRUE
138 | bus_LV_4761-11_0_6_node_129 | 0.4 | n |  | TRUE
139 | bus_LV_4761-11_0_6_node_130 | 0.4 | n |  | TRUE
140 | bus_LV_4761-11_0_6_node_131 | 0.4 | n |  | TRUE
141 | bus_LV_4761-11_0_6_node_132 | 0.4 | n |  | TRUE
142 | bus_LV_4761-11_0_6_node_141 | 0.4 | n |  | TRUE
143 | bus_LV_4761-11_0_6_node_142 | 0.4 | n |  | TRUE
144 | bus_LV_4761-11_0_6_node_143 | 0.4 | n |  | TRUE
145 | bus_LV_4761-11_0_6_node_144 | 0.4 | n |  | TRUE
146 | bus_LV_4761-11_0_6_node_145 | 0.4 | n |  | TRUE
147 | bus_LV_4761-11_0_6_node_146 | 0.4 | n |  | TRUE
148 | bus_LV_4761-11_0_6_node_147 | 0.4 | n |  | TRUE
149 | bus_LV_4761-11_0_6_node_148 | 0.4 | n |  | TRUE
150 | bus_LV_4761-11_0_6_node_155 | 0.4 | n |  | TRUE
151 | bus_LV_4761-11_0_6_node_153 | 0.4 | n |  | TRUE
152 | bus_LV_4761-11_0_6_node_157 | 0.4 | n |  | TRUE
153 | bus_LV_4761-11_0_6_node_156 | 0.4 | n |  | TRUE
154 | bus_LV_4761-11_0_6_node_152 | 0.4 | n |  | TRUE
155 | bus_LV_4761-11_0_6_node_158 | 0.4 | n |  | TRUE
156 | bus_LV_4761-11_0_6_node_151 | 0.4 | n |  | TRUE
157 | bus_LV_4761-11_0_6_node_154 | 0.4 | n |  | TRUE
158 | bus_LV_4761-11_0_6_node_159 | 0.4 | n |  | TRUE
159 | bus_LV_4761-11_0_6_node_160 | 0.4 | n |  | TRUE
160 | bus_LV_4761-11_0_6_node_161 | 0.4 | n |  | TRUE
161 | bus_LV_4761-11_0_6_node_162 | 0.4 | n |  | TRUE
162 | bus_MV_443_0_node_41 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4761-11_0_6_load_0 | 0 | 0.0073955 | 0.0018535 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4761-11_0_6_load_4 | 5 | 0.0010656 | 0.00026705 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4761-11_0_6_load_6 | 6 | 0.0038298 | 0.00095984 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4761-11_0_6_load_38 | 7 | 0.0014949 | 0.00037466 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4761-11_0_6_load_37 | 9 | 0.0038734 | 0.00097077 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4761-11_0_6_load_8 | 10 | 0.0030075 | 0.00075375 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4761-11_0_6_load_9 | 11 | 0.0037202 | 0.00093237 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4761-11_0_6_load_10 | 12 | 0.0030133 | 0.00075522 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4761-11_0_6_load_11 | 13 | 0.0029344 | 0.00073543 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4761-11_0_6_load_12 | 14 | 0.0034171 | 0.0008564 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4761-11_0_6_load_13 | 15 | 0.0017393 | 0.00043591 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4761-11_0_6_load_14 | 16 | 0.002988 | 0.00074887 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4761-11_0_6_load_26 | 18 | 0.0026597 | 0.00066658 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4761-11_0_6_load_139 | 19 | 0.0018877 | 0.0004731 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4761-11_0_6_load_140 | 21 | 0.0020478 | 0.00051322 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4761-11_0_6_load_16 | 22 | 0.0025124 | 0.00062966 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4761-11_0_6_load_17 | 23 | 0.0015131 | 0.00037921 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4761-11_0_6_load_18 | 24 | 0.0028218 | 0.00070722 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4761-11_0_6_load_19 | 25 | 0.0013675 | 0.00034274 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4761-11_0_6_load_20 | 26 | 0.0036653 | 0.00091861 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4761-11_0_6_load_21 | 27 | 0.0023965 | 0.00060061 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4761-11_0_6_load_22 | 28 | 0.0031333 | 0.00078528 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4761-11_0_6_load_27 | 29 | 0.0036606 | 0.00091744 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4761-11_0_6_load_24 | 30 | 0.0011806 | 0.00029589 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4761-11_0_6_load_83 | 31 | 0.00090536 | 0.0002269 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4761-11_0_6_load_25 | 32 | 0.0017737 | 0.00044452 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4761-11_0_6_load_138 | 34 | 0.00076393 | 0.00019146 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4761-11_0_6_load_81 | 35 | 0.0017254 | 0.00043243 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4761-11_0_6_load_77 | 36 | 0.0013518 | 0.00033879 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4761-11_0_6_load_28 | 37 | 0.036475 | 0.0091415 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4761-11_0_6_load_29 | 38 | 0.0039608 | 0.00099266 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4761-11_0_6_load_30 | 39 | 0.0020764 | 0.00052039 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4761-11_0_6_load_31 | 40 | 0.0015185 | 0.00038057 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4761-11_0_6_load_32 | 41 | 0.0014835 | 0.00037179 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4761-11_0_6_load_33 | 42 | 0.0018638 | 0.00046711 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4761-11_0_6_load_34 | 43 | 0.0018153 | 0.00045495 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4761-11_0_6_load_35 | 44 | 0.0015542 | 0.00038953 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4761-11_0_6_load_36 | 45 | 0.0014951 | 0.0003747 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4761-11_0_6_load_40 | 46 | 0.0014495 | 0.00036328 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4761-11_0_6_load_41 | 47 | 0.0011162 | 0.00027974 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4761-11_0_6_load_42 | 48 | 0.00082241 | 0.00020612 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4761-11_0_6_load_44 | 49 | 0.00084636 | 0.00021212 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4761-11_0_6_load_43 | 50 | 0.0014045 | 0.00035201 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4761-11_0_6_load_82 | 51 | 0.0018103 | 0.00045371 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4761-11_0_6_load_45 | 52 | 0.0015437 | 0.00038689 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4761-11_0_6_load_80 | 53 | 0.0023175 | 0.00058081 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4761-11_0_6_load_47 | 55 | 0.0022182 | 0.00055594 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4761-11_0_6_load_48 | 56 | 0.0045925 | 0.001151 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4761-11_0_6_load_52 | 57 | 0.0014811 | 0.00037119 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4761-11_0_6_load_56 | 59 | 0.0021723 | 0.00054442 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4761-11_0_6_load_50 | 60 | 0.0035698 | 0.00089467 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4761-11_0_6_load_51 | 61 | 0.002216 | 0.00055538 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4761-11_0_6_load_53 | 62 | 0.0014153 | 0.0003547 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4761-11_0_6_load_54 | 63 | 0.0020959 | 0.00052528 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4761-11_0_6_load_57 | 64 | 0.0017138 | 0.00042952 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4761-11_0_6_load_55 | 65 | 0.0018995 | 0.00047606 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4761-11_0_6_load_58 | 66 | 0.0018084 | 0.00045322 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4761-11_0_6_load_59 | 67 | 0.0017966 | 0.00045028 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4761-11_0_6_load_60 | 68 | 0.0017945 | 0.00044974 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4761-11_0_6_load_61 | 69 | 0.0013409 | 0.00033607 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4761-11_0_6_load_62 | 70 | 0.0013758 | 0.0003448 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4761-11_0_6_load_63 | 71 | 0.0013859 | 0.00034734 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4761-11_0_6_load_64 | 72 | 0.0012172 | 0.00030507 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4761-11_0_6_load_65 | 73 | 0.0020357 | 0.00051019 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4761-11_0_6_load_66 | 74 | 0.0016789 | 0.00042077 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4761-11_0_6_load_67 | 75 | 0.0020626 | 0.00051693 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4761-11_0_6_load_70 | 76 | 0.0014401 | 0.00036092 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4761-11_0_6_load_71 | 77 | 0.0017123 | 0.00042915 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4761-11_0_6_load_68 | 78 | 0.0012437 | 0.00031169 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4761-11_0_6_load_69 | 79 | 0.0024101 | 0.00060402 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4761-11_0_6_load_134 | 80 | 0.0042407 | 0.0010628 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4761-11_0_6_load_133 | 81 | 0.0024619 | 0.00061701 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4761-11_0_6_load_72 | 82 | 0.00098399 | 0.00024661 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4761-11_0_6_load_73 | 83 | 0.0013038 | 0.00032677 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4761-11_0_6_load_74 | 84 | 0.00073843 | 0.00018507 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4761-11_0_6_load_84 | 85 | 0.0017842 | 0.00044716 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4761-11_0_6_load_85 | 86 | 0.0013017 | 0.00032625 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4761-11_0_6_load_75 | 87 | 0.0019963 | 0.00050031 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4761-11_0_6_load_76 | 88 | 0.0013016 | 0.00032621 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4761-11_0_6_load_78 | 89 | 0.0010167 | 0.00025482 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4761-11_0_6_load_86 | 90 | 0.001565 | 0.00039223 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4761-11_0_6_load_89 | 91 | 0.0014934 | 0.00037428 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4761-11_0_6_load_137 | 92 | 0.0012682 | 0.00031784 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4761-11_0_6_load_87 | 93 | 0.0013024 | 0.00032641 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4761-11_0_6_load_88 | 94 | 0.0019175 | 0.00048057 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4761-11_0_6_load_90 | 95 | 0.0017419 | 0.00043657 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4761-11_0_6_load_91 | 96 | 0.0028409 | 0.00071199 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4761-11_0_6_load_92 | 97 | 0.001672 | 0.00041904 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4761-11_0_6_load_93 | 98 | 0.0020418 | 0.00051173 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4761-11_0_6_load_94 | 99 | 0.0015773 | 0.00039532 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4761-11_0_6_load_95 | 100 | 0.0023831 | 0.00059725 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4761-11_0_6_load_96 | 101 | 0.0015504 | 0.00038856 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4761-11_0_6_load_99 | 102 | 0.0013198 | 0.00033077 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4761-11_0_6_load_97 | 103 | 0.0038681 | 0.00096945 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4761-11_0_6_load_102 | 104 | 0.0036538 | 0.00091574 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4761-11_0_6_load_103 | 105 | 0.0027959 | 0.00070071 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4761-11_0_6_load_98 | 106 | 0.00069101 | 0.00017318 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4761-11_0_6_load_100 | 107 | 0.0019969 | 0.00050048 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4761-11_0_6_load_101 | 108 | 0.0050296 | 0.0012605 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4761-11_0_6_load_108 | 110 | 0.0048872 | 0.0012248 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4761-11_0_6_load_109 | 111 | 0.0028544 | 0.00071539 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4761-11_0_6_load_105 | 113 | 0.0019986 | 0.0005009 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4761-11_0_6_load_106 | 114 | 0.0022032 | 0.00055217 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4761-11_0_6_load_123 | 115 | 0.0033408 | 0.00083727 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4761-11_0_6_load_114 | 118 | 0.0013105 | 0.00032844 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4761-11_0_6_load_111 | 119 | 0.0020673 | 0.00051813 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4761-11_0_6_load_112 | 121 | 0.00073141 | 0.00018331 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4761-11_0_6_load_115 | 123 | 0.002037 | 0.00051053 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4761-11_0_6_load_116 | 124 | 0.0018661 | 0.00046769 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4761-11_0_6_load_121 | 125 | 0.0019495 | 0.0004886 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4761-11_0_6_load_122 | 126 | 0.0020905 | 0.00052392 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4761-11_0_6_load_118 | 127 | 0.011089 | 0.0027791 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4761-11_0_6_load_119 | 128 | 0.0014368 | 0.0003601 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4761-11_0_6_load_120 | 129 | 0.0039473 | 0.00098929 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4761-11_0_6_load_135 | 130 | 0.001658 | 0.00041553 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4761-11_0_6_load_149 | 131 | 0.0012618 | 0.00031623 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4761-11_0_6_load_136 | 132 | 0.0011731 | 0.000294 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4761-11_0_6_load_150 | 133 | 0.0038833 | 0.00097324 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4761-11_0_6_load_125 | 134 | 0.0022025 | 0.00055201 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4761-11_0_6_load_126 | 135 | 0.0007952 | 0.0001993 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4761-11_0_6_load_127 | 136 | 0.0021546 | 0.00054 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4761-11_0_6_load_128 | 137 | 0.0027491 | 0.00068899 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4761-11_0_6_load_129 | 138 | 0.0028131 | 0.00070502 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4761-11_0_6_load_131 | 140 | 0.0021714 | 0.00054419 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4761-11_0_6_load_132 | 141 | 0.0045234 | 0.0011337 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4761-11_0_6_load_141 | 142 | 0.0031446 | 0.0007881 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4761-11_0_6_load_142 | 143 | 0.0025959 | 0.00065059 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4761-11_0_6_load_143 | 144 | 0.0018907 | 0.00047386 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4761-11_0_6_load_145 | 146 | 0.0011552 | 0.00028952 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4761-11_0_6_load_146 | 147 | 0.0014767 | 0.0003701 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4761-11_0_6_load_148 | 149 | 0.0020506 | 0.00051393 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4761-11_0_6_load_155 | 150 | 0.022478 | 0.0056336 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4761-11_0_6_load_153 | 151 | 0.013993 | 0.0035069 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4761-11_0_6_load_157 | 152 | 0.00119 | 0.00029824 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4761-11_0_6_load_156 | 153 | 0.0014774 | 0.00037028 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4761-11_0_6_load_152 | 154 | 0.018065 | 0.0045274 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4761-11_0_6_load_158 | 155 | 0.0010959 | 0.00027466 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4761-11_0_6_load_151 | 156 | 0.0010987 | 0.00027535 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4761-11_0_6_load_154 | 157 | 0.0011777 | 0.00029515 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_4761-11_0_6_load_159 | 158 | 0.001166 | 0.00029224 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_4761-11_0_6_load_160 | 159 | 0.0095808 | 0.0024012 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_4761-11_0_6_load_161 | 160 | 0.00086924 | 0.00021785 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_4761-11_0_6_load_162 | 161 | 0.0010396 | 0.00026054 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4761-11_0_6_line_0 |  | 0 | 1 | 0.026842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4761-11_0_6_line_1 |  | 0 | 2 | 0.02546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4761-11_0_6_line_2 |  | 1 | 3 | 0.025136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4761-11_0_6_line_3 |  | 2 | 4 | 0.14831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4761-11_0_6_line_4 |  | 3 | 5 | 0.0032606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4761-11_0_6_line_5 |  | 4 | 6 | 0.021418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4761-11_0_6_line_6 |  | 6 | 7 | 0.1295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4761-11_0_6_line_7 |  | 7 | 8 | 0.016555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_4761-11_0_6_line_8 |  | 7 | 9 | 0.01817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_4761-11_0_6_line_9 |  | 8 | 46 | 0.0043994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_4761-11_0_6_line_10 |  | 8 | 47 | 0.014745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4761-11_0_6_line_11 |  | 9 | 45 | 0.0061657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_4761-11_0_6_line_12 |  | 10 | 11 | 0.018456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4761-11_0_6_line_13 |  | 10 | 12 | 0.002433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4761-11_0_6_line_14 |  | 11 | 13 | 0.0043502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4761-11_0_6_line_15 |  | 12 | 14 | 0.019413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4761-11_0_6_line_16 |  | 13 | 15 | 0.0074579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4761-11_0_6_line_17 |  | 14 | 16 | 0.00087195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4761-11_0_6_line_18 |  | 15 | 17 | 0.0080108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4761-11_0_6_line_19 |  | 17 | 18 | 0.01244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4761-11_0_6_line_20 |  | 17 | 19 | 0.032017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4761-11_0_6_line_21 |  | 18 | 20 | 0.032449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4761-11_0_6_line_22 |  | 19 | 21 | 0.0067573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4761-11_0_6_line_23 |  | 20 | 30 | 0.013181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4761-11_0_6_line_24 |  | 20 | 28 | 0.025647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4761-11_0_6_line_25 |  | 21 | 142 | 0.013905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4761-11_0_6_line_26 |  | 22 | 23 | 0.019177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4761-11_0_6_line_27 |  | 22 | 24 | 0.0054075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4761-11_0_6_line_28 |  | 23 | 25 | 0.0061492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4761-11_0_6_line_29 |  | 24 | 26 | 0.022959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4761-11_0_6_line_30 |  | 25 | 27 | 0.021196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4761-11_0_6_line_31 |  | 26 | 28 | 0.0022332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4761-11_0_6_line_32 |  | 27 | 29 | 0.0093502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4761-11_0_6_line_33 |  | 30 | 31 | 0.029964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_4761-11_0_6_line_34 |  | 31 | 34 | 0.010099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_4761-11_0_6_line_35 |  | 32 | 33 | 0.01409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4761-11_0_6_line_36 |  | 33 | 35 | 0.014904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4761-11_0_6_line_37 |  | 33 | 36 | 0.01768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4761-11_0_6_line_38 |  | 34 | 92 | 0.0086592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_4761-11_0_6_line_39 |  | 35 | 90 | 0.02068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4761-11_0_6_line_40 |  | 36 | 87 | 0.029038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4761-11_0_6_line_41 |  | 37 | 38 | 0.030877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4761-11_0_6_line_42 |  | 38 | 39 | 0.017491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4761-11_0_6_line_43 |  | 39 | 40 | 0.014638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4761-11_0_6_line_44 |  | 40 | 41 | 0.02699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4761-11_0_6_line_45 |  | 41 | 42 | 0.021791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_4761-11_0_6_line_46 |  | 42 | 43 | 0.026734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_4761-11_0_6_line_47 |  | 43 | 44 | 0.0013503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_4761-11_0_6_line_48 |  | 44 | 45 | 0.022708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_4761-11_0_6_line_49 |  | 46 | 48 | 0.026805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_4761-11_0_6_line_50 |  | 48 | 49 | 0.00068988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_4761-11_0_6_line_51 |  | 49 | 52 | 0.0059466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_4761-11_0_6_line_52 |  | 50 | 51 | 0.027362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4761-11_0_6_line_53 |  | 51 | 53 | 0.028025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4761-11_0_6_line_54 |  | 52 | 54 | 0.01247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_4761-11_0_6_line_55 |  | 53 | 89 | 0.0042022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4761-11_0_6_line_56 |  | 54 | 55 | 0.013892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_4761-11_0_6_line_57 |  | 54 | 56 | 0.0079957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_4761-11_0_6_line_58 |  | 55 | 57 | 0.023224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_4761-11_0_6_line_59 |  | 56 | 58 | 0.03867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_4761-11_0_6_line_60 |  | 57 | 59 | 0.0022707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_4761-11_0_6_line_61 |  | 58 | 60 | 0.01983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4761-11_0_6_line_62 |  | 58 | 61 | 0.014192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_4761-11_0_6_line_63 |  | 59 | 64 | 0.021716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_4761-11_0_6_line_64 |  | 61 | 62 | 0.023236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_4761-11_0_6_line_65 |  | 62 | 63 | 0.0018292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_4761-11_0_6_line_66 |  | 63 | 65 | 0.027044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_4761-11_0_6_line_67 |  | 64 | 68 | 0.010635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_4761-11_0_6_line_68 |  | 65 | 66 | 8.6923e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_4761-11_0_6_line_69 |  | 66 | 67 | 0.023437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_4761-11_0_6_line_70 |  | 67 | 70 | 0.0054977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_4761-11_0_6_line_71 |  | 68 | 69 | 0.013433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_4761-11_0_6_line_72 |  | 69 | 72 | 0.013657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_4761-11_0_6_line_73 |  | 70 | 71 | 0.0223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_4761-11_0_6_line_74 |  | 71 | 74 | 0.0010086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4761-11_0_6_line_75 |  | 72 | 73 | 0.013421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_4761-11_0_6_line_76 |  | 73 | 76 | 0.009523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_4761-11_0_6_line_77 |  | 74 | 75 | 0.02457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4761-11_0_6_line_78 |  | 75 | 78 | 0.0092077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4761-11_0_6_line_79 |  | 76 | 77 | 0.013313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_4761-11_0_6_line_80 |  | 77 | 82 | 0.01028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_4761-11_0_6_line_81 |  | 78 | 79 | 0.020368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4761-11_0_6_line_82 |  | 79 | 80 | 0.010863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4761-11_0_6_line_83 |  | 80 | 81 | 0.032929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4761-11_0_6_line_84 |  | 81 | 140 | 0.026854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4761-11_0_6_line_85 |  | 82 | 83 | 0.014105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_4761-11_0_6_line_86 |  | 83 | 84 | 0.0097865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_4761-11_0_6_line_87 |  | 84 | 85 | 0.015699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_4761-11_0_6_line_88 |  | 85 | 86 | 0.0094391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_4761-11_0_6_line_89 |  | 86 | 93 | 0.016952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_4761-11_0_6_line_90 |  | 87 | 88 | 0.0029521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4761-11_0_6_line_91 |  | 88 | 89 | 0.020352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4761-11_0_6_line_92 |  | 90 | 91 | 0.0059883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4761-11_0_6_line_93 |  | 91 | 95 | 0.013616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4761-11_0_6_line_94 |  | 92 | 132 | 0.020409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_4761-11_0_6_line_95 |  | 93 | 94 | 0.020402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_4761-11_0_6_line_96 |  | 94 | 96 | 0.0059188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_4761-11_0_6_line_97 |  | 95 | 98 | 0.018346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4761-11_0_6_line_98 |  | 96 | 97 | 0.020851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_4761-11_0_6_line_99 |  | 97 | 100 | 0.009836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_4761-11_0_6_line_100 |  | 98 | 99 | 0.0059794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4761-11_0_6_line_101 |  | 99 | 102 | 0.0080269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4761-11_0_6_line_102 |  | 100 | 101 | 0.018892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_4761-11_0_6_line_103 |  | 101 | 104 | 0.012744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_4761-11_0_6_line_104 |  | 102 | 103 | 0.017646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4761-11_0_6_line_105 |  | 103 | 106 | 0.0050815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4761-11_0_6_line_106 |  | 104 | 105 | 0.013047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_4761-11_0_6_line_107 |  | 105 | 112 | 0.019613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_4761-11_0_6_line_108 |  | 106 | 107 | 0.01803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4761-11_0_6_line_109 |  | 107 | 108 | 0.00056409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4761-11_0_6_line_110 |  | 108 | 109 | 0.020561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4761-11_0_6_line_111 |  | 109 | 110 | 0.01029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_4761-11_0_6_line_112 |  | 109 | 111 | 0.03028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_4761-11_0_6_line_113 |  | 110 | 117 | 0.025944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_4761-11_0_6_line_114 |  | 111 | 114 | 0.0288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_4761-11_0_6_line_115 |  | 112 | 113 | 0.019731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4761-11_0_6_line_116 |  | 112 | 114 | 0.01102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_4761-11_0_6_line_117 |  | 115 | 116 | 0.022511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4761-11_0_6_line_118 |  | 116 | 134 | 0.013351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4761-11_0_6_line_119 |  | 117 | 118 | 0.016077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4761-11_0_6_line_120 |  | 117 | 119 | 0.011972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_4761-11_0_6_line_121 |  | 118 | 120 | 0.12476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4761-11_0_6_line_122 |  | 119 | 121 | 0.014323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_4761-11_0_6_line_123 |  | 120 | 127 | 0.020731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4761-11_0_6_line_124 |  | 120 | 128 | 0.049489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4761-11_0_6_line_125 |  | 121 | 122 | 0.030341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_4761-11_0_6_line_126 |  | 122 | 123 | 0.030395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
127 | LV_4761-11_0_6_line_127 |  | 122 | 124 | 0.0048263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_4761-11_0_6_line_128 |  | 123 | 125 | 0.0027118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
129 | LV_4761-11_0_6_line_129 |  | 124 | 126 | 0.014923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_4761-11_0_6_line_130 |  | 125 | 130 | 0.031961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_4761-11_0_6_line_131 |  | 126 | 131 | 0.0049401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_4761-11_0_6_line_132 |  | 127 | 129 | 0.026683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4761-11_0_6_line_133 |  | 130 | 132 | 0.0014773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
134 | LV_4761-11_0_6_line_134 |  | 131 | 133 | 0.0065014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
135 | LV_4761-11_0_6_line_135 |  | 133 | 156 | 0.0062362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_4761-11_0_6_line_136 |  | 134 | 135 | 0.0095243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4761-11_0_6_line_137 |  | 135 | 136 | 0.014956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4761-11_0_6_line_138 |  | 136 | 137 | 0.0072148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4761-11_0_6_line_139 |  | 137 | 138 | 0.031558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4761-11_0_6_line_140 |  | 138 | 139 | 0.027382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4761-11_0_6_line_141 |  | 139 | 140 | 0.010454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4761-11_0_6_line_142 |  | 139 | 141 | 0.025045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4761-11_0_6_line_143 |  | 142 | 143 | 0.014293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4761-11_0_6_line_144 |  | 143 | 144 | 0.013826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4761-11_0_6_line_145 |  | 145 | 146 | 0.013489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4761-11_0_6_line_146 |  | 145 | 147 | 0.045401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4761-11_0_6_line_147 |  | 146 | 148 | 0.023258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4761-11_0_6_line_148 |  | 147 | 149 | 0.023287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4761-11_0_6_line_149 |  | 148 | 150 | 0.02617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4761-11_0_6_line_150 |  | 148 | 151 | 0.015384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4761-11_0_6_line_151 |  | 149 | 152 | 0.020565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4761-11_0_6_line_152 |  | 150 | 153 | 0.014259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4761-11_0_6_line_153 |  | 151 | 154 | 0.038687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4761-11_0_6_line_154 |  | 152 | 155 | 0.021731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4761-11_0_6_line_155 |  | 153 | 158 | 0.018191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4761-11_0_6_line_156 |  | 154 | 157 | 0.03751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4761-11_0_6_line_157 |  | 156 | 157 | 0.00010956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4761-11_0_6_line_158 |  | 158 | 159 | 0.0051123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4761-11_0_6_line_159 |  | 159 | 160 | 0.015784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4761-11_0_6_line_160 |  | 160 | 161 | 0.02015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4761-11_0_6_trafo_24 | 0.63 MVA 20/0.4 kV | 162 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2718214.2613 | 1258840.8612 | 2718188.0412 | 1258835.115
1 | 2718163.1715 | 1258829.6646 | 2718188.0412 | 1258835.115
2 | 2718233.866 | 1258825.0613 | 2718214.2613 | 1258840.8612
3 | 2718163.1715 | 1258829.6646 | 2718043.9656 | 1258917.8959
4 | 2718233.866 | 1258825.0613 | 2718236.4044 | 1258823.015
5 | 2718043.9656 | 1258917.8959 | 2718024.5431 | 1258908.8693
6 | 2717907.077 | 1258854.359 | 2718024.5431 | 1258908.8693
7 | 2717914.2805 | 1258839.4537 | 2717907.077 | 1258854.359
8 | 2717907.077 | 1258854.359 | 2717899.1706 | 1258870.7185
9 | 2717914.2805 | 1258839.4537 | 2717916.1665 | 1258835.4791
10 | 2717914.2805 | 1258839.4537 | 2717900.9568 | 1258833.1381
11 | 2717896.4876 | 1258876.2699 | 2717899.1706 | 1258870.7185
12 | 2717740.9749 | 1258871.8088 | 2717724.0892 | 1258864.3589
13 | 2717740.9749 | 1258871.8088 | 2717743.201 | 1258872.7909
14 | 2717720.1092 | 1258862.6029 | 2717724.0892 | 1258864.3589
15 | 2717760.9624 | 1258880.6272 | 2717743.201 | 1258872.7909
16 | 2717713.2859 | 1258859.5925 | 2717713.2859 | 1258859.5925 | 2717720.1092 | 1258862.6029
17 | 2717761.7601 | 1258880.9792 | 2717760.9624 | 1258880.6272
18 | 2717714.9275 | 1258851.7516 | 2717713.2859 | 1258859.5925
19 | 2717714.9275 | 1258851.7516 | 2717720.1591 | 1258840.4652
20 | 2717714.9275 | 1258851.7516 | 2717685.8275 | 1258838.3992
21 | 2717733.8054 | 1258811.0251 | 2717720.1591 | 1258840.4652
22 | 2717685.8275 | 1258838.3992 | 2717679.6859 | 1258835.5812
23 | 2717733.8054 | 1258811.0251 | 2717722.0824 | 1258805.0003
24 | 2717733.8054 | 1258811.0251 | 2717756.7794 | 1258822.4257
25 | 2717667.0477 | 1258829.7822 | 2717679.6859 | 1258835.5812
26 | 2717801.3675 | 1258844.5518 | 2717784.1893 | 1258836.0274
27 | 2717779.3454 | 1258833.6237 | 2717784.1893 | 1258836.0274
28 | 2717806.8758 | 1258847.2852 | 2717801.3675 | 1258844.5518
29 | 2717779.3454 | 1258833.6237 | 2717758.7798 | 1258823.4183
30 | 2717806.8758 | 1258847.2852 | 2717825.8627 | 1258856.7072
31 | 2717756.7794 | 1258822.4257 | 2717758.7798 | 1258823.4183
32 | 2717834.2384 | 1258860.8635 | 2717825.8627 | 1258856.7072
33 | 2717695.4317 | 1258791.3036 | 2717722.0824 | 1258805.0003
34 | 2717695.4317 | 1258791.3036 | 2717690.9682 | 1258789.0096 | 2717686.2487 | 1258787.1286
35 | 2717756.1696 | 1258764.5075 | 2717750.0643 | 1258777.2065
36 | 2717756.1696 | 1258764.5075 | 2717743.2193 | 1258757.1304
37 | 2717756.1696 | 1258764.5075 | 2717772.1459 | 1258772.0804
38 | 2717686.2487 | 1258787.1286 | 2717678.2048 | 1258783.9227
39 | 2717725.4472 | 1258746.5808 | 2717729.022 | 1258749.0429 | 2717743.2193 | 1258757.1304
40 | 2717798.3851 | 1258784.5181 | 2717772.1459 | 1258772.0804
41 | 2717793.3231 | 1258954.1387 | 2717823.3401 | 1258961.3773
42 | 2717823.3401 | 1258961.3773 | 2717840.3436 | 1258965.4777
43 | 2717840.3436 | 1258965.4777 | 2717852.0142 | 1258968.292 | 2717853.1597 | 1258965.9218
44 | 2717864.9043 | 1258941.6206 | 2717853.1597 | 1258965.9218
45 | 2717864.9043 | 1258941.6206 | 2717874.3861 | 1258922.0012
46 | 2717874.3861 | 1258922.0012 | 2717886.0191 | 1258897.9309
47 | 2717886.6066 | 1258896.7151 | 2717886.0191 | 1258897.9309
48 | 2717886.6066 | 1258896.7151 | 2717896.4876 | 1258876.2699
49 | 2717916.1665 | 1258835.4791 | 2717927.6575 | 1258811.2616
50 | 2717927.6575 | 1258811.2616 | 2717927.9532 | 1258810.6383
51 | 2717927.9532 | 1258810.6383 | 2717930.5024 | 1258805.2658
52 | 2717848.5649 | 1258808.3038 | 2717873.2898 | 1258820.0237
53 | 2717823.2405 | 1258796.2998 | 2717848.5649 | 1258808.3038
54 | 2717935.8482 | 1258793.9996 | 2717930.5024 | 1258805.2658
55 | 2717823.2405 | 1258796.2998 | 2717819.4433 | 1258794.4999
56 | 2717935.8482 | 1258793.9996 | 2717923.4748 | 1258787.6831
57 | 2717935.8482 | 1258793.9996 | 2717939.4583 | 1258786.8652
58 | 2717923.4748 | 1258787.6831 | 2717902.7898 | 1258777.1236
59 | 2717956.9178 | 1258752.3611 | 2717939.4583 | 1258786.8652
60 | 2717900.7673 | 1258776.0912 | 2717902.7898 | 1258777.1236
61 | 2717956.9178 | 1258752.3611 | 2717974.7175 | 1258761.1022
62 | 2717956.9178 | 1258752.3611 | 2717944.2778 | 1258745.9077
63 | 2717900.7673 | 1258776.0912 | 2717881.4262 | 1258766.2178
64 | 2717923.583 | 1258735.342 | 2717944.2778 | 1258745.9077
65 | 2717923.583 | 1258735.342 | 2717921.9539 | 1258734.5102
66 | 2717897.8661 | 1258722.2151 | 2717898.0736 | 1258722.3181 | 2717921.9539 | 1258734.5102
67 | 2717871.9537 | 1258761.3822 | 2717881.4262 | 1258766.2178
68 | 2717897.7883 | 1258722.1764 | 2717897.8661 | 1258722.2151
69 | 2717897.7883 | 1258722.1764 | 2717876.7958 | 1258711.7539
70 | 2717871.8716 | 1258709.309 | 2717876.7958 | 1258711.7539
71 | 2717871.9537 | 1258761.3822 | 2717859.9898 | 1258755.2747
72 | 2717847.7939 | 1258749.1302 | 2717850.5867 | 1258750.4746 | 2717859.9898 | 1258755.2747
73 | 2717871.8716 | 1258709.309 | 2717851.8981 | 1258699.3924
74 | 2717850.9948 | 1258698.9439 | 2717851.8981 | 1258699.3924
75 | 2717847.7939 | 1258749.1302 | 2717835.7012 | 1258743.3092
76 | 2717827.1206 | 1258739.1787 | 2717835.7012 | 1258743.3092
77 | 2717850.9948 | 1258698.9439 | 2717828.9875 | 1258688.0175
78 | 2717820.7403 | 1258683.9229 | 2717828.9875 | 1258688.0175
79 | 2717827.1206 | 1258739.1787 | 2717815.1249 | 1258733.4044
80 | 2717815.1249 | 1258733.4044 | 2717805.8625 | 1258728.9458
81 | 2717820.7403 | 1258683.9229 | 2717817.1928 | 1258682.1616 | 2717805.0497 | 1258671.1282
82 | 2717797.0099 | 1258663.8233 | 2717805.0497 | 1258671.1282
83 | 2717775.3218 | 1258639.0873 | 2717793.8172 | 1258660.9224 | 2717797.0099 | 1258663.8233
84 | 2717761.5031 | 1258616.1303 | 2717772.805 | 1258636.116 | 2717775.3218 | 1258639.0873
85 | 2717793.1535 | 1258722.8281 | 2717805.8625 | 1258728.9458
86 | 2717793.1535 | 1258722.8281 | 2717784.3354 | 1258718.5833
87 | 2717770.1897 | 1258711.774 | 2717784.3354 | 1258718.5833
88 | 2717770.1897 | 1258711.774 | 2717770.1897 | 1258711.774 | 2717762.9226 | 1258705.7503
89 | 2717749.8711 | 1258694.9319 | 2717762.9226 | 1258705.7503
90 | 2717798.3851 | 1258784.5181 | 2717801.0527 | 1258785.7825
91 | 2717819.4433 | 1258794.4999 | 2717801.0527 | 1258785.7825
92 | 2717725.4472 | 1258746.5808 | 2717720.5154 | 1258743.1842
93 | 2717720.5154 | 1258743.1842 | 2717709.302 | 1258735.4611 | 2717709.302 | 1258735.4611
94 | 2717659.2458 | 1258776.3665 | 2717678.2048 | 1258783.9227
95 | 2717749.8711 | 1258694.9319 | 2717739.4113 | 1258686.2618 | 2717735.3668 | 1258680.7756
96 | 2717731.8546 | 1258676.0115 | 2717735.3668 | 1258680.7756
97 | 2717696.7088 | 1258722.1199 | 2717709.302 | 1258735.4611
98 | 2717731.8546 | 1258676.0115 | 2717719.4817 | 1258659.2282
99 | 2717713.6451 | 1258651.3111 | 2717719.4817 | 1258659.2282
100 | 2717696.7088 | 1258722.1199 | 2717692.6044 | 1258717.7717
101 | 2717692.6044 | 1258717.7717 | 2717687.0945 | 1258711.9345
102 | 2717713.6451 | 1258651.3111 | 2717702.4345 | 1258636.1044
103 | 2717694.3974 | 1258626.2268 | 2717699.4313 | 1258632.0307 | 2717702.4345 | 1258636.1044
104 | 2717674.982 | 1258699.1026 | 2717687.0945 | 1258711.9345
105 | 2717674.982 | 1258699.1026 | 2717671.494 | 1258695.4074
106 | 2717694.3974 | 1258626.2268 | 2717685.8492 | 1258616.3708
107 | 2717669.6391 | 1258605.8045 | 2717682.5207 | 1258612.5331 | 2717685.8492 | 1258616.3708
108 | 2717658.5302 | 1258682.9475 | 2717662.8503 | 1258686.2504 | 2717671.494 | 1258695.4074
109 | 2717658.5302 | 1258682.9475 | 2717658.0821 | 1258682.6049
110 | 2717641.748 | 1258670.1169 | 2717658.0821 | 1258682.6049
111 | 2717641.748 | 1258670.1169 | 2717636.8971 | 1258679.1914
112 | 2717641.748 | 1258670.1169 | 2717653.7957 | 1258642.3368
113 | 2717624.666 | 1258702.0718 | 2717636.8971 | 1258679.1914
114 | 2717653.7957 | 1258642.3368 | 2717665.2545 | 1258615.9146
115 | 2717669.6391 | 1258605.8045 | 2717677.3041 | 1258587.6236
116 | 2717669.6391 | 1258605.8045 | 2717665.2545 | 1258615.9146
117 | 2717699.9011 | 1258523.5572 | 2717694.7779 | 1258545.4775
118 | 2717699.9011 | 1258523.5572 | 2717709.8298 | 1258525.9678 | 2717711.9075 | 1258528.3134
119 | 2717624.666 | 1258702.0718 | 2717610.5178 | 1258694.4374
120 | 2717624.666 | 1258702.0718 | 2717618.9085 | 1258712.5688
121 | 2717610.5178 | 1258694.4374 | 2717489.8176 | 1258662.8706
122 | 2717618.9085 | 1258712.5688 | 2717612.0205 | 1258725.1268
123 | 2717489.8176 | 1258662.8706 | 2717469.3702 | 1258666.2878
124 | 2717489.8176 | 1258662.8706 | 2717484.8631 | 1258613.6304
125 | 2717597.4293 | 1258751.7292 | 2717612.0205 | 1258725.1268
126 | 2717597.4293 | 1258751.7292 | 2717625.6644 | 1258762.9824
127 | 2717597.4293 | 1258751.7292 | 2717595.3197 | 1258756.07
128 | 2717625.6644 | 1258762.9824 | 2717628.1834 | 1258763.9864
129 | 2717588.797 | 1258769.492 | 2717595.3197 | 1258756.07
130 | 2717628.1834 | 1258763.9864 | 2717657.8735 | 1258775.8195
131 | 2717588.797 | 1258769.492 | 2717586.6377 | 1258773.9352
132 | 2717469.3702 | 1258666.2878 | 2717443.0524 | 1258670.6861
133 | 2717659.2458 | 1258776.3665 | 2717657.8735 | 1258775.8195
134 | 2717586.6377 | 1258773.9352 | 2717583.796 | 1258779.7826
135 | 2717581.9658 | 1258785.7441 | 2717583.796 | 1258779.7826 | 2717583.796 | 1258779.7826
136 | 2717711.9075 | 1258528.3134 | 2717718.2227 | 1258535.443
137 | 2717718.2227 | 1258535.443 | 2717718.2227 | 1258535.443 | 2717725.2545 | 1258548.6433
138 | 2717725.2545 | 1258548.6433 | 2717728.6465 | 1258555.011
139 | 2717728.6465 | 1258555.011 | 2717743.4836 | 1258582.8637
140 | 2717756.357 | 1258607.0302 | 2717743.4836 | 1258582.8637
141 | 2717756.357 | 1258607.0302 | 2717761.5031 | 1258616.1303
142 | 2717756.357 | 1258607.0302 | 2717774.9297 | 1258590.2287
143 | 2717667.0477 | 1258829.7822 | 2717654.0569 | 1258823.8214
144 | 2717641.4909 | 1258818.0555 | 2717654.0569 | 1258823.8214
145 | 2717614.9167 | 1258871.1246 | 2717602.8461 | 1258872.9307 | 2717601.5753 | 1258873.1143
146 | 2717614.9167 | 1258871.1246 | 2717637.7839 | 1258874.6933 | 2717648.1799 | 1258884.6641 | 2717649.9938 | 1258892.304
147 | 2717578.5562 | 1258876.4401 | 2717601.5753 | 1258873.1143
148 | 2717649.9938 | 1258892.304 | 2717651.443 | 1258898.4076 | 2717653.9477 | 1258915.2363
149 | 2717578.5562 | 1258876.4401 | 2717581.7618 | 1258902.413
150 | 2717578.5562 | 1258876.4401 | 2717577.3861 | 1258861.1004
151 | 2717656.9751 | 1258935.5776 | 2717653.9477 | 1258915.2363
152 | 2717583.5084 | 1258916.5652 | 2717581.7618 | 1258902.413
153 | 2717575.2668 | 1258822.5244 | 2717574.8597 | 1258827.9802 | 2717577.3861 | 1258861.1004
154 | 2717660.1742 | 1258957.0718 | 2717656.9751 | 1258935.5776
155 | 2717583.5084 | 1258916.5652 | 2717585.7366 | 1258934.6191
156 | 2717575.2668 | 1258822.5244 | 2717576.7411 | 1258802.7624 | 2717581.9336 | 1258785.8489
157 | 2717581.9336 | 1258785.8489 | 2717581.9658 | 1258785.7441
158 | 2717585.7366 | 1258934.6191 | 2717586.3628 | 1258939.6928
159 | 2717588.2961 | 1258955.3581 | 2717586.3628 | 1258939.6928
160 | 2717588.2961 | 1258955.3581 | 2717588.9469 | 1258960.6306 | 2717590.8024 | 1258975.352

## bus_geodata
| x | y | coords
0 | 2718188.0412 | 1258835.115
1 | 2718214.2613 | 1258840.8612
2 | 2718163.1715 | 1258829.6646
3 | 2718233.866 | 1258825.0613
4 | 2718043.9656 | 1258917.8959
5 | 2718236.4044 | 1258823.015
6 | 2718024.5431 | 1258908.8693
7 | 2717907.077 | 1258854.359
8 | 2717914.2805 | 1258839.4537
9 | 2717899.1706 | 1258870.7185
10 | 2717740.9749 | 1258871.8088
11 | 2717724.0892 | 1258864.3589
12 | 2717743.201 | 1258872.7909
13 | 2717720.1092 | 1258862.6029
14 | 2717760.9624 | 1258880.6272
15 | 2717713.2859 | 1258859.5925
16 | 2717761.7601 | 1258880.9792
17 | 2717714.9275 | 1258851.7516
18 | 2717720.1591 | 1258840.4652
19 | 2717685.8275 | 1258838.3992
20 | 2717733.8054 | 1258811.0251
21 | 2717679.6859 | 1258835.5812
22 | 2717784.1893 | 1258836.0274
23 | 2717801.3675 | 1258844.5518
24 | 2717779.3454 | 1258833.6237
25 | 2717806.8758 | 1258847.2852
26 | 2717758.7798 | 1258823.4183
27 | 2717825.8627 | 1258856.7072
28 | 2717756.7794 | 1258822.4256
29 | 2717834.2384 | 1258860.8635
30 | 2717722.0824 | 1258805.0003
31 | 2717695.4317 | 1258791.3036
32 | 2717750.0643 | 1258777.2065
33 | 2717756.1696 | 1258764.5075
34 | 2717686.2487 | 1258787.1286
35 | 2717743.2193 | 1258757.1304
36 | 2717772.1459 | 1258772.0804
37 | 2717793.3231 | 1258954.1387
38 | 2717823.3401 | 1258961.3773
39 | 2717840.3436 | 1258965.4777
40 | 2717853.1597 | 1258965.9218
41 | 2717864.9043 | 1258941.6206
42 | 2717874.3861 | 1258922.0012
43 | 2717886.0191 | 1258897.9309
44 | 2717886.6066 | 1258896.7151
45 | 2717896.4876 | 1258876.2699
46 | 2717916.1665 | 1258835.4791
47 | 2717900.9568 | 1258833.1381
48 | 2717927.6575 | 1258811.2616
49 | 2717927.9532 | 1258810.6383
50 | 2717873.2898 | 1258820.0237
51 | 2717848.5649 | 1258808.3038
52 | 2717930.5024 | 1258805.2658
53 | 2717823.2405 | 1258796.2998
54 | 2717935.8482 | 1258793.9996
55 | 2717923.4748 | 1258787.6831
56 | 2717939.4583 | 1258786.8652
57 | 2717902.7898 | 1258777.1236
58 | 2717956.9178 | 1258752.3611
59 | 2717900.7673 | 1258776.0912
60 | 2717974.7175 | 1258761.1022
61 | 2717944.2778 | 1258745.9077
62 | 2717923.583 | 1258735.342
63 | 2717921.9539 | 1258734.5102
64 | 2717881.4262 | 1258766.2178
65 | 2717897.8661 | 1258722.2151
66 | 2717897.7883 | 1258722.1764
67 | 2717876.7958 | 1258711.7539
68 | 2717871.9537 | 1258761.3822
69 | 2717859.9898 | 1258755.2747
70 | 2717871.8716 | 1258709.309
71 | 2717851.8981 | 1258699.3924
72 | 2717847.7939 | 1258749.1302
73 | 2717835.7012 | 1258743.3092
74 | 2717850.9948 | 1258698.9439
75 | 2717828.9875 | 1258688.0175
76 | 2717827.1206 | 1258739.1787
77 | 2717815.1249 | 1258733.4044
78 | 2717820.7403 | 1258683.9229
79 | 2717805.0497 | 1258671.1282
80 | 2717797.0099 | 1258663.8233
81 | 2717775.3218 | 1258639.0873
82 | 2717805.8625 | 1258728.9458
83 | 2717793.1535 | 1258722.8281
84 | 2717784.3354 | 1258718.5833
85 | 2717770.1897 | 1258711.774
86 | 2717762.9226 | 1258705.7503
87 | 2717798.3851 | 1258784.5181
88 | 2717801.0527 | 1258785.7825
89 | 2717819.4433 | 1258794.4999
90 | 2717725.4472 | 1258746.5808
91 | 2717720.5154 | 1258743.1842
92 | 2717678.2048 | 1258783.9227
93 | 2717749.8711 | 1258694.9319
94 | 2717735.3668 | 1258680.7756
95 | 2717709.302 | 1258735.4611
96 | 2717731.8546 | 1258676.0115
97 | 2717719.4817 | 1258659.2282
98 | 2717696.7088 | 1258722.1199
99 | 2717692.6044 | 1258717.7717
100 | 2717713.6451 | 1258651.3111
101 | 2717702.4345 | 1258636.1044
102 | 2717687.0945 | 1258711.9345
103 | 2717674.982 | 1258699.1026
104 | 2717694.3974 | 1258626.2268
105 | 2717685.8492 | 1258616.3708
106 | 2717671.494 | 1258695.4074
107 | 2717658.5302 | 1258682.9475
108 | 2717658.0821 | 1258682.6049
109 | 2717641.748 | 1258670.1169
110 | 2717636.8971 | 1258679.1914
111 | 2717653.7957 | 1258642.3368
112 | 2717669.6391 | 1258605.8045
113 | 2717677.3041 | 1258587.6236
114 | 2717665.2545 | 1258615.9146
115 | 2717694.7779 | 1258545.4775
116 | 2717699.9011 | 1258523.5572
117 | 2717624.666 | 1258702.0718
118 | 2717610.5178 | 1258694.4374
119 | 2717618.9085 | 1258712.5688
120 | 2717489.8176 | 1258662.8706
121 | 2717612.0205 | 1258725.1268
122 | 2717597.4293 | 1258751.7292
123 | 2717625.6644 | 1258762.9824
124 | 2717595.3197 | 1258756.07
125 | 2717628.1834 | 1258763.9864
126 | 2717588.797 | 1258769.492
127 | 2717469.3702 | 1258666.2878
128 | 2717484.8631 | 1258613.6304
129 | 2717443.0524 | 1258670.6861
130 | 2717657.8735 | 1258775.8195
131 | 2717586.6377 | 1258773.9352
132 | 2717659.2458 | 1258776.3665
133 | 2717583.796 | 1258779.7826
134 | 2717711.9075 | 1258528.3134
135 | 2717718.2227 | 1258535.443
136 | 2717725.2545 | 1258548.6433
137 | 2717728.6465 | 1258555.011
138 | 2717743.4836 | 1258582.8637
139 | 2717756.357 | 1258607.0302
140 | 2717761.5031 | 1258616.1303
141 | 2717774.9297 | 1258590.2287
142 | 2717667.0477 | 1258829.7822
143 | 2717654.0569 | 1258823.8214
144 | 2717641.4909 | 1258818.0555
145 | 2717614.9167 | 1258871.1246
146 | 2717601.5753 | 1258873.1143
147 | 2717649.9938 | 1258892.304
148 | 2717578.5562 | 1258876.4401
149 | 2717653.9477 | 1258915.2363
150 | 2717581.7618 | 1258902.413
151 | 2717577.3861 | 1258861.1004
152 | 2717656.9751 | 1258935.5776
153 | 2717583.5084 | 1258916.5652
154 | 2717575.2668 | 1258822.5244
155 | 2717660.1742 | 1258957.0718
156 | 2717581.9658 | 1258785.7441
157 | 2717581.9336 | 1258785.8489
158 | 2717585.7366 | 1258934.6191
159 | 2717586.3628 | 1258939.6928
160 | 2717588.2961 | 1258955.3581
161 | 2717590.8024 | 1258975.352
162 | 2717733.8054 | 1258811.0251

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1