## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4761-6_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4761-6_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4761-6_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4761-6_0_5_node_88 | 0.4 | n |  | TRUE
4 | bus_LV_4761-6_0_5_node_86 | 0.4 | n |  | TRUE
5 | bus_LV_4761-6_0_5_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_4761-6_0_5_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_4761-6_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_4761-6_0_5_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_4761-6_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_4761-6_0_5_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_4761-6_0_5_node_143 | 0.4 | n |  | TRUE
12 | bus_LV_4761-6_0_5_node_148 | 0.4 | n |  | TRUE
13 | bus_LV_4761-6_0_5_node_142 | 0.4 | n |  | TRUE
14 | bus_LV_4761-6_0_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_4761-6_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_4761-6_0_5_node_84 | 0.4 | n |  | TRUE
17 | bus_LV_4761-6_0_5_node_79 | 0.4 | n |  | TRUE
18 | bus_LV_4761-6_0_5_node_133 | 0.4 | n |  | TRUE
19 | bus_LV_4761-6_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_4761-6_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_4761-6_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_4761-6_0_5_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_4761-6_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_4761-6_0_5_node_107 | 0.4 | n |  | TRUE
25 | bus_LV_4761-6_0_5_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_4761-6_0_5_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_4761-6_0_5_node_105 | 0.4 | n |  | TRUE
28 | bus_LV_4761-6_0_5_node_152 | 0.4 | n |  | TRUE
29 | bus_LV_4761-6_0_5_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_4761-6_0_5_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_4761-6_0_5_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_4761-6_0_5_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_4761-6_0_5_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_4761-6_0_5_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_4761-6_0_5_node_45 | 0.4 | n |  | TRUE
36 | bus_LV_4761-6_0_5_node_46 | 0.4 | n |  | TRUE
37 | bus_LV_4761-6_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_4761-6_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_4761-6_0_5_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_4761-6_0_5_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_4761-6_0_5_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_4761-6_0_5_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_4761-6_0_5_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_4761-6_0_5_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_4761-6_0_5_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_4761-6_0_5_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_4761-6_0_5_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_4761-6_0_5_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_4761-6_0_5_node_57 | 0.4 | n |  | TRUE
50 | bus_LV_4761-6_0_5_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_4761-6_0_5_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_4761-6_0_5_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_4761-6_0_5_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_4761-6_0_5_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_4761-6_0_5_node_58 | 0.4 | n |  | TRUE
56 | bus_LV_4761-6_0_5_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_4761-6_0_5_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_4761-6_0_5_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_4761-6_0_5_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_4761-6_0_5_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_4761-6_0_5_node_64 | 0.4 | n |  | TRUE
62 | bus_LV_4761-6_0_5_node_62 | 0.4 | n |  | TRUE
63 | bus_LV_4761-6_0_5_node_154 | 0.4 | n |  | TRUE
64 | bus_LV_4761-6_0_5_node_155 | 0.4 | n |  | TRUE
65 | bus_LV_4761-6_0_5_node_156 | 0.4 | n |  | TRUE
66 | bus_LV_4761-6_0_5_node_157 | 0.4 | n |  | TRUE
67 | bus_LV_4761-6_0_5_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_4761-6_0_5_node_103 | 0.4 | n |  | TRUE
69 | bus_LV_4761-6_0_5_node_97 | 0.4 | n |  | TRUE
70 | bus_LV_4761-6_0_5_node_54 | 0.4 | n |  | TRUE
71 | bus_LV_4761-6_0_5_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_4761-6_0_5_node_55 | 0.4 | n |  | TRUE
73 | bus_LV_4761-6_0_5_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_4761-6_0_5_node_59 | 0.4 | n |  | TRUE
75 | bus_LV_4761-6_0_5_node_100 | 0.4 | n |  | TRUE
76 | bus_LV_4761-6_0_5_node_147 | 0.4 | n |  | TRUE
77 | bus_LV_4761-6_0_5_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_4761-6_0_5_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_4761-6_0_5_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_4761-6_0_5_node_85 | 0.4 | n |  | TRUE
81 | bus_LV_4761-6_0_5_node_102 | 0.4 | n |  | TRUE
82 | bus_LV_4761-6_0_5_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_4761-6_0_5_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_4761-6_0_5_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_4761-6_0_5_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_4761-6_0_5_node_94 | 0.4 | n |  | TRUE
87 | bus_LV_4761-6_0_5_node_71 | 0.4 | n |  | TRUE
88 | bus_LV_4761-6_0_5_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_4761-6_0_5_node_93 | 0.4 | n |  | TRUE
90 | bus_LV_4761-6_0_5_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_4761-6_0_5_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_4761-6_0_5_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_4761-6_0_5_node_72 | 0.4 | n |  | TRUE
94 | bus_LV_4761-6_0_5_node_101 | 0.4 | n |  | TRUE
95 | bus_LV_4761-6_0_5_node_89 | 0.4 | n |  | TRUE
96 | bus_LV_4761-6_0_5_node_90 | 0.4 | n |  | TRUE
97 | bus_LV_4761-6_0_5_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_4761-6_0_5_node_92 | 0.4 | n |  | TRUE
99 | bus_LV_4761-6_0_5_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_4761-6_0_5_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_4761-6_0_5_node_76 | 0.4 | n |  | TRUE
102 | bus_LV_4761-6_0_5_node_77 | 0.4 | n |  | TRUE
103 | bus_LV_4761-6_0_5_node_78 | 0.4 | n |  | TRUE
104 | bus_LV_4761-6_0_5_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_4761-6_0_5_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_4761-6_0_5_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_4761-6_0_5_node_82 | 0.4 | n |  | TRUE
108 | bus_LV_4761-6_0_5_node_96 | 0.4 | n |  | TRUE
109 | bus_LV_4761-6_0_5_node_161 | 0.4 | n |  | TRUE
110 | bus_LV_4761-6_0_5_node_160 | 0.4 | n |  | TRUE
111 | bus_LV_4761-6_0_5_node_95 | 0.4 | n |  | TRUE
112 | bus_LV_4761-6_0_5_node_123 | 0.4 | n |  | TRUE
113 | bus_LV_4761-6_0_5_node_124 | 0.4 | n |  | TRUE
114 | bus_LV_4761-6_0_5_node_146 | 0.4 | n |  | TRUE
115 | bus_LV_4761-6_0_5_node_159 | 0.4 | n |  | TRUE
116 | bus_LV_4761-6_0_5_node_104 | 0.4 | n |  | TRUE
117 | bus_LV_4761-6_0_5_node_106 | 0.4 | n |  | TRUE
118 | bus_LV_4761-6_0_5_node_108 | 0.4 | n |  | TRUE
119 | bus_LV_4761-6_0_5_node_109 | 0.4 | n |  | TRUE
120 | bus_LV_4761-6_0_5_node_110 | 0.4 | n |  | TRUE
121 | bus_LV_4761-6_0_5_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_4761-6_0_5_node_112 | 0.4 | n |  | TRUE
123 | bus_LV_4761-6_0_5_node_113 | 0.4 | n |  | TRUE
124 | bus_LV_4761-6_0_5_node_120 | 0.4 | n |  | TRUE
125 | bus_LV_4761-6_0_5_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_4761-6_0_5_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_4761-6_0_5_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_4761-6_0_5_node_116 | 0.4 | n |  | TRUE
129 | bus_LV_4761-6_0_5_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_4761-6_0_5_node_118 | 0.4 | n |  | TRUE
131 | bus_LV_4761-6_0_5_node_122 | 0.4 | n |  | TRUE
132 | bus_LV_4761-6_0_5_node_151 | 0.4 | n |  | TRUE
133 | bus_LV_4761-6_0_5_node_121 | 0.4 | n |  | TRUE
134 | bus_LV_4761-6_0_5_node_150 | 0.4 | n |  | TRUE
135 | bus_LV_4761-6_0_5_node_125 | 0.4 | n |  | TRUE
136 | bus_LV_4761-6_0_5_node_126 | 0.4 | n |  | TRUE
137 | bus_LV_4761-6_0_5_node_127 | 0.4 | n |  | TRUE
138 | bus_LV_4761-6_0_5_node_128 | 0.4 | n |  | TRUE
139 | bus_LV_4761-6_0_5_node_129 | 0.4 | n |  | TRUE
140 | bus_LV_4761-6_0_5_node_130 | 0.4 | n |  | TRUE
141 | bus_LV_4761-6_0_5_node_131 | 0.4 | n |  | TRUE
142 | bus_LV_4761-6_0_5_node_132 | 0.4 | n |  | TRUE
143 | bus_LV_4761-6_0_5_node_134 | 0.4 | n |  | TRUE
144 | bus_LV_4761-6_0_5_node_141 | 0.4 | n |  | TRUE
145 | bus_LV_4761-6_0_5_node_140 | 0.4 | n |  | TRUE
146 | bus_LV_4761-6_0_5_node_135 | 0.4 | n |  | TRUE
147 | bus_LV_4761-6_0_5_node_136 | 0.4 | n |  | TRUE
148 | bus_LV_4761-6_0_5_node_137 | 0.4 | n |  | TRUE
149 | bus_LV_4761-6_0_5_node_138 | 0.4 | n |  | TRUE
150 | bus_LV_4761-6_0_5_node_139 | 0.4 | n |  | TRUE
151 | bus_LV_4761-6_0_5_node_144 | 0.4 | n |  | TRUE
152 | bus_LV_4761-6_0_5_node_145 | 0.4 | n |  | TRUE
153 | bus_MV_443_0_node_62 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4761-6_0_5_load_0 | 0 | 0.010258 | 0.0025709 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4761-6_0_5_load_1 | 1 | 0.0011645 | 0.00029184 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4761-6_0_5_load_86 | 4 | 0.0043086 | 0.0010798 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4761-6_0_5_load_3 | 5 | 0.013608 | 0.0034105 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4761-6_0_5_load_4 | 6 | 0.0078838 | 0.0019759 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4761-6_0_5_load_7 | 9 | 0.0022852 | 0.00057272 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4761-6_0_5_load_148 | 12 | 0.0019271 | 0.00048298 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4761-6_0_5_load_142 | 13 | 0.0042721 | 0.0010707 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4761-6_0_5_load_6 | 14 | 0.016042 | 0.0040206 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4761-6_0_5_load_10 | 15 | 0.0089522 | 0.0022436 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4761-6_0_5_load_84 | 16 | 0.0087734 | 0.0021988 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4761-6_0_5_load_79 | 17 | 0.0088343 | 0.0022141 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4761-6_0_5_load_133 | 18 | 0.005685 | 0.0014248 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4761-6_0_5_load_13 | 19 | 0.00028668 | 7.1848e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4761-6_0_5_load_14 | 20 | 0.0020023 | 0.00050181 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4761-6_0_5_load_15 | 21 | 0.00052559 | 0.00013173 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4761-6_0_5_load_42 | 22 | 0.00065932 | 0.00016524 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4761-6_0_5_load_16 | 23 | 0.00052534 | 0.00013166 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4761-6_0_5_load_107 | 24 | 0.0084229 | 0.002111 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4761-6_0_5_load_33 | 25 | 0.0008447 | 0.0002117 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4761-6_0_5_load_105 | 27 | 0.0024827 | 0.00062224 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4761-6_0_5_load_152 | 28 | 0.002238 | 0.0005609 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4761-6_0_5_load_17 | 29 | 0.0018382 | 0.0004607 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4761-6_0_5_load_18 | 30 | 0.0035325 | 0.00088532 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4761-6_0_5_load_19 | 31 | 0.001839 | 0.0004609 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4761-6_0_5_load_20 | 32 | 0.0024568 | 0.00061574 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4761-6_0_5_load_21 | 33 | 0.0018326 | 0.00045929 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4761-6_0_5_load_22 | 34 | 0.0033023 | 0.00082762 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4761-6_0_5_load_45 | 35 | 0.0018323 | 0.00045923 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4761-6_0_5_load_23 | 37 | 0.00096773 | 0.00024254 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4761-6_0_5_load_24 | 38 | 0.0021833 | 0.00054719 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4761-6_0_5_load_29 | 43 | 0.0030806 | 0.00077207 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4761-6_0_5_load_40 | 44 | 0.0017339 | 0.00043456 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4761-6_0_5_load_37 | 45 | 0.0019063 | 0.00047777 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4761-6_0_5_load_34 | 46 | 0.001891 | 0.00047392 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4761-6_0_5_load_51 | 48 | 0.0075988 | 0.0019044 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4761-6_0_5_load_57 | 49 | 0.0049359 | 0.0012371 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4761-6_0_5_load_49 | 50 | 0.0015637 | 0.0003919 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4761-6_0_5_load_38 | 51 | 0.0020277 | 0.00050819 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4761-6_0_5_load_47 | 52 | 0.0016566 | 0.00041519 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4761-6_0_5_load_58 | 55 | 0.0049322 | 0.0012361 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4761-6_0_5_load_30 | 56 | 0.0012638 | 0.00031673 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4761-6_0_5_load_31 | 57 | 0.00054043 | 0.00013544 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4761-6_0_5_load_36 | 58 | 0.0026328 | 0.00065984 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4761-6_0_5_load_50 | 59 | 0.0020229 | 0.000507 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4761-6_0_5_load_39 | 60 | 0.0019039 | 0.00047716 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4761-6_0_5_load_64 | 61 | 0.0020267 | 0.00050794 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4761-6_0_5_load_62 | 62 | 0.001963 | 0.00049198 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4761-6_0_5_load_155 | 64 | 0.001144 | 0.00028671 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4761-6_0_5_load_156 | 65 | 0.00022879 | 5.7341e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4761-6_0_5_load_157 | 66 | 0.00039087 | 9.7962e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4761-6_0_5_load_103 | 68 | 0.0063103 | 0.0015815 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4761-6_0_5_load_97 | 69 | 0.0063097 | 0.0015814 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4761-6_0_5_load_54 | 70 | 0.007615 | 0.0019085 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4761-6_0_5_load_53 | 71 | 0.0076108 | 0.0019074 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4761-6_0_5_load_55 | 72 | 0.0024653 | 0.00061787 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4761-6_0_5_load_100 | 75 | 0.0028681 | 0.0007188 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4761-6_0_5_load_147 | 76 | 0.0019921 | 0.00049927 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4761-6_0_5_load_60 | 77 | 0.0020298 | 0.00050871 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4761-6_0_5_load_61 | 78 | 0.0018455 | 0.00046253 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4761-6_0_5_load_63 | 79 | 0.0032583 | 0.00081661 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4761-6_0_5_load_65 | 82 | 0.0026125 | 0.00065475 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4761-6_0_5_load_66 | 83 | 0.0053035 | 0.0013292 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4761-6_0_5_load_67 | 84 | 0.0082523 | 0.0020682 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4761-6_0_5_load_80 | 88 | 0.01281 | 0.0032105 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4761-6_0_5_load_73 | 90 | 0.0050957 | 0.0012771 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4761-6_0_5_load_69 | 91 | 0.0051959 | 0.0013022 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4761-6_0_5_load_70 | 92 | 0.0053035 | 0.0013292 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4761-6_0_5_load_101 | 94 | 0.003985 | 0.00099875 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4761-6_0_5_load_90 | 96 | 0.0049123 | 0.0012311 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4761-6_0_5_load_87 | 97 | 0.0095483 | 0.002393 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4761-6_0_5_load_92 | 98 | 0.0089512 | 0.0022434 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4761-6_0_5_load_91 | 99 | 0.0087776 | 0.0021999 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4761-6_0_5_load_75 | 100 | 0.010622 | 0.0026621 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4761-6_0_5_load_76 | 101 | 0.0093181 | 0.0023353 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4761-6_0_5_load_78 | 103 | 0.0091603 | 0.0022958 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4761-6_0_5_load_98 | 104 | 0.0068161 | 0.0017083 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4761-6_0_5_load_99 | 105 | 0.0071661 | 0.001796 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4761-6_0_5_load_81 | 106 | 0.016638 | 0.0041699 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4761-6_0_5_load_96 | 108 | 0.0063097 | 0.0015814 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4761-6_0_5_load_161 | 109 | 0.010202 | 0.0025568 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4761-6_0_5_load_160 | 110 | 0.0020612 | 0.00051658 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4761-6_0_5_load_95 | 111 | 0.012908 | 0.0032351 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4761-6_0_5_load_123 | 112 | 0.0066978 | 0.0016786 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4761-6_0_5_load_124 | 113 | 0.018273 | 0.0045796 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4761-6_0_5_load_146 | 114 | 0.0025045 | 0.00062768 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4761-6_0_5_load_159 | 115 | 0.0019995 | 0.00050111 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4761-6_0_5_load_104 | 116 | 0.0013248 | 0.00033203 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4761-6_0_5_load_106 | 117 | 0.00095527 | 0.00023941 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4761-6_0_5_load_108 | 118 | 0.0016023 | 0.00040158 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4761-6_0_5_load_109 | 119 | 0.002072 | 0.00051929 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4761-6_0_5_load_111 | 121 | 0.0022636 | 0.0005673 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4761-6_0_5_load_112 | 122 | 0.0022636 | 0.0005673 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4761-6_0_5_load_113 | 123 | 0.0017303 | 0.00043366 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4761-6_0_5_load_120 | 124 | 0.0017293 | 0.0004334 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4761-6_0_5_load_119 | 125 | 0.00173 | 0.00043358 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4761-6_0_5_load_114 | 126 | 0.0014253 | 0.00035722 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4761-6_0_5_load_115 | 127 | 0.0014244 | 0.00035698 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4761-6_0_5_load_116 | 128 | 0.0014561 | 0.00036492 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4761-6_0_5_load_117 | 129 | 0.0023511 | 0.00058925 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4761-6_0_5_load_118 | 130 | 0.0023702 | 0.00059403 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4761-6_0_5_load_122 | 131 | 0.0029113 | 0.00072964 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4761-6_0_5_load_151 | 132 | 0.0019965 | 0.00050037 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4761-6_0_5_load_121 | 133 | 0.0030693 | 0.00076923 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4761-6_0_5_load_150 | 134 | 0.0023809 | 0.00059672 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4761-6_0_5_load_125 | 135 | 0.007294 | 0.001828 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4761-6_0_5_load_126 | 136 | 0.015581 | 0.0039049 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4761-6_0_5_load_127 | 137 | 0.0066978 | 0.0016786 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4761-6_0_5_load_128 | 138 | 0.0086915 | 0.0021783 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4761-6_0_5_load_129 | 139 | 0.0011 | 0.00027569 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4761-6_0_5_load_130 | 140 | 0.0010257 | 0.00025707 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4761-6_0_5_load_132 | 142 | 0.0011003 | 0.00027575 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4761-6_0_5_load_134 | 143 | 0.001146 | 0.00028721 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4761-6_0_5_load_141 | 144 | 0.0011596 | 0.00029063 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4761-6_0_5_load_140 | 145 | 0.0011596 | 0.00029063 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4761-6_0_5_load_135 | 146 | 0.0011608 | 0.00029093 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4761-6_0_5_load_136 | 147 | 0.00087941 | 0.0002204 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4761-6_0_5_load_137 | 148 | 0.001162 | 0.00029123 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4761-6_0_5_load_138 | 149 | 0.0019474 | 0.00048807 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4761-6_0_5_load_139 | 150 | 0.0011596 | 0.00029062 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4761-6_0_5_load_144 | 151 | 0.001673 | 0.0004193 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4761-6_0_5_load_145 | 152 | 0.0028788 | 0.0007215 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 92 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4761-6_0_5_line_0 |  | 0 | 1 | 0.097019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4761-6_0_5_line_1 |  | 1 | 2 | 0.030546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4761-6_0_5_line_2 |  | 2 | 3 | 0.084683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4761-6_0_5_line_3 |  | 3 | 4 | 0.046996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4761-6_0_5_line_4 |  | 4 | 97 | 0.024619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4761-6_0_5_line_5 |  | 5 | 6 | 0.0061063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4761-6_0_5_line_6 |  | 6 | 7 | 0.061062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4761-6_0_5_line_7 |  | 7 | 8 | 0.028821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_4761-6_0_5_line_8 |  | 7 | 9 | 0.018009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4761-6_0_5_line_9 |  | 8 | 11 | 0.011193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_4761-6_0_5_line_10 |  | 8 | 13 | 0.062269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4761-6_0_5_line_11 |  | 9 | 14 | 0.019557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4761-6_0_5_line_12 |  | 10 | 11 | 0.006416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4761-6_0_5_line_13 |  | 10 | 12 | 0.010188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4761-6_0_5_line_14 |  | 11 | 18 | 0.016121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_4761-6_0_5_line_15 |  | 15 | 16 | 0.033539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4761-6_0_5_line_16 |  | 16 | 17 | 0.0014322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4761-6_0_5_line_17 |  | 17 | 102 | 0.017764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4761-6_0_5_line_18 |  | 18 | 141 | 0.020553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_4761-6_0_5_line_19 |  | 19 | 20 | 0.020482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_4761-6_0_5_line_20 |  | 19 | 21 | 0.022119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_4761-6_0_5_line_21 |  | 20 | 22 | 0.026135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_4761-6_0_5_line_22 |  | 21 | 23 | 0.022813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4761-6_0_5_line_23 |  | 21 | 24 | 0.057362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_4761-6_0_5_line_24 |  | 22 | 25 | 0.018626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_4761-6_0_5_line_25 |  | 23 | 26 | 0.055891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4761-6_0_5_line_26 |  | 24 | 27 | 0.060945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_4761-6_0_5_line_27 |  | 25 | 57 | 0.022864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_4761-6_0_5_line_28 |  | 26 | 28 | 0.25395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4761-6_0_5_line_29 |  | 27 | 116 | 0.020338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_4761-6_0_5_line_30 |  | 28 | 63 | 0.029376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4761-6_0_5_line_31 |  | 29 | 30 | 0.019553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4761-6_0_5_line_32 |  | 29 | 31 | 0.007978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4761-6_0_5_line_33 |  | 30 | 32 | 0.037895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4761-6_0_5_line_34 |  | 31 | 33 | 0.016448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4761-6_0_5_line_35 |  | 32 | 34 | 0.021506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4761-6_0_5_line_36 |  | 33 | 35 | 0.0079567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4761-6_0_5_line_37 |  | 35 | 36 | 0.013323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4761-6_0_5_line_38 |  | 36 | 67 | 0.012834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_4761-6_0_5_line_39 |  | 36 | 52 | 0.029851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_4761-6_0_5_line_40 |  | 37 | 38 | 0.023753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4761-6_0_5_line_41 |  | 37 | 39 | 0.013006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4761-6_0_5_line_42 |  | 38 | 40 | 0.013933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4761-6_0_5_line_43 |  | 39 | 41 | 0.018884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_4761-6_0_5_line_44 |  | 39 | 42 | 0.004708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_4761-6_0_5_line_45 |  | 39 | 43 | 0.031211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_4761-6_0_5_line_46 |  | 40 | 44 | 0.002557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4761-6_0_5_line_47 |  | 40 | 45 | 0.019266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4761-6_0_5_line_48 |  | 41 | 46 | 0.016098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_4761-6_0_5_line_49 |  | 42 | 47 | 0.026664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_4761-6_0_5_line_50 |  | 42 | 48 | 0.016871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4761-6_0_5_line_51 |  | 43 | 49 | 0.033469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_4761-6_0_5_line_52 |  | 44 | 50 | 0.025252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4761-6_0_5_line_53 |  | 45 | 51 | 0.0077696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4761-6_0_5_line_54 |  | 46 | 53 | 0.037429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_4761-6_0_5_line_55 |  | 47 | 52 | 0.0086609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_4761-6_0_5_line_56 |  | 48 | 54 | 0.022668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4761-6_0_5_line_57 |  | 49 | 55 | 0.027548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_4761-6_0_5_line_58 |  | 51 | 60 | 0.015595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4761-6_0_5_line_59 |  | 53 | 58 | 0.0056527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4761-6_0_5_line_60 |  | 53 | 56 | 0.019716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_4761-6_0_5_line_61 |  | 54 | 70 | 0.019616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4761-6_0_5_line_62 |  | 55 | 74 | 0.030418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_4761-6_0_5_line_63 |  | 56 | 57 | 0.021591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_4761-6_0_5_line_64 |  | 58 | 59 | 0.038414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4761-6_0_5_line_65 |  | 60 | 61 | 0.0068497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4761-6_0_5_line_66 |  | 61 | 62 | 0.016827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4761-6_0_5_line_67 |  | 62 | 77 | 0.0060001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4761-6_0_5_line_68 |  | 63 | 64 | 0.019647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4761-6_0_5_line_69 |  | 64 | 65 | 0.011905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4761-6_0_5_line_70 |  | 65 | 66 | 0.01544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4761-6_0_5_line_71 |  | 67 | 68 | 0.054341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_4761-6_0_5_line_72 |  | 68 | 69 | 0.034029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_4761-6_0_5_line_73 |  | 69 | 108 | 0.03418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_4761-6_0_5_line_74 |  | 69 | 107 | 0.074133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4761-6_0_5_line_75 |  | 71 | 72 | 0.030483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4761-6_0_5_line_76 |  | 72 | 73 | 0.0055895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4761-6_0_5_line_77 |  | 73 | 74 | 0.005638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4761-6_0_5_line_78 |  | 74 | 75 | 0.0081752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_4761-6_0_5_line_79 |  | 75 | 76 | 0.022158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_4761-6_0_5_line_80 |  | 76 | 114 | 0.018201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_4761-6_0_5_line_81 |  | 77 | 78 | 0.018784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4761-6_0_5_line_82 |  | 78 | 79 | 0.0057667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4761-6_0_5_line_83 |  | 79 | 80 | 0.02185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4761-6_0_5_line_84 |  | 80 | 81 | 0.01384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4761-6_0_5_line_85 |  | 81 | 109 | 0.021163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4761-6_0_5_line_86 |  | 81 | 110 | 0.021177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4761-6_0_5_line_87 |  | 82 | 83 | 0.018643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4761-6_0_5_line_88 |  | 82 | 84 | 0.028768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4761-6_0_5_line_89 |  | 83 | 85 | 0.028865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4761-6_0_5_line_90 |  | 85 | 86 | 0.027756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_4761-6_0_5_line_91 |  | 85 | 87 | 0.003243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_4761-6_0_5_line_92 |  | 86 | 88 | 0.036234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_4761-6_0_5_line_93 |  | 86 | 89 | 0.020683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4761-6_0_5_line_94 |  | 87 | 90 | 0.027522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_4761-6_0_5_line_95 |  | 87 | 91 | 0.016599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_4761-6_0_5_line_96 |  | 88 | 102 | 0.002826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4761-6_0_5_line_97 |  | 89 | 99 | 0.013907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4761-6_0_5_line_98 |  | 90 | 95 | 0.011241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_4761-6_0_5_line_99 |  | 91 | 92 | 0.018583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_4761-6_0_5_line_100 |  | 92 | 93 | 0.014944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4761-6_0_5_line_101 |  | 93 | 94 | 0.0082729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4761-6_0_5_line_102 |  | 95 | 96 | 0.018637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_4761-6_0_5_line_103 |  | 95 | 97 | 0.025338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4761-6_0_5_line_104 |  | 96 | 111 | 0.0033231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_4761-6_0_5_line_105 |  | 98 | 99 | 0.018757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4761-6_0_5_line_106 |  | 100 | 101 | 0.0086821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4761-6_0_5_line_107 |  | 100 | 102 | 0.039354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4761-6_0_5_line_108 |  | 101 | 103 | 0.003433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4761-6_0_5_line_109 |  | 103 | 104 | 0.026979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4761-6_0_5_line_110 |  | 104 | 105 | 0.0051517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4761-6_0_5_line_111 |  | 105 | 112 | 0.0059354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4761-6_0_5_line_112 |  | 106 | 107 | 0.014877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4761-6_0_5_line_113 |  | 108 | 111 | 0.024708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_4761-6_0_5_line_114 |  | 110 | 115 | 0.0033511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4761-6_0_5_line_115 |  | 112 | 113 | 0.0045281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4761-6_0_5_line_116 |  | 113 | 135 | 0.025288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4761-6_0_5_line_117 |  | 114 | 152 | 0.0071118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_4761-6_0_5_line_118 |  | 116 | 117 | 0.028749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_4761-6_0_5_line_119 |  | 117 | 118 | 0.031343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_4761-6_0_5_line_120 |  | 118 | 119 | 0.025509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_4761-6_0_5_line_121 |  | 119 | 120 | 0.017741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_4761-6_0_5_line_122 |  | 120 | 121 | 0.020641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_4761-6_0_5_line_123 |  | 121 | 122 | 0.015956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_4761-6_0_5_line_124 |  | 122 | 123 | 0.019884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_4761-6_0_5_line_125 |  | 123 | 124 | 0.026742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_4761-6_0_5_line_126 |  | 124 | 125 | 0.021342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4761-6_0_5_line_127 |  | 125 | 133 | 0.038486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4761-6_0_5_line_128 |  | 126 | 127 | 0.0094135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4761-6_0_5_line_129 |  | 126 | 128 | 0.024391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4761-6_0_5_line_130 |  | 127 | 129 | 0.023291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4761-6_0_5_line_131 |  | 128 | 130 | 0.015403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4761-6_0_5_line_132 |  | 129 | 131 | 0.021718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4761-6_0_5_line_133 |  | 130 | 132 | 0.026798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4761-6_0_5_line_134 |  | 131 | 133 | 0.022718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4761-6_0_5_line_135 |  | 132 | 134 | 0.018948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4761-6_0_5_line_136 |  | 135 | 136 | 0.0023305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4761-6_0_5_line_137 |  | 136 | 137 | 0.008757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4761-6_0_5_line_138 |  | 137 | 138 | 0.015207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4761-6_0_5_line_139 |  | 139 | 140 | 0.0085729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_4761-6_0_5_line_140 |  | 139 | 141 | 0.022315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_4761-6_0_5_line_141 |  | 140 | 142 | 0.0061028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
142 | LV_4761-6_0_5_line_142 |  | 141 | 143 | 0.014383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4761-6_0_5_line_143 |  | 142 | 144 | 0.0088807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
144 | LV_4761-6_0_5_line_144 |  | 144 | 145 | 0.016053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
145 | LV_4761-6_0_5_line_145 |  | 145 | 150 | 0.023306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
146 | LV_4761-6_0_5_line_146 |  | 146 | 147 | 0.0053462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
147 | LV_4761-6_0_5_line_147 |  | 146 | 148 | 0.016547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
148 | LV_4761-6_0_5_line_148 |  | 147 | 149 | 0.011559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
149 | LV_4761-6_0_5_line_149 |  | 148 | 150 | 0.0090673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
150 | LV_4761-6_0_5_line_150 |  | 149 | 151 | 0.013364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
151 | LV_4761-6_0_5_line_151 |  | 151 | 152 | 0.021491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4761-6_0_5_trafo_70 | 0.63 MVA 20/0.4 kV | 153 | 92 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2718005.2479 | 1258431.6861 | 2718069.271 | 1258504.5815
1 | 2717985.0908 | 1258408.7356 | 2718005.2479 | 1258431.6861
2 | 2718047.9033 | 1258351.9388 | 2717985.0908 | 1258408.7356
3 | 2718047.9033 | 1258351.9388 | 2718058.5989 | 1258306.1761
4 | 2718058.5989 | 1258306.1761 | 2718064.2018 | 1258282.2033
5 | 2717852.0851 | 1258202.901 | 2717857.4579 | 1258199.9994
6 | 2717891.5426 | 1258153.039 | 2717884.2109 | 1258175.0565 | 2717874.4548 | 1258190.8203 | 2717857.4579 | 1258199.9994
7 | 2717872.573 | 1258138.0483 | 2717870.236 | 1258142.5501 | 2717891.5426 | 1258153.039
8 | 2717891.5426 | 1258153.039 | 2717908.1777 | 1258159.938
9 | 2717864.3686 | 1258130.8231 | 2717869.0882 | 1258133.9197 | 2717870.4678 | 1258136.594 | 2717872.573 | 1258138.0483
10 | 2717872.573 | 1258138.0483 | 2717887.2931 | 1258146.4153 | 2717910.1364 | 1258156.2344 | 2717929.2855 | 1258163.4774
11 | 2717926.3988 | 1258167.0294 | 2717917.3173 | 1258163.7284 | 2717908.1777 | 1258159.938
12 | 2717860.8454 | 1258136.1909 | 2717864.3686 | 1258130.8231
13 | 2717860.8454 | 1258136.1909 | 2717854.9527 | 1258144.5014
14 | 2717864.3686 | 1258130.8231 | 2717874.2494 | 1258118.0853
15 | 2717967.8441 | 1258245.6862 | 2717967.0966 | 1258249.2499 | 2717961.6318 | 1258269.9144 | 2717953.6441 | 1258272.8875
16 | 2717953.6441 | 1258272.8875 | 2717952.3018 | 1258273.387 | 2717952.3018 | 1258273.387
17 | 2717964.9752 | 1258284.9051 | 2717961.2593 | 1258278.381 | 2717952.3018 | 1258273.387
18 | 2717886.8466 | 1258101.8456 | 2717874.2494 | 1258118.0853
19 | 2718387.2943 | 1258207.1851 | 2718407.7049 | 1258208.8913
20 | 2718429.74 | 1258210.8076 | 2718427.4551 | 1258210.5423 | 2718407.7049 | 1258208.8913
21 | 2718362.2679 | 1258199.6541 | 2718387.2943 | 1258207.1851
22 | 2718429.74 | 1258210.8076 | 2718452.4003 | 1258213.4382
23 | 2718422.8717 | 1258153.8583 | 2718429.74 | 1258210.8076
24 | 2718362.2679 | 1258199.6541 | 2718343.687 | 1258198.3575
25 | 2718507.7114 | 1258221.4136 | 2718467.2791 | 1258215.1655 | 2718452.4003 | 1258213.4382
26 | 2718363.8377 | 1258138.8522 | 2718405.8527 | 1258150.4692 | 2718422.8717 | 1258153.8583
27 | 2718320.8612 | 1258197.0962 | 2718330.7047 | 1258197.4516 | 2718343.687 | 1258198.3575
28 | 2718507.7114 | 1258221.4136 | 2718513.3796 | 1258475.2992
29 | 2718344.2432 | 1258133.4043 | 2718347.968 | 1258134.4643 | 2718363.8377 | 1258138.8522
30 | 2718541.8195 | 1258482.5901 | 2718520.7014 | 1258476.7288 | 2718513.3796 | 1258475.2992
31 | 2718286.0959 | 1258240.4107 | 2718304.0025 | 1258239.9547 | 2718305.6333 | 1258240.1322
32 | 2718278.1204 | 1258240.6138 | 2718286.0959 | 1258240.4107
33 | 2718343.3062 | 1258244.2318 | 2718305.6333 | 1258240.1322
34 | 2718261.6774 | 1258241.0325 | 2718278.1204 | 1258240.6138
35 | 2718364.686 | 1258246.5583 | 2718343.3062 | 1258244.2318
36 | 2718261.6774 | 1258241.0325 | 2718253.7233 | 1258241.2351
37 | 2718240.4042 | 1258241.5743 | 2718253.7233 | 1258241.2351
38 | 2718238.717 | 1258254.296 | 2718240.4042 | 1258241.5743
39 | 2718240.4042 | 1258241.5743 | 2718241.3079 | 1258232.9626 | 2718241.0831 | 1258227.9871 | 2718239.8146 | 1258224.2919 | 2718238.4013 | 1258221.806 | 2718236.1711 | 1258219.8153 | 2718232.469 | 1258218.2733 | 2718230.0876 | 1258217.7189
40 | 2718209.4057 | 1258157.0902 | 2718207.9397 | 1258180.7979
41 | 2718207.1369 | 1258193.7795 | 2718207.9397 | 1258180.7979
42 | 2718206.6856 | 1258143.9161 | 2718208.7435 | 1258146.9821 | 2718209.7668 | 1258151.2507 | 2718209.4057 | 1258157.0902
43 | 2718207.1369 | 1258193.7795 | 2718226.0734 | 1258194.158
44 | 2718206.8469 | 1258198.4777 | 2718207.1369 | 1258193.7795
45 | 2718207.1369 | 1258193.7795 | 2718175.9421 | 1258192.7884
46 | 2718206.6856 | 1258143.9161 | 2718209.1475 | 1258144.6071
47 | 2718206.6856 | 1258143.9161 | 2718201.1175 | 1258141.0246 | 2718188.553 | 1258137.7191
48 | 2718226.0734 | 1258194.158 | 2718242.1659 | 1258194.5935
49 | 2718206.8469 | 1258198.4777 | 2718206.7629 | 1258203.814 | 2718207.2078 | 1258206.8366 | 2718208.457 | 1258209.9865 | 2718209.742 | 1258211.7248 | 2718213.3685 | 1258214.0326 | 2718221.6522 | 1258215.7551
50 | 2718206.8469 | 1258198.4777 | 2718189.9795 | 1258198.1217
51 | 2718142.4901 | 1258191.7256 | 2718175.9421 | 1258192.7884
52 | 2718233.4597 | 1258151.4306 | 2718209.1475 | 1258144.6071
53 | 2718188.553 | 1258137.7191 | 2718181.039 | 1258135.7423
54 | 2718279.5808 | 1258195.606 | 2718242.1659 | 1258194.5935
55 | 2718221.6522 | 1258215.7551 | 2718230.0876 | 1258217.7189
56 | 2718167.3166 | 1258197.6433 | 2718189.9795 | 1258198.1217
57 | 2718142.4901 | 1258191.7256 | 2718114.9562 | 1258190.8508
58 | 2718165.9569 | 1258131.7745 | 2718181.039 | 1258135.7423
59 | 2718279.5808 | 1258195.606 | 2718280.084 | 1258192.6913 | 2718281.5843 | 1258190.4527
60 | 2718279.5808 | 1258195.606 | 2718299.2837 | 1258196.3173
61 | 2718166.7439 | 1258217.2489 | 2718167.3166 | 1258197.6433
62 | 2718084.554 | 1258189.8849 | 2718114.9562 | 1258190.8508
63 | 2718320.8612 | 1258197.0962 | 2718299.2837 | 1258196.3173
64 | 2718281.5843 | 1258190.4527 | 2718285.115 | 1258188.4993 | 2718287.2144 | 1258186.0947 | 2718287.6538 | 1258182.9786 | 2718287.7717 | 1258175.1964 | 2718287.1708 | 1258172.0595 | 2718286.1131 | 1258169.5139 | 2718284.4238 | 1258167.256 | 2718281.5914 | 1258165.2087 | 2718273.9216 | 1258162.9655
65 | 2718165.9569 | 1258131.7745 | 2718159.3326 | 1258130.0318
66 | 2718159.3326 | 1258130.0318 | 2718143.0592 | 1258125.7505
67 | 2718137.2566 | 1258124.2239 | 2718143.0592 | 1258125.7505
68 | 2718541.8195 | 1258482.5901 | 2718559.4029 | 1258491.3562
69 | 2718559.4029 | 1258491.3562 | 2718570.0574 | 1258496.668
70 | 2718568.6137 | 1258510.4818 | 2718571.5285 | 1258504.1595 | 2718572.4321 | 1258499.3401 | 2718570.0574 | 1258496.668 | 2718570.0574 | 1258496.668
71 | 2718238.717 | 1258254.296 | 2718233.9632 | 1258255.1907 | 2718229.4701 | 1258255.4901 | 2718184.4825 | 1258254.3996
72 | 2718184.4825 | 1258254.3996 | 2718150.4639 | 1258253.575
73 | 2718150.4639 | 1258253.575 | 2718116.2938 | 1258252.7467
74 | 2718150.4639 | 1258253.575 | 2718165.321 | 1258326.2038
75 | 2718121.9592 | 1258196.3463 | 2718091.4875 | 1258195.5136
76 | 2718085.9001 | 1258195.361 | 2718091.4875 | 1258195.5136
77 | 2718085.9001 | 1258195.361 | 2718084.554 | 1258189.8849
78 | 2718084.554 | 1258189.8849 | 2718083.6539 | 1258186.2416 | 2718080.037 | 1258183.6969
79 | 2718060.2058 | 1258174.1247 | 2718074.2833 | 1258179.6489 | 2718080.037 | 1258183.6969
80 | 2718060.2058 | 1258174.1247 | 2718043.2623 | 1258167.4758
81 | 2718137.2566 | 1258124.2239 | 2718119.0907 | 1258119.4448
82 | 2718119.0907 | 1258119.4448 | 2718113.5138 | 1258117.9776
83 | 2718092.3828 | 1258112.4184 | 2718113.5138 | 1258117.9776
84 | 2718092.3828 | 1258112.4184 | 2718078.6701 | 1258110.2652
85 | 2718057.7027 | 1258106.9664 | 2718078.6701 | 1258110.2652
86 | 2718078.6701 | 1258110.2652 | 2718074.5511 | 1258131.0382
87 | 2718017.9209 | 1258310.5007 | 2718022.0759 | 1258292.3265
88 | 2717998.0925 | 1258324.0325 | 2718008.1053 | 1258324.1322 | 2718010.8423 | 1258323.7753 | 2718012.8825 | 1258322.8152 | 2718015.1466 | 1258320.8364 | 2718015.9914 | 1258318.9405 | 2718017.9209 | 1258310.5007
89 | 2718028.5091 | 1258264.1871 | 2718022.0759 | 1258292.3265
90 | 2718001.631 | 1258271.413 | 2718028.5091 | 1258264.1871
91 | 2718031.6481 | 1258263.3378 | 2718028.5091 | 1258264.1871
92 | 2718001.631 | 1258271.413 | 2717967.6272 | 1258283.929
93 | 2717986.3572 | 1258263.6129 | 2717999.4168 | 1258264.0847 | 2718001.631 | 1258271.413
94 | 2718031.6481 | 1258263.3378 | 2718049.9622 | 1258260.8787 | 2718058.8814 | 1258259.3859
95 | 2718031.6481 | 1258263.3378 | 2718033.9421 | 1258254.1979 | 2718035.4673 | 1258247.1863
96 | 2717964.9752 | 1258284.9051 | 2717967.6272 | 1258283.929
97 | 2717986.3572 | 1258263.6129 | 2717990.8036 | 1258250.4357
98 | 2718069.9683 | 1258257.5304 | 2718058.8814 | 1258259.3859
99 | 2718035.4673 | 1258247.1863 | 2718039.4174 | 1258229.0277
100 | 2718042.594 | 1258214.4248 | 2718039.4174 | 1258229.0277
101 | 2718042.594 | 1258214.4248 | 2718050.8472 | 1258214.9956
102 | 2718069.9683 | 1258257.5304 | 2718088.4349 | 1258255.0137
103 | 2718069.9683 | 1258257.5304 | 2718064.2018 | 1258282.2033
104 | 2718091.7275 | 1258254.5649 | 2718088.4349 | 1258255.0137
105 | 2717990.8036 | 1258250.4357 | 2717996.8005 | 1258232.6633
106 | 2717929.1366 | 1258301.163 | 2717921.23 | 1258304.7497
107 | 2717964.9752 | 1258284.9051 | 2717929.1366 | 1258301.163
108 | 2717918.1036 | 1258306.168 | 2717921.23 | 1258304.7497
109 | 2717918.1036 | 1258306.168 | 2717893.5346 | 1258317.3135
110 | 2717888.8431 | 1258319.4417 | 2717890.7008 | 1258318.599 | 2717893.5346 | 1258317.3135
111 | 2717883.4378 | 1258321.8936 | 2717888.8431 | 1258319.4417
112 | 2718165.321 | 1258326.2038 | 2718161.797 | 1258340.6571
113 | 2718091.7275 | 1258254.5649 | 2718106.7645 | 1258252.5157 | 2718116.2938 | 1258252.7467
114 | 2718073.8993 | 1258134.3253 | 2718074.5511 | 1258131.0382
115 | 2717883.4378 | 1258321.8936 | 2717879.3141 | 1258323.7642
116 | 2717856.2852 | 1258334.2107 | 2717879.3141 | 1258323.7642
117 | 2718043.2623 | 1258167.4758 | 2718036.642 | 1258164.8778
118 | 2718344.2432 | 1258133.4043 | 2718316.5921 | 1258125.5351
119 | 2718286.4457 | 1258116.9557 | 2718316.5921 | 1258125.5351
120 | 2718286.4457 | 1258116.9557 | 2718267.5208 | 1258111.5699 | 2718261.9219 | 1258109.9335
121 | 2718244.8928 | 1258104.9566 | 2718261.9219 | 1258109.9335
122 | 2718244.8928 | 1258104.9566 | 2718225.341 | 1258098.3395
123 | 2718225.341 | 1258098.3395 | 2718210.2272 | 1258093.2245
124 | 2718210.2272 | 1258093.2245 | 2718191.3924 | 1258086.8501
125 | 2718166.0616 | 1258078.2773 | 2718191.3924 | 1258086.8501
126 | 2718145.8457 | 1258071.4355 | 2718166.0616 | 1258078.2773
127 | 2718145.8457 | 1258071.4355 | 2718109.3913 | 1258059.0981
128 | 2718037.6397 | 1258030.8482 | 2718046.3452 | 1258034.4299
129 | 2718015.0832 | 1258021.5675 | 2718037.6397 | 1258030.8482
130 | 2718067.8843 | 1258043.292 | 2718046.3452 | 1258034.4299
131 | 2718015.0832 | 1258021.5675 | 2718012.3776 | 1258020.4543 | 2718000.5387 | 1258016.5138
132 | 2718087.9692 | 1258051.5557 | 2718067.8843 | 1258043.292
133 | 2717975.1122 | 1258008.0507 | 2718000.5387 | 1258016.5138
134 | 2718087.9692 | 1258051.5557 | 2718091.9739 | 1258053.2034 | 2718109.3913 | 1258059.0981
135 | 2717957.1344 | 1258002.0668 | 2717975.1122 | 1258008.0507
136 | 2717856.2852 | 1258334.2107 | 2717854.1629 | 1258335.1735
137 | 2717846.188 | 1258338.791 | 2717854.1629 | 1258335.1735
138 | 2717832.3395 | 1258345.0731 | 2717846.188 | 1258338.791
139 | 2717914.7529 | 1258115.0863 | 2717907.0076 | 1258111.4114
140 | 2717886.8466 | 1258101.8456 | 2717907.0076 | 1258111.4114
141 | 2717920.2666 | 1258117.7024 | 2717914.7529 | 1258115.0863
142 | 2717886.8466 | 1258101.8456 | 2717895.2119 | 1258090.1454
143 | 2717920.2666 | 1258117.7024 | 2717928.2899 | 1258121.5092
144 | 2717928.2899 | 1258121.5092 | 2717938.6418 | 1258126.4209 | 2717942.9194 | 1258128.0995
145 | 2717964.6145 | 1258136.613 | 2717942.9194 | 1258128.0995
146 | 2717988.459 | 1258145.97 | 2717993.4357 | 1258147.923
147 | 2717973.0553 | 1258139.9253 | 2717988.459 | 1258145.97
148 | 2717993.4357 | 1258147.923 | 2718004.1958 | 1258152.1454
149 | 2717973.0553 | 1258139.9253 | 2717964.6145 | 1258136.613
150 | 2718016.6361 | 1258157.0272 | 2718004.1958 | 1258152.1454
151 | 2718016.6361 | 1258157.0272 | 2718036.642 | 1258164.8778

## bus_geodata
| x | y | coords
0 | 2718069.271 | 1258504.5815
1 | 2718005.2479 | 1258431.6861
2 | 2717985.0908 | 1258408.7356
3 | 2718047.9033 | 1258351.9388
4 | 2718058.5989 | 1258306.1761
5 | 2717852.0851 | 1258202.901
6 | 2717857.4579 | 1258199.9994
7 | 2717891.5426 | 1258153.039
8 | 2717872.573 | 1258138.0483
9 | 2717908.1777 | 1258159.938
10 | 2717860.8454 | 1258136.1909
11 | 2717864.3686 | 1258130.8231
12 | 2717854.9527 | 1258144.5014
13 | 2717929.2855 | 1258163.4774
14 | 2717926.3988 | 1258167.0294
15 | 2717967.8441 | 1258245.6862
16 | 2717953.6441 | 1258272.8875
17 | 2717952.3018 | 1258273.387
18 | 2717874.2494 | 1258118.0853
19 | 2718407.7049 | 1258208.8913
20 | 2718387.2943 | 1258207.1851
21 | 2718429.74 | 1258210.8076
22 | 2718362.2679 | 1258199.6541
23 | 2718452.4003 | 1258213.4382
24 | 2718422.8717 | 1258153.8583
25 | 2718343.687 | 1258198.3575
26 | 2718507.7114 | 1258221.4136
27 | 2718363.8377 | 1258138.8522
28 | 2718513.3796 | 1258475.2992
29 | 2718286.0959 | 1258240.4107
30 | 2718305.6333 | 1258240.1322
31 | 2718278.1204 | 1258240.6138
32 | 2718343.3062 | 1258244.2318
33 | 2718261.6774 | 1258241.0325
34 | 2718364.686 | 1258246.5583
35 | 2718253.7233 | 1258241.2351
36 | 2718240.4042 | 1258241.5743
37 | 2718207.9397 | 1258180.7979
38 | 2718209.4057 | 1258157.0902
39 | 2718207.1369 | 1258193.7795
40 | 2718206.6856 | 1258143.9161
41 | 2718226.0734 | 1258194.158
42 | 2718206.8469 | 1258198.4777
43 | 2718175.9421 | 1258192.7884
44 | 2718209.1475 | 1258144.6071
45 | 2718188.553 | 1258137.7191
46 | 2718242.1659 | 1258194.5935
47 | 2718221.6522 | 1258215.7551
48 | 2718189.9795 | 1258198.1217
49 | 2718142.4901 | 1258191.7256
50 | 2718233.4597 | 1258151.4306
51 | 2718181.039 | 1258135.7423
52 | 2718230.0876 | 1258217.7189
53 | 2718279.5808 | 1258195.606
54 | 2718167.3166 | 1258197.6433
55 | 2718114.9562 | 1258190.8508
56 | 2718299.2837 | 1258196.3173
57 | 2718320.8612 | 1258197.0962
58 | 2718281.5843 | 1258190.4527
59 | 2718273.9216 | 1258162.9655
60 | 2718165.9569 | 1258131.7745
61 | 2718159.3326 | 1258130.0318
62 | 2718143.0592 | 1258125.7505
63 | 2718541.8195 | 1258482.5901
64 | 2718559.4029 | 1258491.3562
65 | 2718570.0574 | 1258496.668
66 | 2718568.6137 | 1258510.4818
67 | 2718238.717 | 1258254.296
68 | 2718184.4825 | 1258254.3996
69 | 2718150.4639 | 1258253.575
70 | 2718166.7439 | 1258217.2489
71 | 2718121.9592 | 1258196.3463
72 | 2718091.4875 | 1258195.5136
73 | 2718085.9001 | 1258195.361
74 | 2718084.554 | 1258189.8849
75 | 2718080.037 | 1258183.6969
76 | 2718060.2058 | 1258174.1247
77 | 2718137.2566 | 1258124.2239
78 | 2718119.0907 | 1258119.4448
79 | 2718113.5138 | 1258117.9776
80 | 2718092.3828 | 1258112.4184
81 | 2718078.6701 | 1258110.2652
82 | 2718017.9209 | 1258310.5007
83 | 2718022.0759 | 1258292.3265
84 | 2717998.0925 | 1258324.0325
85 | 2718028.5091 | 1258264.1871
86 | 2718001.631 | 1258271.413
87 | 2718031.6481 | 1258263.3378
88 | 2717967.6272 | 1258283.929
89 | 2717986.3572 | 1258263.6129
90 | 2718058.8814 | 1258259.3859
91 | 2718035.4673 | 1258247.1863
92 | 2718039.4174 | 1258229.0277
93 | 2718042.594 | 1258214.4248
94 | 2718050.8472 | 1258214.9956
95 | 2718069.9683 | 1258257.5304
96 | 2718088.4349 | 1258255.0137
97 | 2718064.2018 | 1258282.2033
98 | 2717996.8005 | 1258232.6633
99 | 2717990.8036 | 1258250.4357
100 | 2717929.1366 | 1258301.163
101 | 2717921.23 | 1258304.7497
102 | 2717964.9752 | 1258284.9051
103 | 2717918.1036 | 1258306.168
104 | 2717893.5346 | 1258317.3135
105 | 2717888.8431 | 1258319.4417
106 | 2718161.797 | 1258340.6571
107 | 2718165.321 | 1258326.2038
108 | 2718116.2938 | 1258252.7467
109 | 2718057.7027 | 1258106.9664
110 | 2718074.5511 | 1258131.0382
111 | 2718091.7275 | 1258254.5649
112 | 2717883.4378 | 1258321.8936
113 | 2717879.3142 | 1258323.7642
114 | 2718043.2623 | 1258167.4758
115 | 2718073.8993 | 1258134.3253
116 | 2718344.2432 | 1258133.4043
117 | 2718316.5921 | 1258125.5351
118 | 2718286.4457 | 1258116.9557
119 | 2718261.9219 | 1258109.9335
120 | 2718244.8928 | 1258104.9566
121 | 2718225.341 | 1258098.3395
122 | 2718210.2272 | 1258093.2245
123 | 2718191.3924 | 1258086.8501
124 | 2718166.0616 | 1258078.2773
125 | 2718145.8457 | 1258071.4355
126 | 2718037.6397 | 1258030.8482
127 | 2718046.3452 | 1258034.4299
128 | 2718015.0832 | 1258021.5675
129 | 2718067.8843 | 1258043.292
130 | 2718000.5387 | 1258016.5138
131 | 2718087.9692 | 1258051.5557
132 | 2717975.1122 | 1258008.0507
133 | 2718109.3913 | 1258059.0981
134 | 2717957.1344 | 1258002.0668
135 | 2717856.2852 | 1258334.2107
136 | 2717854.1629 | 1258335.1735
137 | 2717846.188 | 1258338.791
138 | 2717832.3395 | 1258345.0731
139 | 2717907.0076 | 1258111.4114
140 | 2717914.7529 | 1258115.0863
141 | 2717886.8466 | 1258101.8456
142 | 2717920.2666 | 1258117.7024
143 | 2717895.212 | 1258090.1454
144 | 2717928.2899 | 1258121.5092
145 | 2717942.9194 | 1258128.0995
146 | 2717988.459 | 1258145.97
147 | 2717993.4357 | 1258147.923
148 | 2717973.0553 | 1258139.9253
149 | 2718004.1958 | 1258152.1454
150 | 2717964.6145 | 1258136.613
151 | 2718016.6361 | 1258157.0272
152 | 2718036.642 | 1258164.8778
153 | 2718042.594 | 1258214.4248

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1