## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4946-22_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4946-22_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4946-22_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_4946-22_0_6_node_154 | 0.4 | n |  | TRUE
4 | bus_LV_4946-22_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4946-22_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_4946-22_0_6_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_4946-22_0_6_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_4946-22_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_4946-22_0_6_node_127 | 0.4 | n |  | TRUE
10 | bus_LV_4946-22_0_6_node_155 | 0.4 | n |  | TRUE
11 | bus_LV_4946-22_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_4946-22_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_4946-22_0_6_node_136 | 0.4 | n |  | TRUE
14 | bus_LV_4946-22_0_6_node_130 | 0.4 | n |  | TRUE
15 | bus_LV_4946-22_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_4946-22_0_6_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_4946-22_0_6_node_72 | 0.4 | n |  | TRUE
18 | bus_LV_4946-22_0_6_node_83 | 0.4 | n |  | TRUE
19 | bus_LV_4946-22_0_6_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_4946-22_0_6_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_4946-22_0_6_node_182 | 0.4 | n |  | TRUE
22 | bus_LV_4946-22_0_6_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_4946-22_0_6_node_49 | 0.4 | n |  | TRUE
24 | bus_LV_4946-22_0_6_node_43 | 0.4 | n |  | TRUE
25 | bus_LV_4946-22_0_6_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_4946-22_0_6_node_165 | 0.4 | n |  | TRUE
27 | bus_LV_4946-22_0_6_node_178 | 0.4 | n |  | TRUE
28 | bus_LV_4946-22_0_6_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_4946-22_0_6_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_4946-22_0_6_node_164 | 0.4 | n |  | TRUE
31 | bus_LV_4946-22_0_6_node_132 | 0.4 | n |  | TRUE
32 | bus_LV_4946-22_0_6_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_4946-22_0_6_node_52 | 0.4 | n |  | TRUE
34 | bus_LV_4946-22_0_6_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_4946-22_0_6_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_4946-22_0_6_node_51 | 0.4 | n |  | TRUE
37 | bus_LV_4946-22_0_6_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_4946-22_0_6_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_4946-22_0_6_node_46 | 0.4 | n |  | TRUE
40 | bus_LV_4946-22_0_6_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_4946-22_0_6_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_4946-22_0_6_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_4946-22_0_6_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_4946-22_0_6_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_4946-22_0_6_node_109 | 0.4 | n |  | TRUE
46 | bus_LV_4946-22_0_6_node_158 | 0.4 | n |  | TRUE
47 | bus_LV_4946-22_0_6_node_107 | 0.4 | n |  | TRUE
48 | bus_LV_4946-22_0_6_node_96 | 0.4 | n |  | TRUE
49 | bus_LV_4946-22_0_6_node_125 | 0.4 | n |  | TRUE
50 | bus_LV_4946-22_0_6_node_58 | 0.4 | n |  | TRUE
51 | bus_LV_4946-22_0_6_node_60 | 0.4 | n |  | TRUE
52 | bus_LV_4946-22_0_6_node_56 | 0.4 | n |  | TRUE
53 | bus_LV_4946-22_0_6_node_135 | 0.4 | n |  | TRUE
54 | bus_LV_4946-22_0_6_node_162 | 0.4 | n |  | TRUE
55 | bus_LV_4946-22_0_6_node_163 | 0.4 | n |  | TRUE
56 | bus_LV_4946-22_0_6_node_138 | 0.4 | n |  | TRUE
57 | bus_LV_4946-22_0_6_node_137 | 0.4 | n |  | TRUE
58 | bus_LV_4946-22_0_6_node_126 | 0.4 | n |  | TRUE
59 | bus_LV_4946-22_0_6_node_71 | 0.4 | n |  | TRUE
60 | bus_LV_4946-22_0_6_node_73 | 0.4 | n |  | TRUE
61 | bus_LV_4946-22_0_6_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_4946-22_0_6_node_166 | 0.4 | n |  | TRUE
63 | bus_LV_4946-22_0_6_node_133 | 0.4 | n |  | TRUE
64 | bus_LV_4946-22_0_6_node_181 | 0.4 | n |  | TRUE
65 | bus_LV_4946-22_0_6_node_180 | 0.4 | n |  | TRUE
66 | bus_LV_4946-22_0_6_node_17 | 0.4 | n |  | TRUE
67 | bus_LV_4946-22_0_6_node_19 | 0.4 | n |  | TRUE
68 | bus_LV_4946-22_0_6_node_18 | 0.4 | n |  | TRUE
69 | bus_LV_4946-22_0_6_node_20 | 0.4 | n |  | TRUE
70 | bus_LV_4946-22_0_6_node_21 | 0.4 | n |  | TRUE
71 | bus_LV_4946-22_0_6_node_23 | 0.4 | n |  | TRUE
72 | bus_LV_4946-22_0_6_node_65 | 0.4 | n |  | TRUE
73 | bus_LV_4946-22_0_6_node_84 | 0.4 | n |  | TRUE
74 | bus_LV_4946-22_0_6_node_22 | 0.4 | n |  | TRUE
75 | bus_LV_4946-22_0_6_node_88 | 0.4 | n |  | TRUE
76 | bus_LV_4946-22_0_6_node_87 | 0.4 | n |  | TRUE
77 | bus_LV_4946-22_0_6_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_4946-22_0_6_node_89 | 0.4 | n |  | TRUE
79 | bus_LV_4946-22_0_6_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_4946-22_0_6_node_86 | 0.4 | n |  | TRUE
81 | bus_LV_4946-22_0_6_node_100 | 0.4 | n |  | TRUE
82 | bus_LV_4946-22_0_6_node_34 | 0.4 | n |  | TRUE
83 | bus_LV_4946-22_0_6_node_24 | 0.4 | n |  | TRUE
84 | bus_LV_4946-22_0_6_node_28 | 0.4 | n |  | TRUE
85 | bus_LV_4946-22_0_6_node_32 | 0.4 | n |  | TRUE
86 | bus_LV_4946-22_0_6_node_33 | 0.4 | n |  | TRUE
87 | bus_LV_4946-22_0_6_node_31 | 0.4 | n |  | TRUE
88 | bus_LV_4946-22_0_6_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_4946-22_0_6_node_85 | 0.4 | n |  | TRUE
90 | bus_LV_4946-22_0_6_node_161 | 0.4 | n |  | TRUE
91 | bus_LV_4946-22_0_6_node_55 | 0.4 | n |  | TRUE
92 | bus_LV_4946-22_0_6_node_42 | 0.4 | n |  | TRUE
93 | bus_LV_4946-22_0_6_node_53 | 0.4 | n |  | TRUE
94 | bus_LV_4946-22_0_6_node_54 | 0.4 | n |  | TRUE
95 | bus_LV_4946-22_0_6_node_48 | 0.4 | n |  | TRUE
96 | bus_LV_4946-22_0_6_node_63 | 0.4 | n |  | TRUE
97 | bus_LV_4946-22_0_6_node_59 | 0.4 | n |  | TRUE
98 | bus_LV_4946-22_0_6_node_57 | 0.4 | n |  | TRUE
99 | bus_LV_4946-22_0_6_node_62 | 0.4 | n |  | TRUE
100 | bus_LV_4946-22_0_6_node_94 | 0.4 | n |  | TRUE
101 | bus_LV_4946-22_0_6_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_4946-22_0_6_node_177 | 0.4 | n |  | TRUE
103 | bus_LV_4946-22_0_6_node_147 | 0.4 | n |  | TRUE
104 | bus_LV_4946-22_0_6_node_176 | 0.4 | n |  | TRUE
105 | bus_LV_4946-22_0_6_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_4946-22_0_6_node_91 | 0.4 | n |  | TRUE
107 | bus_LV_4946-22_0_6_node_97 | 0.4 | n |  | TRUE
108 | bus_LV_4946-22_0_6_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_4946-22_0_6_node_67 | 0.4 | n |  | TRUE
110 | bus_LV_4946-22_0_6_node_70 | 0.4 | n |  | TRUE
111 | bus_LV_4946-22_0_6_node_66 | 0.4 | n |  | TRUE
112 | bus_LV_4946-22_0_6_node_68 | 0.4 | n |  | TRUE
113 | bus_LV_4946-22_0_6_node_80 | 0.4 | n |  | TRUE
114 | bus_LV_4946-22_0_6_node_78 | 0.4 | n |  | TRUE
115 | bus_LV_4946-22_0_6_node_75 | 0.4 | n |  | TRUE
116 | bus_LV_4946-22_0_6_node_76 | 0.4 | n |  | TRUE
117 | bus_LV_4946-22_0_6_node_108 | 0.4 | n |  | TRUE
118 | bus_LV_4946-22_0_6_node_77 | 0.4 | n |  | TRUE
119 | bus_LV_4946-22_0_6_node_81 | 0.4 | n |  | TRUE
120 | bus_LV_4946-22_0_6_node_98 | 0.4 | n |  | TRUE
121 | bus_LV_4946-22_0_6_node_101 | 0.4 | n |  | TRUE
122 | bus_LV_4946-22_0_6_node_99 | 0.4 | n |  | TRUE
123 | bus_LV_4946-22_0_6_node_103 | 0.4 | n |  | TRUE
124 | bus_LV_4946-22_0_6_node_92 | 0.4 | n |  | TRUE
125 | bus_LV_4946-22_0_6_node_95 | 0.4 | n |  | TRUE
126 | bus_LV_4946-22_0_6_node_145 | 0.4 | n |  | TRUE
127 | bus_LV_4946-22_0_6_node_110 | 0.4 | n |  | TRUE
128 | bus_LV_4946-22_0_6_node_102 | 0.4 | n |  | TRUE
129 | bus_LV_4946-22_0_6_node_105 | 0.4 | n |  | TRUE
130 | bus_LV_4946-22_0_6_node_106 | 0.4 | n |  | TRUE
131 | bus_LV_4946-22_0_6_node_122 | 0.4 | n |  | TRUE
132 | bus_LV_4946-22_0_6_node_146 | 0.4 | n |  | TRUE
133 | bus_LV_4946-22_0_6_node_123 | 0.4 | n |  | TRUE
134 | bus_LV_4946-22_0_6_node_111 | 0.4 | n |  | TRUE
135 | bus_LV_4946-22_0_6_node_156 | 0.4 | n |  | TRUE
136 | bus_LV_4946-22_0_6_node_112 | 0.4 | n |  | TRUE
137 | bus_LV_4946-22_0_6_node_113 | 0.4 | n |  | TRUE
138 | bus_LV_4946-22_0_6_node_118 | 0.4 | n |  | TRUE
139 | bus_LV_4946-22_0_6_node_134 | 0.4 | n |  | TRUE
140 | bus_LV_4946-22_0_6_node_148 | 0.4 | n |  | TRUE
141 | bus_LV_4946-22_0_6_node_116 | 0.4 | n |  | TRUE
142 | bus_LV_4946-22_0_6_node_149 | 0.4 | n |  | TRUE
143 | bus_LV_4946-22_0_6_node_114 | 0.4 | n |  | TRUE
144 | bus_LV_4946-22_0_6_node_115 | 0.4 | n |  | TRUE
145 | bus_LV_4946-22_0_6_node_117 | 0.4 | n |  | TRUE
146 | bus_LV_4946-22_0_6_node_119 | 0.4 | n |  | TRUE
147 | bus_LV_4946-22_0_6_node_120 | 0.4 | n |  | TRUE
148 | bus_LV_4946-22_0_6_node_121 | 0.4 | n |  | TRUE
149 | bus_LV_4946-22_0_6_node_141 | 0.4 | n |  | TRUE
150 | bus_LV_4946-22_0_6_node_152 | 0.4 | n |  | TRUE
151 | bus_LV_4946-22_0_6_node_140 | 0.4 | n |  | TRUE
152 | bus_LV_4946-22_0_6_node_153 | 0.4 | n |  | TRUE
153 | bus_LV_4946-22_0_6_node_151 | 0.4 | n |  | TRUE
154 | bus_LV_4946-22_0_6_node_150 | 0.4 | n |  | TRUE
155 | bus_LV_4946-22_0_6_node_124 | 0.4 | n |  | TRUE
156 | bus_LV_4946-22_0_6_node_128 | 0.4 | n |  | TRUE
157 | bus_LV_4946-22_0_6_node_129 | 0.4 | n |  | TRUE
158 | bus_LV_4946-22_0_6_node_131 | 0.4 | n |  | TRUE
159 | bus_LV_4946-22_0_6_node_179 | 0.4 | n |  | TRUE
160 | bus_LV_4946-22_0_6_node_139 | 0.4 | n |  | TRUE
161 | bus_LV_4946-22_0_6_node_142 | 0.4 | n |  | TRUE
162 | bus_LV_4946-22_0_6_node_143 | 0.4 | n |  | TRUE
163 | bus_LV_4946-22_0_6_node_144 | 0.4 | n |  | TRUE
164 | bus_LV_4946-22_0_6_node_171 | 0.4 | n |  | TRUE
165 | bus_LV_4946-22_0_6_node_172 | 0.4 | n |  | TRUE
166 | bus_LV_4946-22_0_6_node_157 | 0.4 | n |  | TRUE
167 | bus_LV_4946-22_0_6_node_159 | 0.4 | n |  | TRUE
168 | bus_LV_4946-22_0_6_node_160 | 0.4 | n |  | TRUE
169 | bus_LV_4946-22_0_6_node_167 | 0.4 | n |  | TRUE
170 | bus_LV_4946-22_0_6_node_168 | 0.4 | n |  | TRUE
171 | bus_LV_4946-22_0_6_node_169 | 0.4 | n |  | TRUE
172 | bus_LV_4946-22_0_6_node_170 | 0.4 | n |  | TRUE
173 | bus_LV_4946-22_0_6_node_173 | 0.4 | n |  | TRUE
174 | bus_LV_4946-22_0_6_node_174 | 0.4 | n |  | TRUE
175 | bus_LV_4946-22_0_6_node_175 | 0.4 | n |  | TRUE
176 | bus_MV_488_1_node_166 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4946-22_0_6_load_0 | 0 | 0.01603 | 0.0040175 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4946-22_0_6_load_154 | 3 | 0.0022997 | 0.00057636 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4946-22_0_6_load_45 | 6 | 0.0095531 | 0.0023942 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4946-22_0_6_load_44 | 7 | 0.0053314 | 0.0013362 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4946-22_0_6_load_127 | 9 | 0.00099134 | 0.00024845 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4946-22_0_6_load_136 | 13 | 0.0032408 | 0.00081222 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4946-22_0_6_load_72 | 17 | 0.0031347 | 0.00078562 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4946-22_0_6_load_83 | 18 | 0.010408 | 0.0026086 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4946-22_0_6_load_74 | 19 | 0.0067836 | 0.0017001 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4946-22_0_6_load_182 | 21 | 0.0081869 | 0.0020518 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4946-22_0_6_load_43 | 24 | 0.0085216 | 0.0021357 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4946-22_0_6_load_178 | 27 | 0.00026628 | 6.6735e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4946-22_0_6_load_164 | 30 | 0.00062506 | 0.00015665 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4946-22_0_6_load_132 | 31 | 0.018214 | 0.0045649 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4946-22_0_6_load_52 | 33 | 0.014811 | 0.003712 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4946-22_0_6_load_50 | 34 | 0.018155 | 0.00455 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4946-22_0_6_load_51 | 36 | 0.013901 | 0.0034838 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4946-22_0_6_load_46 | 39 | 0.010745 | 0.0026929 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4946-22_0_6_load_35 | 41 | 0.0011136 | 0.00027911 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4946-22_0_6_load_40 | 44 | 0.0027894 | 0.00069908 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4946-22_0_6_load_158 | 46 | 0.0017075 | 0.00042793 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4946-22_0_6_load_107 | 47 | 0.0060151 | 0.0015075 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4946-22_0_6_load_60 | 51 | 0.0040704 | 0.0010201 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4946-22_0_6_load_56 | 52 | 0.0052377 | 0.0013127 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4946-22_0_6_load_135 | 53 | 0.0088378 | 0.002215 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4946-22_0_6_load_162 | 54 | 0.0046052 | 0.0011542 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4946-22_0_6_load_163 | 55 | 0.00053964 | 0.00013525 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4946-22_0_6_load_137 | 57 | 0.03973 | 0.0099573 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4946-22_0_6_load_71 | 59 | 0.013548 | 0.0033955 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4946-22_0_6_load_73 | 60 | 0.0020044 | 0.00050236 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4946-22_0_6_load_166 | 62 | 0.00070539 | 0.00017679 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4946-22_0_6_load_181 | 64 | 0.0096275 | 0.0024129 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4946-22_0_6_load_180 | 65 | 0.0098732 | 0.0024745 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4946-22_0_6_load_17 | 66 | 0.0099642 | 0.0024973 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4946-22_0_6_load_18 | 68 | 0.007766 | 0.0019464 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4946-22_0_6_load_21 | 70 | 0.0063837 | 0.0015999 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4946-22_0_6_load_65 | 72 | 0.0057071 | 0.0014303 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4946-22_0_6_load_87 | 76 | 0.0069619 | 0.0017448 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4946-22_0_6_load_69 | 79 | 0.0057077 | 0.0014305 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4946-22_0_6_load_100 | 81 | 0.0095543 | 0.0023945 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4946-22_0_6_load_24 | 83 | 0.0059877 | 0.0015007 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4946-22_0_6_load_28 | 84 | 0.0041033 | 0.0010284 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4946-22_0_6_load_33 | 86 | 0.0055842 | 0.0013995 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4946-22_0_6_load_31 | 87 | 0.0058772 | 0.001473 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4946-22_0_6_load_82 | 88 | 0.011696 | 0.0029314 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4946-22_0_6_load_161 | 90 | 0.0061585 | 0.0015435 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4946-22_0_6_load_42 | 92 | 0.00076725 | 0.00019229 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4946-22_0_6_load_53 | 93 | 0.025201 | 0.0063161 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4946-22_0_6_load_54 | 94 | 0.0033405 | 0.00083722 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4946-22_0_6_load_48 | 95 | 0.011307 | 0.0028338 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4946-22_0_6_load_57 | 98 | 0.0057207 | 0.0014337 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4946-22_0_6_load_62 | 99 | 0.0013935 | 0.00034925 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4946-22_0_6_load_94 | 100 | 0.0030408 | 0.0007621 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4946-22_0_6_load_147 | 103 | 0.001674 | 0.00041955 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4946-22_0_6_load_176 | 104 | 0.0016371 | 0.0004103 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4946-22_0_6_load_90 | 105 | 0.0063801 | 0.001599 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4946-22_0_6_load_91 | 106 | 0.0078316 | 0.0019628 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4946-22_0_6_load_97 | 107 | 0.0028244 | 0.00070786 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4946-22_0_6_load_104 | 108 | 0.0025985 | 0.00065124 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4946-22_0_6_load_67 | 109 | 0.0046009 | 0.0011531 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4946-22_0_6_load_66 | 111 | 0.0027271 | 0.00068347 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4946-22_0_6_load_68 | 112 | 0.004604 | 0.0011539 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4946-22_0_6_load_78 | 114 | 0.0036625 | 0.00091792 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4946-22_0_6_load_75 | 115 | 0.0097341 | 0.0024396 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4946-22_0_6_load_108 | 117 | 0.0059161 | 0.0014827 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4946-22_0_6_load_77 | 118 | 0.0072153 | 0.0018083 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4946-22_0_6_load_98 | 120 | 0.0026079 | 0.0006536 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4946-22_0_6_load_101 | 121 | 0.00099938 | 0.00025047 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4946-22_0_6_load_99 | 122 | 0.003983 | 0.00099824 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4946-22_0_6_load_103 | 123 | 0.001847 | 0.0004629 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4946-22_0_6_load_92 | 124 | 0.0013999 | 0.00035084 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4946-22_0_6_load_95 | 125 | 0.0015043 | 0.00037702 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4946-22_0_6_load_110 | 127 | 0.0035539 | 0.00089069 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4946-22_0_6_load_105 | 129 | 0.0020285 | 0.00050838 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4946-22_0_6_load_106 | 130 | 0.0030591 | 0.00076667 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4946-22_0_6_load_122 | 131 | 0.0019174 | 0.00048054 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4946-22_0_6_load_146 | 132 | 0.0017912 | 0.00044892 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4946-22_0_6_load_123 | 133 | 0.0020651 | 0.00051757 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4946-22_0_6_load_111 | 134 | 0.0039409 | 0.00098769 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4946-22_0_6_load_156 | 135 | 0.0011149 | 0.00027943 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4946-22_0_6_load_113 | 137 | 0.0026595 | 0.00066652 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4946-22_0_6_load_118 | 138 | 0.0028791 | 0.00072157 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4946-22_0_6_load_134 | 139 | 0.0032397 | 0.00081195 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4946-22_0_6_load_148 | 140 | 0.0020365 | 0.00051039 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4946-22_0_6_load_116 | 141 | 0.0046052 | 0.0011542 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4946-22_0_6_load_149 | 142 | 0.0035041 | 0.00087821 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4946-22_0_6_load_114 | 143 | 0.00048781 | 0.00012226 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4946-22_0_6_load_115 | 144 | 0.0063466 | 0.0015906 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4946-22_0_6_load_117 | 145 | 0.0023911 | 0.00059926 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4946-22_0_6_load_120 | 147 | 0.00065819 | 0.00016496 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4946-22_0_6_load_121 | 148 | 0.0014178 | 0.00035534 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4946-22_0_6_load_141 | 149 | 0.0012212 | 0.00030605 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4946-22_0_6_load_152 | 150 | 0.00065776 | 0.00016485 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4946-22_0_6_load_140 | 151 | 0.0023021 | 0.00057696 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4946-22_0_6_load_153 | 152 | 0.0011926 | 0.0002989 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4946-22_0_6_load_151 | 153 | 0.0032349 | 0.00081073 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4946-22_0_6_load_150 | 154 | 0.0020882 | 0.00052336 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4946-22_0_6_load_124 | 155 | 0.010642 | 0.0026672 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4946-22_0_6_load_128 | 156 | 0.0057737 | 0.001447 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4946-22_0_6_load_129 | 157 | 0.01064 | 0.0026666 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4946-22_0_6_load_131 | 158 | 0.01064 | 0.0026666 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4946-22_0_6_load_179 | 159 | 0.0040097 | 0.0010049 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4946-22_0_6_load_139 | 160 | 0.013042 | 0.0032686 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4946-22_0_6_load_142 | 161 | 0.0010457 | 0.00026207 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4946-22_0_6_load_143 | 162 | 0.0012409 | 0.000311 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4946-22_0_6_load_144 | 163 | 0.0014737 | 0.00036935 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4946-22_0_6_load_171 | 164 | 0.00057425 | 0.00014392 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4946-22_0_6_load_157 | 166 | 0.0013491 | 0.00033811 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4946-22_0_6_load_159 | 167 | 0.0014349 | 0.00035961 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4946-22_0_6_load_160 | 168 | 0.0014599 | 0.0003659 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4946-22_0_6_load_167 | 169 | 0.0004529 | 0.00011351 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4946-22_0_6_load_168 | 170 | 0.0005167 | 0.0001295 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4946-22_0_6_load_169 | 171 | 0.00049913 | 0.00012509 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4946-22_0_6_load_170 | 172 | 0.00054042 | 0.00013544 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4946-22_0_6_load_173 | 173 | 0.0019069 | 0.00047792 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4946-22_0_6_load_174 | 174 | 0.0022763 | 0.0005705 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4946-22_0_6_load_175 | 175 | 0.0022771 | 0.00057069 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4946-22_0_6_line_0 |  | 0 | 1 | 0.091961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4946-22_0_6_line_1 |  | 1 | 2 | 0.015159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4946-22_0_6_line_2 |  | 2 | 3 | 0.068764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4946-22_0_6_line_3 |  | 3 | 10 | 0.089984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4946-22_0_6_line_4 |  | 4 | 5 | 0.038985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_4946-22_0_6_line_5 |  | 4 | 6 | 0.013876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_4946-22_0_6_line_6 |  | 5 | 7 | 0.016824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_4946-22_0_6_line_7 |  | 6 | 38 | 0.015238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_4946-22_0_6_line_8 |  | 7 | 22 | 0.027144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_4946-22_0_6_line_9 |  | 8 | 9 | 0.13918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4946-22_0_6_line_10 |  | 8 | 10 | 0.008573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4946-22_0_6_line_11 |  | 9 | 49 | 0.0016441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4946-22_0_6_line_12 |  | 10 | 45 | 0.058734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4946-22_0_6_line_13 |  | 11 | 12 | 0.040874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_4946-22_0_6_line_14 |  | 11 | 13 | 0.011001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_4946-22_0_6_line_15 |  | 12 | 14 | 0.035006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_4946-22_0_6_line_16 |  | 13 | 53 | 0.0067315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_4946-22_0_6_line_17 |  | 14 | 56 | 0.015565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4946-22_0_6_line_18 |  | 14 | 57 | 0.016804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_4946-22_0_6_line_19 |  | 14 | 58 | 0.049194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_4946-22_0_6_line_20 |  | 15 | 16 | 0.06499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_4946-22_0_6_line_21 |  | 15 | 17 | 0.013255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_4946-22_0_6_line_22 |  | 16 | 18 | 0.010648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4946-22_0_6_line_23 |  | 16 | 19 | 0.0065322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_4946-22_0_6_line_24 |  | 17 | 59 | 0.025883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_4946-22_0_6_line_25 |  | 19 | 60 | 0.013489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_4946-22_0_6_line_26 |  | 20 | 21 | 0.006624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4946-22_0_6_line_27 |  | 20 | 22 | 0.019769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_4946-22_0_6_line_28 |  | 20 | 23 | 0.011658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_4946-22_0_6_line_29 |  | 22 | 24 | 0.011776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4946-22_0_6_line_30 |  | 23 | 59 | 0.052267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_4946-22_0_6_line_31 |  | 23 | 61 | 0.013885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_4946-22_0_6_line_32 |  | 25 | 26 | 0.032218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4946-22_0_6_line_33 |  | 25 | 27 | 0.037148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4946-22_0_6_line_34 |  | 26 | 62 | 0.0087386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_4946-22_0_6_line_35 |  | 26 | 28 | 0.013259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_4946-22_0_6_line_36 |  | 28 | 29 | 0.010411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_4946-22_0_6_line_37 |  | 28 | 30 | 0.030134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4946-22_0_6_line_38 |  | 29 | 31 | 0.044871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_4946-22_0_6_line_39 |  | 30 | 55 | 0.020894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4946-22_0_6_line_40 |  | 32 | 33 | 0.015751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4946-22_0_6_line_41 |  | 32 | 34 | 0.027333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4946-22_0_6_line_42 |  | 33 | 71 | 0.0078434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4946-22_0_6_line_43 |  | 34 | 36 | 0.0019769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4946-22_0_6_line_44 |  | 35 | 36 | 0.027894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4946-22_0_6_line_45 |  | 35 | 37 | 0.017295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4946-22_0_6_line_46 |  | 37 | 83 | 0.032843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4946-22_0_6_line_47 |  | 38 | 39 | 0.0047224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4946-22_0_6_line_48 |  | 40 | 41 | 0.012524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4946-22_0_6_line_49 |  | 40 | 42 | 0.020447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4946-22_0_6_line_50 |  | 41 | 43 | 0.016736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4946-22_0_6_line_51 |  | 42 | 84 | 0.011744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4946-22_0_6_line_52 |  | 42 | 83 | 0.027736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4946-22_0_6_line_53 |  | 43 | 44 | 0.020136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4946-22_0_6_line_54 |  | 45 | 46 | 0.11302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4946-22_0_6_line_55 |  | 46 | 135 | 0.015854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4946-22_0_6_line_56 |  | 47 | 48 | 0.01261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4946-22_0_6_line_57 |  | 48 | 117 | 0.032264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_4946-22_0_6_line_58 |  | 48 | 116 | 0.014569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_4946-22_0_6_line_59 |  | 49 | 156 | 0.041615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4946-22_0_6_line_60 |  | 49 | 155 | 0.033547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_4946-22_0_6_line_61 |  | 50 | 51 | 0.014424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4946-22_0_6_line_62 |  | 50 | 52 | 0.018276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4946-22_0_6_line_63 |  | 51 | 100 | 0.0055014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4946-22_0_6_line_64 |  | 53 | 139 | 0.00097247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_4946-22_0_6_line_65 |  | 54 | 55 | 0.019818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4946-22_0_6_line_66 |  | 56 | 160 | 0.011525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4946-22_0_6_line_67 |  | 58 | 157 | 0.019917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_4946-22_0_6_line_68 |  | 58 | 158 | 0.015125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_4946-22_0_6_line_69 |  | 58 | 155 | 0.028933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_4946-22_0_6_line_70 |  | 60 | 115 | 0.031357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_4946-22_0_6_line_71 |  | 61 | 95 | 0.006293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_4946-22_0_6_line_72 |  | 62 | 169 | 0.010189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_4946-22_0_6_line_73 |  | 63 | 64 | 0.018266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4946-22_0_6_line_74 |  | 63 | 65 | 0.0030949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4946-22_0_6_line_75 |  | 65 | 159 | 0.032882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4946-22_0_6_line_76 |  | 66 | 67 | 0.021659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4946-22_0_6_line_77 |  | 67 | 70 | 0.016432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_4946-22_0_6_line_78 |  | 67 | 71 | 0.026632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_4946-22_0_6_line_79 |  | 68 | 69 | 0.0028985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4946-22_0_6_line_80 |  | 69 | 72 | 0.018558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4946-22_0_6_line_81 |  | 70 | 73 | 0.021939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_4946-22_0_6_line_82 |  | 71 | 75 | 0.027677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4946-22_0_6_line_83 |  | 72 | 80 | 0.021893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4946-22_0_6_line_84 |  | 73 | 80 | 0.004408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_4946-22_0_6_line_85 |  | 74 | 75 | 0.00904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4946-22_0_6_line_86 |  | 74 | 76 | 0.014836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4946-22_0_6_line_87 |  | 75 | 81 | 0.0026653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4946-22_0_6_line_88 |  | 76 | 82 | 0.018354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4946-22_0_6_line_89 |  | 77 | 78 | 0.026769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_4946-22_0_6_line_90 |  | 77 | 79 | 0.017498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_4946-22_0_6_line_91 |  | 78 | 107 | 0.010671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_4946-22_0_6_line_92 |  | 78 | 108 | 0.0064225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4946-22_0_6_line_93 |  | 79 | 109 | 0.014482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_4946-22_0_6_line_94 |  | 80 | 110 | 0.010148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_4946-22_0_6_line_95 |  | 82 | 88 | 0.011299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4946-22_0_6_line_96 |  | 84 | 85 | 0.031893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4946-22_0_6_line_97 |  | 85 | 86 | 0.049097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4946-22_0_6_line_98 |  | 85 | 87 | 0.028951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4946-22_0_6_line_99 |  | 86 | 89 | 0.027311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4946-22_0_6_line_100 |  | 89 | 90 | 0.017671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4946-22_0_6_line_101 |  | 89 | 91 | 0.014065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4946-22_0_6_line_102 |  | 90 | 96 | 0.0056786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4946-22_0_6_line_103 |  | 91 | 94 | 0.0094202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4946-22_0_6_line_104 |  | 92 | 93 | 0.0054441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4946-22_0_6_line_105 |  | 93 | 94 | 0.016386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4946-22_0_6_line_106 |  | 96 | 97 | 0.050729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4946-22_0_6_line_107 |  | 97 | 99 | 0.019634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4946-22_0_6_line_108 |  | 97 | 98 | 0.024822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4946-22_0_6_line_109 |  | 100 | 101 | 0.012524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4946-22_0_6_line_110 |  | 101 | 125 | 0.018233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4946-22_0_6_line_111 |  | 101 | 124 | 0.046069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4946-22_0_6_line_112 |  | 102 | 103 | 0.011153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4946-22_0_6_line_113 |  | 102 | 104 | 0.039138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4946-22_0_6_line_114 |  | 103 | 126 | 0.034429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4946-22_0_6_line_115 |  | 104 | 175 | 0.010807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4946-22_0_6_line_116 |  | 105 | 106 | 0.011685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4946-22_0_6_line_117 |  | 106 | 119 | 0.02493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_4946-22_0_6_line_118 |  | 107 | 116 | 0.0051147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_4946-22_0_6_line_119 |  | 108 | 123 | 0.024454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4946-22_0_6_line_120 |  | 109 | 111 | 0.012483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_4946-22_0_6_line_121 |  | 110 | 113 | 0.024155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4946-22_0_6_line_122 |  | 110 | 112 | 0.00058692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_4946-22_0_6_line_123 |  | 111 | 112 | 0.015841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_4946-22_0_6_line_124 |  | 113 | 114 | 0.01874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4946-22_0_6_line_125 |  | 114 | 118 | 0.00037621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4946-22_0_6_line_126 |  | 115 | 116 | 0.030214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_4946-22_0_6_line_127 |  | 117 | 127 | 0.0086934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
128 | LV_4946-22_0_6_line_128 |  | 119 | 120 | 0.016124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
129 | LV_4946-22_0_6_line_129 |  | 120 | 121 | 0.021038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_4946-22_0_6_line_130 |  | 121 | 128 | 0.014838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
131 | LV_4946-22_0_6_line_131 |  | 122 | 123 | 0.023932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4946-22_0_6_line_132 |  | 125 | 126 | 0.014082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4946-22_0_6_line_133 |  | 127 | 134 | 0.014202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
134 | LV_4946-22_0_6_line_134 |  | 128 | 129 | 0.028566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
135 | LV_4946-22_0_6_line_135 |  | 128 | 130 | 0.00052485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4946-22_0_6_line_136 |  | 129 | 131 | 0.010198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_4946-22_0_6_line_137 |  | 130 | 132 | 0.019656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4946-22_0_6_line_138 |  | 131 | 133 | 0.011769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
139 | LV_4946-22_0_6_line_139 |  | 133 | 153 | 0.0039964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
140 | LV_4946-22_0_6_line_140 |  | 134 | 136 | 0.030653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
141 | LV_4946-22_0_6_line_141 |  | 134 | 137 | 0.016899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
142 | LV_4946-22_0_6_line_142 |  | 135 | 166 | 0.020216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4946-22_0_6_line_143 |  | 136 | 138 | 0.0059821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
144 | LV_4946-22_0_6_line_144 |  | 136 | 139 | 0.015162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
145 | LV_4946-22_0_6_line_145 |  | 137 | 140 | 0.015114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
146 | LV_4946-22_0_6_line_146 |  | 138 | 141 | 0.027502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
147 | LV_4946-22_0_6_line_147 |  | 140 | 142 | 0.0091444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
148 | LV_4946-22_0_6_line_148 |  | 141 | 143 | 0.01248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
149 | LV_4946-22_0_6_line_149 |  | 142 | 154 | 0.0027895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
150 | LV_4946-22_0_6_line_150 |  | 143 | 144 | 0.009316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
151 | LV_4946-22_0_6_line_151 |  | 144 | 145 | 0.023212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
152 | LV_4946-22_0_6_line_152 |  | 145 | 146 | 0.0039441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
153 | LV_4946-22_0_6_line_153 |  | 146 | 147 | 0.018118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4946-22_0_6_line_154 |  | 146 | 148 | 0.011145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
155 | LV_4946-22_0_6_line_155 |  | 147 | 149 | 0.0037847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4946-22_0_6_line_156 |  | 148 | 150 | 0.0043929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
157 | LV_4946-22_0_6_line_157 |  | 149 | 151 | 0.023583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4946-22_0_6_line_158 |  | 150 | 152 | 0.026406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
159 | LV_4946-22_0_6_line_159 |  | 151 | 161 | 0.00014597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4946-22_0_6_line_160 |  | 152 | 164 | 0.0017956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
161 | LV_4946-22_0_6_line_161 |  | 153 | 154 | 0.020475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
162 | LV_4946-22_0_6_line_162 |  | 156 | 159 | 0.00168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4946-22_0_6_line_163 |  | 161 | 162 | 0.028724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4946-22_0_6_line_164 |  | 162 | 163 | 0.0029209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4946-22_0_6_line_165 |  | 164 | 165 | 0.015436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
166 | LV_4946-22_0_6_line_166 |  | 165 | 173 | 0.025796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
167 | LV_4946-22_0_6_line_167 |  | 165 | 172 | 0.002954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
168 | LV_4946-22_0_6_line_168 |  | 166 | 167 | 0.042245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4946-22_0_6_line_169 |  | 167 | 168 | 0.00031675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4946-22_0_6_line_170 |  | 169 | 170 | 0.019594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
171 | LV_4946-22_0_6_line_171 |  | 170 | 171 | 0.0057946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
172 | LV_4946-22_0_6_line_172 |  | 171 | 172 | 0.024126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
173 | LV_4946-22_0_6_line_173 |  | 173 | 174 | 0.011713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
174 | LV_4946-22_0_6_line_174 |  | 174 | 175 | 0.033004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4946-22_0_6_trafo_64 | 0.63 MVA 20/0.4 kV | 176 | 77 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2725345.8566 | 1269217.1338 | 2725372.9789 | 1269201.5393 | 2725374.433 | 1269201.8371 | 2725378.7217 | 1269204.0635 | 2725380.2974 | 1269203.5965 | 2725397.1143 | 1269193.6775 | 2725426.6344 | 1269178.5047
1 | 2725336.6525 | 1269210.2878 | 2725341.9526 | 1269219.4754 | 2725345.8566 | 1269217.1338
2 | 2725336.6525 | 1269210.2878 | 2725302.3008 | 1269150.7187
3 | 2725255.7883 | 1269073.7686 | 2725262.8581 | 1269083.294 | 2725269.7176 | 1269094.2162 | 2725302.3008 | 1269150.7187
4 | 2725591.9525 | 1269112.7854 | 2725601.8435 | 1269106.4453 | 2725624.7702 | 1269091.7413
5 | 2725624.7702 | 1269091.7413 | 2725625.32 | 1269077.8763
6 | 2725591.9525 | 1269112.7854 | 2725586.3068 | 1269096.9366
7 | 2725625.9238 | 1269062.65 | 2725625.32 | 1269077.8763
8 | 2725577.1982 | 1269071.3667 | 2725586.3068 | 1269096.9366
9 | 2725262.2175 | 1269068.0774 | 2725264.0333 | 1269063.3894 | 2725318.2423 | 1268940.6751
10 | 2725262.2175 | 1269068.0774 | 2725255.7883 | 1269073.7686
11 | 2725318.9066 | 1268939.1713 | 2725318.2423 | 1268940.6751
12 | 2725205.7607 | 1269047.7286 | 2725217.8797 | 1269047.7744 | 2725226.7162 | 1269050.3196 | 2725235.6753 | 1269055.6032 | 2725241.7625 | 1269060.7037 | 2725251.258 | 1269068.7346 | 2725255.7883 | 1269073.7686
13 | 2725457.0078 | 1268849.2632 | 2725449.6349 | 1268851.8757 | 2725458.1445 | 1268875.8341 | 2725451.4351 | 1268879.4617
14 | 2725457.0078 | 1268849.2632 | 2725467.3783 | 1268845.5929
15 | 2725451.4351 | 1268879.4617 | 2725420.5763 | 1268896.1554
16 | 2725467.3783 | 1268845.5929 | 2725473.724 | 1268843.3471
17 | 2725412.8995 | 1268882.6021 | 2725420.5763 | 1268896.1554
18 | 2725420.5763 | 1268896.1554 | 2725428.8552 | 1268910.778
19 | 2725420.5763 | 1268896.1554 | 2725394.8277 | 1268910.0884 | 2725377.7574 | 1268920.5581
20 | 2725511.4656 | 1268970.4097 | 2725499.27 | 1268975.0216 | 2725512.8527 | 1269013.1566 | 2725517.1464 | 1269017.6297 | 2725518.043 | 1269020.0733 | 2725520.5892 | 1269019.2822
21 | 2725520.5892 | 1269019.2822 | 2725531.7874 | 1269012.1894
22 | 2725511.4656 | 1268970.4097 | 2725519.6989 | 1268963.6576
23 | 2725511.4656 | 1268970.4097 | 2725517.6104 | 1268968.1938
24 | 2725554.5507 | 1269003.203 | 2725554.2017 | 1269002.6476 | 2725547.0909 | 1269002.4964 | 2725531.7874 | 1269012.1894
25 | 2725529.0471 | 1268961.0412 | 2725517.6104 | 1268968.1938
26 | 2725571.7214 | 1269053.1556 | 2725568.2812 | 1269047.4884
27 | 2725571.7214 | 1269053.1556 | 2725570.8901 | 1269053.6607 | 2725577.1982 | 1269071.3667
28 | 2725571.7214 | 1269053.1556 | 2725581.6682 | 1269047.028
29 | 2725577.1982 | 1269071.3667 | 2725566.0637 | 1269075.1999
30 | 2725581.6682 | 1269047.028 | 2725571.4156 | 1269030.7283 | 2725571.3402 | 1269027.546 | 2725560.3714 | 1269010.2302 | 2725558.1119 | 1269008.8698 | 2725554.5507 | 1269003.203
31 | 2725581.6682 | 1269047.028 | 2725593.5144 | 1269039.7286
32 | 2725421.1943 | 1268715.7681 | 2725429.4003 | 1268736.3169 | 2725430.4381 | 1268740.2648 | 2725430.5551 | 1268743.9707 | 2725429.5473 | 1268746.0512
33 | 2725421.1943 | 1268715.7681 | 2725420.272 | 1268713.4686 | 2725418.2601 | 1268707.5316 | 2725418.0441 | 1268703.1674 | 2725419.9975 | 1268698.7492 | 2725425.2813 | 1268693.1339 | 2725432.3309 | 1268689.8027 | 2725435.9296 | 1268688.9701
34 | 2725429.5473 | 1268746.0512 | 2725438.0507 | 1268744.0377
35 | 2725429.5473 | 1268746.0512 | 2725428.4842 | 1268748.2529 | 2725423.9482 | 1268751.2706 | 2725418.9444 | 1268753.2773
36 | 2725409.3288 | 1268757.2658 | 2725414.5711 | 1268755.0194 | 2725418.9444 | 1268753.2773
37 | 2725418.9444 | 1268753.2773 | 2725429.3118 | 1268781.5722
38 | 2725409.3288 | 1268757.2658 | 2725418.5359 | 1268782.0731 | 2725424.8301 | 1268799.3738
39 | 2725438.7973 | 1268799.3427 | 2725437.1532 | 1268794.8357 | 2725433.2611 | 1268792.3507 | 2725429.3118 | 1268781.5722
40 | 2725635.9905 | 1269016.9327 | 2725636.3257 | 1269001.1854
41 | 2725635.9905 | 1269016.9327 | 2725651.4397 | 1269017.206 | 2725654.5997 | 1269019.7644 | 2725662.4147 | 1269019.8455
42 | 2725636.4926 | 1268993.3438 | 2725636.3257 | 1269001.1854
43 | 2725662.4147 | 1269019.8455 | 2725664.3915 | 1269019.866
44 | 2725692.284 | 1269020.1552 | 2725664.3915 | 1269019.866
45 | 2725689.2892 | 1269003.1202 | 2725692.284 | 1269020.1552
46 | 2725689.2892 | 1269003.1202 | 2725722.0375 | 1269000.6268
47 | 2725625.9238 | 1269062.65 | 2725626.1092 | 1269057.9312
48 | 2725743.6694 | 1269024.0745 | 2725755.8359 | 1269021.1023
49 | 2725743.6694 | 1269024.0745 | 2725748.3917 | 1269004.1787
50 | 2725771.5056 | 1269015.3477 | 2725760.5446 | 1269019.952 | 2725755.8359 | 1269021.1023
51 | 2725748.3917 | 1269004.1787 | 2725751.1027 | 1268992.7523
52 | 2725748.3917 | 1269004.1787 | 2725742.6585 | 1269003.3226 | 2725741.1075 | 1269001.9216 | 2725736.2534 | 1269002.2075 | 2725734.6381 | 1269000.9942 | 2725730.3072 | 1269001.1021 | 2725729.0112 | 1269000.0958 | 2725722.0375 | 1269000.6268
53 | 2725771.5056 | 1269015.3477 | 2725777.6812 | 1269012.7546 | 2725790.5227 | 1269008.7963
54 | 2725205.7607 | 1269047.7286 | 2725203.0241 | 1269027.6854 | 2725201.2612 | 1269019.9409 | 2725196.2382 | 1269009.0243 | 2725189.5952 | 1268999.2412 | 2725187.9919 | 1268993.2016 | 2725187.4999 | 1268985.5174 | 2725189.896 | 1268978.3171 | 2725195.7756 | 1268972.6253 | 2725203.6131 | 1268966.9083 | 2725220.184 | 1268953.0844
55 | 2725233.5218 | 1268944.6141 | 2725230.068 | 1268946.2609 | 2725222.5423 | 1268951.117 | 2725220.184 | 1268953.0844
56 | 2725518.4629 | 1268918.5436 | 2725507.5653 | 1268924.8879
57 | 2725518.4629 | 1268918.5436 | 2725507.1856 | 1268888.315
58 | 2725518.4629 | 1268918.5436 | 2725531.0782 | 1268911.1937
59 | 2725318.9066 | 1268939.1713 | 2725334.7452 | 1268900.6884
60 | 2725318.9066 | 1268939.1713 | 2725341.3192 | 1268935.9103 | 2725351.877 | 1268933.2078
61 | 2725688.4886 | 1268731.3512 | 2725674.5121 | 1268734.9145
62 | 2725688.4886 | 1268731.3512 | 2725692.0137 | 1268738.6885 | 2725697.7733 | 1268747.0292
63 | 2725669.1812 | 1268736.2736 | 2725674.5121 | 1268734.9145
64 | 2725473.724 | 1268843.3471 | 2725474.6408 | 1268843.0226
65 | 2725445.5888 | 1268817.9602 | 2725438.7973 | 1268799.3427
66 | 2725412.8995 | 1268882.6021 | 2725412.8055 | 1268871.0783
67 | 2725388.6421 | 1268937.2601 | 2725377.7574 | 1268920.5581
68 | 2725377.7574 | 1268920.5581 | 2725374.783 | 1268915.9908 | 2725375.0762 | 1268906.3209
69 | 2725377.7574 | 1268920.5581 | 2725372.1284 | 1268924.0085 | 2725356.2835 | 1268932.0798 | 2725351.877 | 1268933.2078
70 | 2725529.0471 | 1268961.0412 | 2725527.0408 | 1268956.6167 | 2725528.7135 | 1268951.9479 | 2725535.8035 | 1268948.829 | 2725530.7323 | 1268936.0008
71 | 2725593.5144 | 1269039.7286 | 2725590.2489 | 1269034.3431
72 | 2725447.9653 | 1268741.69 | 2725438.0507 | 1268744.0377
73 | 2725367.3873 | 1268866.5102 | 2725349.0774 | 1268865.8656
74 | 2725349.0774 | 1268865.8656 | 2725347.8995 | 1268868.7276
75 | 2725335.3846 | 1268899.1348 | 2725347.8995 | 1268868.7276
76 | 2725631.5989 | 1268968.6057 | 2725625.1498 | 1268967.0782 | 2725611.9509 | 1268974.2718
77 | 2725631.5989 | 1268968.6057 | 2725623.3813 | 1268954.3764
78 | 2725631.5989 | 1268968.6057 | 2725638.0024 | 1268979.7077 | 2725636.68 | 1268984.5396 | 2725636.4926 | 1268993.3438
79 | 2725573.754 | 1268947.3452 | 2725575.2317 | 1268949.8387
80 | 2725573.754 | 1268947.3452 | 2725580.8684 | 1268948.7421 | 2725590.6623 | 1268943.0909
81 | 2725612.4093 | 1268935.378 | 2725623.3813 | 1268954.3764
82 | 2725648.1332 | 1268970.2477 | 2725643.8631 | 1268972.4478 | 2725642.0518 | 1268974.4333 | 2725638.3996 | 1268991.8162 | 2725636.4926 | 1268993.3438
83 | 2725609.6249 | 1268932.1491 | 2725590.6623 | 1268943.0909
84 | 2725609.6249 | 1268932.1491 | 2725610.9518 | 1268934.5351 | 2725612.4093 | 1268935.378
85 | 2725648.1332 | 1268970.2477 | 2725648.3632 | 1268961.2108
86 | 2725648.3632 | 1268961.2108 | 2725661.4602 | 1268954.2416
87 | 2725648.1332 | 1268970.2477 | 2725648.0626 | 1268972.9121
88 | 2725677.6631 | 1268945.6195 | 2725661.4602 | 1268954.2416
89 | 2725558.1187 | 1268926.438 | 2725544.7151 | 1268903.2428
90 | 2725558.1187 | 1268926.438 | 2725573.3985 | 1268917.9107
91 | 2725544.7151 | 1268903.2428 | 2725535.4968 | 1268908.6175
92 | 2725544.7151 | 1268903.2428 | 2725550.2648 | 1268900.0101
93 | 2725586.3784 | 1268911.8705 | 2725576.7517 | 1268917.192 | 2725574.1862 | 1268917.4711 | 2725573.3985 | 1268917.9107
94 | 2725606.39 | 1268922.8495 | 2725609.5142 | 1268928.1542 | 2725609.6249 | 1268932.1491
95 | 2725677.6631 | 1268945.6195 | 2725677.0071 | 1268943.5481 | 2725673.1873 | 1268935.26
96 | 2725758.4654 | 1268961.7204 | 2725751.1027 | 1268992.7523
97 | 2725758.4654 | 1268961.7204 | 2725764.1817 | 1268937.2193 | 2725767.7237 | 1268916.1975 | 2725768.0627 | 1268913.5995
98 | 2725758.4654 | 1268961.7204 | 2725745.318 | 1268963.9983 | 2725743.2529 | 1268963.0534 | 2725737.9888 | 1268963.8533 | 2725732.3215 | 1268960.9633 | 2725730.6918 | 1268961.2229
99 | 2725770.1648 | 1268886.4218 | 2725770.1078 | 1268897.9313 | 2725768.0627 | 1268913.5995
100 | 2725770.1648 | 1268886.4218 | 2725767.1458 | 1268869.0107
101 | 2725783.3621 | 1268881.4537 | 2725770.1648 | 1268886.4218
102 | 2725766.1757 | 1268863.4156 | 2725767.1458 | 1268869.0107
103 | 2725783.3621 | 1268881.4537 | 2725791.8024 | 1268885.6373 | 2725791.8024 | 1268885.6373
104 | 2725807.0171 | 1268891.7207 | 2725812.0721 | 1268893.7419
105 | 2725807.0171 | 1268891.7207 | 2725791.8024 | 1268885.6373
106 | 2725744.9256 | 1268817.3762 | 2725757.429 | 1268841.8094 | 2725766.1757 | 1268863.4156
107 | 2725744.9256 | 1268817.3762 | 2725729.4731 | 1268823.9534 | 2725726.7461 | 1268824.7458
108 | 2725744.9256 | 1268817.3762 | 2725732.4002 | 1268797.1575 | 2725731.81 | 1268796.3034
109 | 2725657.0451 | 1268739.3676 | 2725669.1812 | 1268736.2736
110 | 2725657.0451 | 1268739.3676 | 2725639.2599 | 1268743.3815
111 | 2725657.0451 | 1268739.3676 | 2725660.4285 | 1268755.8437 | 2725662.5866 | 1268785.0135
112 | 2725616.2418 | 1268701.8542 | 2725618.5127 | 1268712.7737
113 | 2725616.2418 | 1268701.8542 | 2725578.1563 | 1268710.869
114 | 2725625.5231 | 1268746.4817 | 2725618.5127 | 1268712.7737
115 | 2725578.1563 | 1268710.869 | 2725567.6396 | 1268713.3583
116 | 2725663.921 | 1268843.5353 | 2725652.9253 | 1268847.4884
117 | 2725629.4651 | 1268855.9225 | 2725652.9253 | 1268847.4884
118 | 2725531.0782 | 1268911.1937 | 2725535.4968 | 1268908.6175
119 | 2725571.3955 | 1268887.7016 | 2725550.2648 | 1268900.0101
120 | 2725598.0564 | 1268908.6926 | 2725598.0564 | 1268908.6926 | 2725592.0176 | 1268908.7531 | 2725586.3784 | 1268911.8705
121 | 2725606.39 | 1268922.8495 | 2725607.8821 | 1268921.7135 | 2725608.2158 | 1268919.83 | 2725603.274 | 1268910.0825 | 2725611.5475 | 1268905.4764
122 | 2725606.0922 | 1268922.3437 | 2725606.39 | 1268922.8495
123 | 2725598.0564 | 1268908.6926 | 2725606.0922 | 1268922.3437
124 | 2725611.5475 | 1268905.4764 | 2725627.8501 | 1268896.2338
125 | 2725628.1774 | 1268896.0483 | 2725627.8501 | 1268896.2338
126 | 2725531.0782 | 1268911.1937 | 2725533.6879 | 1268915.5643 | 2725533.9816 | 1268917.3278 | 2725529.7395 | 1268919.2728 | 2725527.7996 | 1268920.9331 | 2725526.5599 | 1268923.6537 | 2725526.6523 | 1268925.6798 | 2725530.7323 | 1268936.0008
127 | 2725504.147 | 1268880.1699 | 2725507.1856 | 1268888.315
128 | 2725629.4651 | 1268855.9225 | 2725621.5638 | 1268841.8673
129 | 2725621.5638 | 1268841.8673 | 2725611.2542 | 1268823.5284
130 | 2725603.983 | 1268810.5943 | 2725611.2542 | 1268823.5284
131 | 2725592.0747 | 1268875.6561 | 2725571.3955 | 1268887.7016
132 | 2725625.5231 | 1268746.4817 | 2725639.2599 | 1268743.3815
133 | 2725499.183 | 1268866.864 | 2725504.147 | 1268880.1699
134 | 2725603.983 | 1268810.5943 | 2725578.8156 | 1268824.1073
135 | 2725604.4391 | 1268810.3346 | 2725603.983 | 1268810.5943
136 | 2725578.8156 | 1268824.1073 | 2725569.8309 | 1268828.9314
137 | 2725621.5198 | 1268800.6079 | 2725604.4391 | 1268810.3346
138 | 2725559.4618 | 1268834.4988 | 2725569.8309 | 1268828.9314
139 | 2725559.4618 | 1268834.4988 | 2725555.9408 | 1268836.3893
140 | 2725488.9342 | 1268837.964 | 2725499.183 | 1268866.864
141 | 2725499.183 | 1268866.864 | 2725514.0712 | 1268858.8702
142 | 2725233.5218 | 1268944.6141 | 2725236.3877 | 1268943.2476 | 2725252.7213 | 1268938.3894 | 2725252.7213 | 1268938.3894
143 | 2725488.9342 | 1268837.964 | 2725486.8671 | 1268832.3504
144 | 2725488.9342 | 1268837.964 | 2725474.6408 | 1268843.0226
145 | 2725527.3876 | 1268851.7203 | 2725514.0712 | 1268858.8702
146 | 2725477.3636 | 1268806.5424 | 2725486.8671 | 1268832.3504
147 | 2725527.3876 | 1268851.7203 | 2725535.4442 | 1268847.3945
148 | 2725477.3636 | 1268806.5424 | 2725475.2759 | 1268800.8729 | 2725481.3295 | 1268798.6805
149 | 2725537.9018 | 1268846.0749 | 2725535.4442 | 1268847.3945
150 | 2725481.3295 | 1268798.6805 | 2725490.0888 | 1268795.5081
151 | 2725511.9135 | 1268787.6038 | 2725490.0888 | 1268795.5081
152 | 2725515.6219 | 1268786.2607 | 2725511.9135 | 1268787.6038
153 | 2725515.6219 | 1268786.2607 | 2725532.6578 | 1268780.0945
154 | 2725515.6219 | 1268786.2607 | 2725511.7572 | 1268775.8069
155 | 2725532.6578 | 1268780.0945 | 2725536.2166 | 1268778.8064
156 | 2725510.234 | 1268771.6865 | 2725511.7572 | 1268775.8069
157 | 2725558.3918 | 1268770.7801 | 2725536.2166 | 1268778.8064
158 | 2725510.234 | 1268771.6865 | 2725505.6555 | 1268759.3018 | 2725502.7779 | 1268746.4173
159 | 2725558.3918 | 1268770.7801 | 2725558.5291 | 1268770.7304
160 | 2725502.3866 | 1268744.6649 | 2725502.7779 | 1268746.4173
161 | 2725555.9408 | 1268836.3893 | 2725537.9018 | 1268846.0749
162 | 2725335.3846 | 1268899.1348 | 2725334.7452 | 1268900.6884
163 | 2725558.5291 | 1268770.7304 | 2725585.5386 | 1268760.9542
164 | 2725585.5386 | 1268760.9542 | 2725588.2851 | 1268759.9601
165 | 2725499.0221 | 1268729.6001 | 2725502.3866 | 1268744.6649
166 | 2725499.0221 | 1268729.6001 | 2725524.1248 | 1268723.6583
167 | 2725499.0221 | 1268729.6001 | 2725496.1476 | 1268730.2808
168 | 2725264.6647 | 1268972.349 | 2725253.7672 | 1268967.5052 | 2725251.4381 | 1268964.453 | 2725251.2669 | 1268960.8126 | 2725253.8412 | 1268951.959 | 2725252.7213 | 1268938.3894
169 | 2725264.9542 | 1268972.4776 | 2725264.6647 | 1268972.349
170 | 2725447.9653 | 1268741.69 | 2725467.0322 | 1268737.1751
171 | 2725472.6709 | 1268735.8399 | 2725467.0322 | 1268737.1751
172 | 2725496.1476 | 1268730.2808 | 2725472.6709 | 1268735.8399
173 | 2725524.1248 | 1268723.6583 | 2725535.5232 | 1268720.9603
174 | 2725535.5232 | 1268720.9603 | 2725567.6396 | 1268713.3583

## bus_geodata
| x | y | coords
0 | 2725426.6344 | 1269178.5047
1 | 2725345.8566 | 1269217.1338
2 | 2725336.6525 | 1269210.2878
3 | 2725302.3008 | 1269150.7187
4 | 2725624.7702 | 1269091.7413
5 | 2725591.9525 | 1269112.7854
6 | 2725625.32 | 1269077.8763
7 | 2725586.3068 | 1269096.9366
8 | 2725262.2175 | 1269068.0774
9 | 2725318.2423 | 1268940.6751
10 | 2725255.7883 | 1269073.7686
11 | 2725457.0078 | 1268849.2632
12 | 2725451.4351 | 1268879.4617
13 | 2725467.3783 | 1268845.5929
14 | 2725420.5763 | 1268896.1554
15 | 2725520.5892 | 1269019.2822
16 | 2725511.4656 | 1268970.4097
17 | 2725531.7874 | 1269012.1894
18 | 2725519.6989 | 1268963.6576
19 | 2725517.6104 | 1268968.1938
20 | 2725571.7214 | 1269053.1556
21 | 2725568.2812 | 1269047.4884
22 | 2725577.1982 | 1269071.3667
23 | 2725581.6682 | 1269047.028
24 | 2725566.0637 | 1269075.1999
25 | 2725421.1943 | 1268715.7681
26 | 2725429.5473 | 1268746.0512
27 | 2725435.9296 | 1268688.9701
28 | 2725418.9444 | 1268753.2773
29 | 2725409.3288 | 1268757.2658
30 | 2725429.3118 | 1268781.5722
31 | 2725424.8301 | 1268799.3738
32 | 2725635.9905 | 1269016.9327
33 | 2725636.3257 | 1269001.1854
34 | 2725662.4147 | 1269019.8455
35 | 2725692.284 | 1269020.1552
36 | 2725664.3915 | 1269019.866
37 | 2725689.2892 | 1269003.1202
38 | 2725625.9238 | 1269062.65
39 | 2725626.1092 | 1269057.9312
40 | 2725743.6694 | 1269024.0745
41 | 2725755.8359 | 1269021.1023
42 | 2725748.3917 | 1269004.1787
43 | 2725771.5056 | 1269015.3477
44 | 2725790.5227 | 1269008.7963
45 | 2725205.7607 | 1269047.7286
46 | 2725220.184 | 1268953.0844
47 | 2725507.5653 | 1268924.8879
48 | 2725518.4629 | 1268918.5436
49 | 2725318.9066 | 1268939.1713
50 | 2725688.4886 | 1268731.3512
51 | 2725674.5121 | 1268734.9145
52 | 2725697.7733 | 1268747.0292
53 | 2725473.724 | 1268843.3471
54 | 2725445.5888 | 1268817.9602
55 | 2725438.7973 | 1268799.3427
56 | 2725412.8995 | 1268882.6021
57 | 2725428.8552 | 1268910.778
58 | 2725377.7574 | 1268920.5581
59 | 2725554.5507 | 1269003.203
60 | 2725529.0471 | 1268961.0412
61 | 2725593.5144 | 1269039.7286
62 | 2725438.0507 | 1268744.0377
63 | 2725349.0774 | 1268865.8656
64 | 2725367.3873 | 1268866.5102
65 | 2725347.8995 | 1268868.7276
66 | 2725611.9509 | 1268974.2718
67 | 2725631.5989 | 1268968.6057
68 | 2725575.2317 | 1268949.8387
69 | 2725573.754 | 1268947.3452
70 | 2725623.3813 | 1268954.3764
71 | 2725636.4926 | 1268993.3438
72 | 2725590.6623 | 1268943.0909
73 | 2725612.4093 | 1268935.378
74 | 2725648.3632 | 1268961.2108
75 | 2725648.1332 | 1268970.2477
76 | 2725661.4602 | 1268954.2416
77 | 2725558.1187 | 1268926.438
78 | 2725544.7151 | 1268903.2428
79 | 2725573.3985 | 1268917.9107
80 | 2725609.6249 | 1268932.1491
81 | 2725648.0626 | 1268972.9121
82 | 2725677.6631 | 1268945.6195
83 | 2725722.0375 | 1269000.6268
84 | 2725751.1027 | 1268992.7523
85 | 2725758.4654 | 1268961.7204
86 | 2725768.0627 | 1268913.5995
87 | 2725730.6918 | 1268961.2229
88 | 2725673.1873 | 1268935.26
89 | 2725770.1648 | 1268886.4218
90 | 2725767.1458 | 1268869.0107
91 | 2725783.3621 | 1268881.4537
92 | 2725812.0721 | 1268893.7419
93 | 2725807.0171 | 1268891.7207
94 | 2725791.8024 | 1268885.6373
95 | 2725590.2489 | 1269034.3431
96 | 2725766.1757 | 1268863.4156
97 | 2725744.9256 | 1268817.3762
98 | 2725731.81 | 1268796.3034
99 | 2725726.7461 | 1268824.7458
100 | 2725669.1812 | 1268736.2736
101 | 2725657.0451 | 1268739.3676
102 | 2725616.2418 | 1268701.8542
103 | 2725618.5127 | 1268712.7737
104 | 2725578.1563 | 1268710.869
105 | 2725663.921 | 1268843.5353
106 | 2725652.9253 | 1268847.4884
107 | 2725535.4968 | 1268908.6175
108 | 2725550.2648 | 1268900.0101
109 | 2725586.3784 | 1268911.8705
110 | 2725606.39 | 1268922.8495
111 | 2725598.0564 | 1268908.6926
112 | 2725606.0922 | 1268922.3437
113 | 2725611.5475 | 1268905.4764
114 | 2725627.8501 | 1268896.2338
115 | 2725530.7323 | 1268936.0008
116 | 2725531.0782 | 1268911.1937
117 | 2725507.1856 | 1268888.315
118 | 2725628.1774 | 1268896.0483
119 | 2725629.4651 | 1268855.9225
120 | 2725621.5638 | 1268841.8673
121 | 2725611.2542 | 1268823.5284
122 | 2725592.0747 | 1268875.6561
123 | 2725571.3955 | 1268887.7016
124 | 2725662.5866 | 1268785.0135
125 | 2725639.2599 | 1268743.3815
126 | 2725625.5231 | 1268746.4817
127 | 2725504.147 | 1268880.1699
128 | 2725603.983 | 1268810.5943
129 | 2725578.8156 | 1268824.1073
130 | 2725604.4391 | 1268810.3346
131 | 2725569.8309 | 1268828.9314
132 | 2725621.5198 | 1268800.6079
133 | 2725559.4618 | 1268834.4988
134 | 2725499.183 | 1268866.864
135 | 2725233.5218 | 1268944.6141
136 | 2725488.9342 | 1268837.964
137 | 2725514.0712 | 1268858.8702
138 | 2725486.8671 | 1268832.3504
139 | 2725474.6408 | 1268843.0226
140 | 2725527.3876 | 1268851.7203
141 | 2725477.3636 | 1268806.5424
142 | 2725535.4442 | 1268847.3945
143 | 2725481.3295 | 1268798.6805
144 | 2725490.0888 | 1268795.5081
145 | 2725511.9135 | 1268787.6038
146 | 2725515.6219 | 1268786.2607
147 | 2725532.6578 | 1268780.0945
148 | 2725511.7572 | 1268775.8069
149 | 2725536.2166 | 1268778.8064
150 | 2725510.234 | 1268771.6865
151 | 2725558.3918 | 1268770.7801
152 | 2725502.7779 | 1268746.4173
153 | 2725555.9408 | 1268836.3893
154 | 2725537.9018 | 1268846.0749
155 | 2725351.877 | 1268933.2078
156 | 2725334.7452 | 1268900.6884
157 | 2725388.6421 | 1268937.2601
158 | 2725375.0762 | 1268906.3209
159 | 2725335.3846 | 1268899.1348
160 | 2725412.8055 | 1268871.0783
161 | 2725558.5291 | 1268770.7304
162 | 2725585.5386 | 1268760.9542
163 | 2725588.2851 | 1268759.9601
164 | 2725502.3866 | 1268744.6649
165 | 2725499.0221 | 1268729.6001
166 | 2725252.7213 | 1268938.3894
167 | 2725264.6647 | 1268972.349
168 | 2725264.9542 | 1268972.4776
169 | 2725447.9653 | 1268741.69
170 | 2725467.0322 | 1268737.1751
171 | 2725472.6709 | 1268735.8399
172 | 2725496.1476 | 1268730.2808
173 | 2725524.1248 | 1268723.6583
174 | 2725535.5232 | 1268720.9603
175 | 2725567.6396 | 1268713.3583
176 | 2725544.7151 | 1268903.2428

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1