## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_53-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_53-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_53-6_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_53-6_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_53-6_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_53-6_0_4_node_75 | 0.4 | n |  | TRUE
6 | bus_LV_53-6_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_53-6_0_4_node_104 | 0.4 | n |  | TRUE
8 | bus_LV_53-6_0_4_node_103 | 0.4 | n |  | TRUE
9 | bus_LV_53-6_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_53-6_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_53-6_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_53-6_0_4_node_69 | 0.4 | n |  | TRUE
13 | bus_LV_53-6_0_4_node_72 | 0.4 | n |  | TRUE
14 | bus_LV_53-6_0_4_node_68 | 0.4 | n |  | TRUE
15 | bus_LV_53-6_0_4_node_60 | 0.4 | n |  | TRUE
16 | bus_LV_53-6_0_4_node_58 | 0.4 | n |  | TRUE
17 | bus_LV_53-6_0_4_node_74 | 0.4 | n |  | TRUE
18 | bus_LV_53-6_0_4_node_73 | 0.4 | n |  | TRUE
19 | bus_LV_53-6_0_4_node_64 | 0.4 | n |  | TRUE
20 | bus_LV_53-6_0_4_node_93 | 0.4 | n |  | TRUE
21 | bus_LV_53-6_0_4_node_87 | 0.4 | n |  | TRUE
22 | bus_LV_53-6_0_4_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_53-6_0_4_node_95 | 0.4 | n |  | TRUE
24 | bus_LV_53-6_0_4_node_61 | 0.4 | n |  | TRUE
25 | bus_LV_53-6_0_4_node_70 | 0.4 | n |  | TRUE
26 | bus_LV_53-6_0_4_node_62 | 0.4 | n |  | TRUE
27 | bus_LV_53-6_0_4_node_9 | 0.4 | n |  | TRUE
28 | bus_LV_53-6_0_4_node_11 | 0.4 | n |  | TRUE
29 | bus_LV_53-6_0_4_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_53-6_0_4_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_53-6_0_4_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_53-6_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_53-6_0_4_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_53-6_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_53-6_0_4_node_37 | 0.4 | n |  | TRUE
36 | bus_LV_53-6_0_4_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_53-6_0_4_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_53-6_0_4_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_53-6_0_4_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_53-6_0_4_node_17 | 0.4 | n |  | TRUE
41 | bus_LV_53-6_0_4_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_53-6_0_4_node_18 | 0.4 | n |  | TRUE
43 | bus_LV_53-6_0_4_node_16 | 0.4 | n |  | TRUE
44 | bus_LV_53-6_0_4_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_53-6_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_53-6_0_4_node_105 | 0.4 | n |  | TRUE
47 | bus_LV_53-6_0_4_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_53-6_0_4_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_53-6_0_4_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_53-6_0_4_node_55 | 0.4 | n |  | TRUE
51 | bus_LV_53-6_0_4_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_53-6_0_4_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_53-6_0_4_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_53-6_0_4_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_53-6_0_4_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_53-6_0_4_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_53-6_0_4_node_82 | 0.4 | n |  | TRUE
58 | bus_LV_53-6_0_4_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_53-6_0_4_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_53-6_0_4_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_53-6_0_4_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_53-6_0_4_node_83 | 0.4 | n |  | TRUE
63 | bus_LV_53-6_0_4_node_97 | 0.4 | n |  | TRUE
64 | bus_LV_53-6_0_4_node_98 | 0.4 | n |  | TRUE
65 | bus_LV_53-6_0_4_node_102 | 0.4 | n |  | TRUE
66 | bus_LV_53-6_0_4_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_53-6_0_4_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_53-6_0_4_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_53-6_0_4_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_53-6_0_4_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_53-6_0_4_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_53-6_0_4_node_47 | 0.4 | n |  | TRUE
73 | bus_LV_53-6_0_4_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_53-6_0_4_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_53-6_0_4_node_100 | 0.4 | n |  | TRUE
76 | bus_LV_53-6_0_4_node_84 | 0.4 | n |  | TRUE
77 | bus_LV_53-6_0_4_node_96 | 0.4 | n |  | TRUE
78 | bus_LV_53-6_0_4_node_99 | 0.4 | n |  | TRUE
79 | bus_LV_53-6_0_4_node_59 | 0.4 | n |  | TRUE
80 | bus_LV_53-6_0_4_node_56 | 0.4 | n |  | TRUE
81 | bus_LV_53-6_0_4_node_90 | 0.4 | n |  | TRUE
82 | bus_LV_53-6_0_4_node_101 | 0.4 | n |  | TRUE
83 | bus_LV_53-6_0_4_node_89 | 0.4 | n |  | TRUE
84 | bus_LV_53-6_0_4_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_53-6_0_4_node_86 | 0.4 | n |  | TRUE
86 | bus_LV_53-6_0_4_node_85 | 0.4 | n |  | TRUE
87 | bus_LV_53-6_0_4_node_94 | 0.4 | n |  | TRUE
88 | bus_LV_53-6_0_4_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_53-6_0_4_node_106 | 0.4 | n |  | TRUE
90 | bus_LV_53-6_0_4_node_71 | 0.4 | n |  | TRUE
91 | bus_LV_53-6_0_4_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_53-6_0_4_node_79 | 0.4 | n |  | TRUE
93 | bus_LV_53-6_0_4_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_53-6_0_4_node_77 | 0.4 | n |  | TRUE
95 | bus_LV_53-6_0_4_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_53-6_0_4_node_92 | 0.4 | n |  | TRUE
97 | bus_LV_53-6_0_4_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_53-6_0_4_node_91 | 0.4 | n |  | TRUE
99 | bus_MV_351_1_node_113 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_53-6_0_4_load_0 | 0 | 0.021004 | 0.005264 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_53-6_0_4_load_75 | 5 | 0.013122 | 0.0032887 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_53-6_0_4_load_104 | 7 | 0.012935 | 0.0032419 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_53-6_0_4_load_103 | 8 | 0.012935 | 0.0032419 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_53-6_0_4_load_69 | 12 | 0.0050448 | 0.0012644 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_53-6_0_4_load_72 | 13 | 0.0093168 | 0.002335 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_53-6_0_4_load_68 | 14 | 0.0044503 | 0.0011154 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_53-6_0_4_load_60 | 15 | 0.0026102 | 0.00065419 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_53-6_0_4_load_74 | 17 | 0.0029175 | 0.00073118 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_53-6_0_4_load_73 | 18 | 0.0041029 | 0.0010283 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_53-6_0_4_load_93 | 20 | 0.00082981 | 0.00020797 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_53-6_0_4_load_87 | 21 | 0.00082672 | 0.0002072 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_53-6_0_4_load_95 | 23 | 0.003384 | 0.00084811 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_53-6_0_4_load_70 | 25 | 0.0014103 | 0.00035346 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_53-6_0_4_load_62 | 26 | 0.0017082 | 0.00042812 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_53-6_0_4_load_9 | 27 | 0.0078306 | 0.0019625 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_53-6_0_4_load_14 | 29 | 0.0049132 | 0.0012314 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_53-6_0_4_load_13 | 30 | 0.0037258 | 0.00093378 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_53-6_0_4_load_26 | 33 | 0.010082 | 0.0025268 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_53-6_0_4_load_32 | 36 | 0.0067203 | 0.0016843 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_53-6_0_4_load_17 | 40 | 0.010753 | 0.0026951 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_53-6_0_4_load_21 | 41 | 0.0050416 | 0.0012636 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_53-6_0_4_load_16 | 43 | 0.0014851 | 0.00037221 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_53-6_0_4_load_23 | 44 | 0.0047646 | 0.0011941 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_53-6_0_4_load_105 | 46 | 0.0058111 | 0.0014564 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_53-6_0_4_load_33 | 48 | 0.0085066 | 0.0021319 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_53-6_0_4_load_55 | 50 | 0.0026732 | 0.00066996 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_53-6_0_4_load_28 | 52 | 0.010202 | 0.0025569 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_53-6_0_4_load_29 | 53 | 0.0070165 | 0.0017585 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_53-6_0_4_load_82 | 57 | 0.0072917 | 0.0018275 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_53-6_0_4_load_53 | 59 | 0.0019597 | 0.00049115 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_53-6_0_4_load_39 | 60 | 0.013717 | 0.0034377 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_53-6_0_4_load_97 | 63 | 0.0058436 | 0.0014646 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_53-6_0_4_load_98 | 64 | 0.0058455 | 0.001465 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_53-6_0_4_load_102 | 65 | 0.0050522 | 0.0012662 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_53-6_0_4_load_45 | 66 | 0.012618 | 0.0031624 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_53-6_0_4_load_40 | 68 | 0.0073498 | 0.001842 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_53-6_0_4_load_46 | 70 | 0.0065775 | 0.0016485 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_53-6_0_4_load_54 | 73 | 0.0032524 | 0.00081512 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_53-6_0_4_load_84 | 76 | 0.0025546 | 0.00064025 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_53-6_0_4_load_96 | 77 | 0.006071 | 0.0015215 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_53-6_0_4_load_99 | 78 | 0.016389 | 0.0041074 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_53-6_0_4_load_59 | 79 | 0.0084303 | 0.0021128 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_53-6_0_4_load_56 | 80 | 0.0099439 | 0.0024922 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_53-6_0_4_load_90 | 81 | 0.011523 | 0.0028878 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_53-6_0_4_load_101 | 82 | 0.0052147 | 0.0013069 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_53-6_0_4_load_85 | 86 | 0.0038828 | 0.00097311 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_53-6_0_4_load_94 | 87 | 0.010285 | 0.0025777 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_53-6_0_4_load_80 | 88 | 0.0063031 | 0.0015797 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_53-6_0_4_load_106 | 89 | 0.0049441 | 0.0012391 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_53-6_0_4_load_71 | 90 | 0.0046724 | 0.001171 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_53-6_0_4_load_78 | 91 | 0.0014278 | 0.00035784 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_53-6_0_4_load_79 | 92 | 0.0051466 | 0.0012899 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_53-6_0_4_load_76 | 93 | 0.0080501 | 0.0020175 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_53-6_0_4_load_77 | 94 | 0.012023 | 0.0030131 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_53-6_0_4_load_92 | 96 | 0.01268 | 0.0031778 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_53-6_0_4_load_88 | 97 | 0.012238 | 0.0030671 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_53-6_0_4_load_91 | 98 | 0.0054553 | 0.0013672 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 82 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_53-6_0_4_line_0 |  | 0 | 1 | 0.054016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_53-6_0_4_line_1 |  | 1 | 2 | 0.13245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_53-6_0_4_line_2 |  | 2 | 3 | 0.010519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_53-6_0_4_line_3 |  | 3 | 4 | 0.042105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_53-6_0_4_line_4 |  | 3 | 5 | 0.021554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_53-6_0_4_line_5 |  | 4 | 8 | 0.02779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_53-6_0_4_line_6 |  | 6 | 7 | 0.03749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_53-6_0_4_line_7 |  | 6 | 8 | 0.015267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_53-6_0_4_line_8 |  | 7 | 16 | 0.038326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_53-6_0_4_line_9 |  | 9 | 10 | 0.019163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_53-6_0_4_line_10 |  | 9 | 11 | 0.028495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_53-6_0_4_line_11 |  | 9 | 12 | 0.017519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_53-6_0_4_line_12 |  | 10 | 13 | 0.020151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_53-6_0_4_line_13 |  | 11 | 14 | 0.026429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_53-6_0_4_line_14 |  | 11 | 15 | 0.043525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_53-6_0_4_line_15 |  | 12 | 25 | 0.019956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_53-6_0_4_line_16 |  | 13 | 18 | 0.030924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_53-6_0_4_line_17 |  | 14 | 26 | 0.031425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_53-6_0_4_line_18 |  | 15 | 24 | 0.018691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_53-6_0_4_line_19 |  | 16 | 81 | 0.031304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_53-6_0_4_line_20 |  | 17 | 18 | 0.033316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_53-6_0_4_line_21 |  | 19 | 20 | 0.019004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_53-6_0_4_line_22 |  | 19 | 21 | 0.035573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_53-6_0_4_line_23 |  | 20 | 87 | 0.038478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_53-6_0_4_line_24 |  | 21 | 88 | 0.023891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_53-6_0_4_line_25 |  | 22 | 23 | 0.024183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_53-6_0_4_line_26 |  | 22 | 24 | 0.010455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_53-6_0_4_line_27 |  | 25 | 90 | 0.018933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_53-6_0_4_line_28 |  | 27 | 28 | 0.019729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_53-6_0_4_line_29 |  | 28 | 29 | 0.017754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_53-6_0_4_line_30 |  | 29 | 32 | 0.01947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_53-6_0_4_line_31 |  | 30 | 31 | 0.0052748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_53-6_0_4_line_32 |  | 31 | 35 | 0.028465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_53-6_0_4_line_33 |  | 31 | 36 | 0.017583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_53-6_0_4_line_34 |  | 32 | 37 | 0.005375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_53-6_0_4_line_35 |  | 32 | 38 | 0.025279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_53-6_0_4_line_36 |  | 33 | 34 | 0.032806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_53-6_0_4_line_37 |  | 34 | 39 | 0.008408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_53-6_0_4_line_38 |  | 35 | 58 | 0.003976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_53-6_0_4_line_39 |  | 35 | 59 | 0.025385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_53-6_0_4_line_40 |  | 36 | 48 | 0.024439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_53-6_0_4_line_41 |  | 37 | 45 | 0.033211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_53-6_0_4_line_42 |  | 37 | 46 | 0.016436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_53-6_0_4_line_43 |  | 38 | 44 | 0.018443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_53-6_0_4_line_44 |  | 38 | 42 | 0.003745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_53-6_0_4_line_45 |  | 39 | 40 | 0.018599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_53-6_0_4_line_46 |  | 40 | 43 | 0.026887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_53-6_0_4_line_47 |  | 41 | 42 | 0.018655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_53-6_0_4_line_48 |  | 42 | 43 | 0.018295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_53-6_0_4_line_49 |  | 45 | 47 | 0.019986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_53-6_0_4_line_50 |  | 45 | 48 | 0.01547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_53-6_0_4_line_51 |  | 47 | 55 | 0.024874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_53-6_0_4_line_52 |  | 47 | 56 | 0.034241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_53-6_0_4_line_53 |  | 47 | 57 | 0.02137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_53-6_0_4_line_54 |  | 49 | 50 | 0.023406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_53-6_0_4_line_55 |  | 49 | 51 | 0.033841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_53-6_0_4_line_56 |  | 50 | 54 | 0.016764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_53-6_0_4_line_57 |  | 51 | 53 | 0.025973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_53-6_0_4_line_58 |  | 52 | 53 | 0.018121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_53-6_0_4_line_59 |  | 54 | 72 | 0.012827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_53-6_0_4_line_60 |  | 55 | 65 | 0.050779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_53-6_0_4_line_61 |  | 56 | 60 | 0.0217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_53-6_0_4_line_62 |  | 57 | 62 | 0.010317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_53-6_0_4_line_63 |  | 58 | 66 | 0.025262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_53-6_0_4_line_64 |  | 59 | 67 | 1.5733e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_53-6_0_4_line_65 |  | 61 | 62 | 0.002433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_53-6_0_4_line_66 |  | 61 | 63 | 0.019545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_53-6_0_4_line_67 |  | 61 | 64 | 0.028284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_53-6_0_4_line_68 |  | 62 | 76 | 0.022044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_53-6_0_4_line_69 |  | 63 | 77 | 0.035567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_53-6_0_4_line_70 |  | 64 | 78 | 0.001485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_53-6_0_4_line_71 |  | 65 | 75 | 0.002768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_53-6_0_4_line_72 |  | 66 | 69 | 0.019276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_53-6_0_4_line_73 |  | 67 | 73 | 0.021517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_53-6_0_4_line_74 |  | 68 | 69 | 0.016668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_53-6_0_4_line_75 |  | 70 | 71 | 0.013372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_53-6_0_4_line_76 |  | 71 | 74 | 0.024757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_53-6_0_4_line_77 |  | 71 | 72 | 0.027972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_53-6_0_4_line_78 |  | 72 | 73 | 0.023471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_53-6_0_4_line_79 |  | 74 | 79 | 0.013942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_53-6_0_4_line_80 |  | 74 | 80 | 0.045676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_53-6_0_4_line_81 |  | 75 | 82 | 0.01581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_53-6_0_4_line_82 |  | 76 | 86 | 0.021346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_53-6_0_4_line_83 |  | 81 | 82 | 0.016611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_53-6_0_4_line_84 |  | 81 | 83 | 0.047264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_53-6_0_4_line_85 |  | 83 | 98 | 0.036524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_53-6_0_4_line_86 |  | 83 | 97 | 0.057708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_53-6_0_4_line_87 |  | 84 | 85 | 0.093714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_53-6_0_4_line_88 |  | 84 | 86 | 0.068332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_53-6_0_4_line_89 |  | 85 | 89 | 0.006376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_53-6_0_4_line_90 |  | 87 | 98 | 0.0042998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_53-6_0_4_line_91 |  | 88 | 92 | 0.032513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_53-6_0_4_line_92 |  | 90 | 91 | 0.0008434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_53-6_0_4_line_93 |  | 91 | 92 | 0.035112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_53-6_0_4_line_94 |  | 93 | 94 | 0.0069401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_53-6_0_4_line_95 |  | 94 | 95 | 0.019437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_53-6_0_4_line_96 |  | 95 | 96 | 0.029321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_53-6_0_4_line_97 |  | 95 | 97 | 0.0091202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_53-6_0_4_trafo_101 | 0.63 MVA 20/0.4 kV | 99 | 82 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2683148.578 | 1264605.6646 | 2683148.9709 | 1264599.6876 | 2683148.9148 | 1264592.9704 | 2683149.3245 | 1264585.8039 | 2683152.7163 | 1264584.0169 | 2683155.2801 | 1264553.8291
1 | 2683113.5124 | 1264512.8875 | 2683113.7221 | 1264556.8807 | 2683113.8615 | 1264586.5949 | 2683113.9693 | 1264609.4588 | 2683119.6897 | 1264605.4361 | 2683148.578 | 1264605.6646
2 | 2683113.5124 | 1264512.8875 | 2683106.2155 | 1264505.2901
3 | 2683066.7679 | 1264520.003 | 2683070.4304 | 1264518.7868 | 2683093.0327 | 1264510.2643 | 2683106.2155 | 1264505.2901
4 | 2683106.2155 | 1264505.2901 | 2683126.0691 | 1264496.8989
5 | 2683066.7679 | 1264520.003 | 2683066.5485 | 1264514.718 | 2683058.5743 | 1264493.6783
6 | 2683071.4854 | 1264485.5311 | 2683072.7316 | 1264484.7479 | 2683081.5858 | 1264475.3427 | 2683080.8571 | 1264468.238 | 2683074.3078 | 1264453.6853
7 | 2683071.4854 | 1264485.5311 | 2683058.5743 | 1264493.6783
8 | 2683055.6649 | 1264420.4132 | 2683065.5266 | 1264434.1736 | 2683074.3078 | 1264453.6853
9 | 2683245.9105 | 1264517.42 | 2683265.1309 | 1264517.4796
10 | 2683265.1309 | 1264517.4796 | 2683269.4388 | 1264517.4958 | 2683268.2944 | 1264510.5186 | 2683272.2297 | 1264505.9816 | 2683269.6253 | 1264495.1808
11 | 2683265.1309 | 1264517.4796 | 2683262.4944 | 1264505.2106 | 2683261.2619 | 1264500.3958
12 | 2683245.9105 | 1264517.42 | 2683225.7696 | 1264516.7745
13 | 2683269.6253 | 1264495.1808 | 2683271.0422 | 1264495.6456 | 2683273.664 | 1264495.5936 | 2683275.5877 | 1264494.8423 | 2683277.574 | 1264493.3914 | 2683279.0485 | 1264490.8435 | 2683285.4512 | 1264477.4488
14 | 2683269.6253 | 1264495.1808 | 2683267.7119 | 1264493.5971 | 2683266.1653 | 1264488.9717 | 2683263.7552 | 1264480.9425 | 2683257.2931 | 1264459.5458 | 2683255.6658 | 1264454.3655
15 | 2683261.2619 | 1264500.3958 | 2683259.3604 | 1264492.9679 | 2683255.7157 | 1264481.2319
16 | 2683225.7696 | 1264516.7745 | 2683194.8614 | 1264515.784
17 | 2683285.4512 | 1264477.4488 | 2683299.004 | 1264449.0965
18 | 2683254.7679 | 1264436.7034 | 2683253.1812 | 1264439.1941 | 2683252.5382 | 1264441.5314 | 2683252.5354 | 1264444.4003 | 2683255.6658 | 1264454.3655
19 | 2683055.6649 | 1264420.4132 | 2683082.8862 | 1264404.8166
20 | 2683194.8614 | 1264515.784 | 2683178.4485 | 1264515.2579 | 2683161.5645 | 1264514.6582
21 | 2683210.2228 | 1264341.5905 | 2683198.3878 | 1264346.5613 | 2683193.3832 | 1264350.1651
22 | 2683210.2228 | 1264341.5905 | 2683221.2651 | 1264375.4068
23 | 2683193.3832 | 1264350.1651 | 2683182.4694 | 1264358.0241 | 2683175.5542 | 1264361.2961 | 2683167.8182 | 1264365.6241 | 2683160.2831 | 1264369.5879 | 2683160.2831 | 1264369.5879
24 | 2683228.6809 | 1264398.1174 | 2683221.2651 | 1264375.4068
25 | 2683251.9572 | 1264426.6337 | 2683249.3407 | 1264425.774 | 2683247.2674 | 1264424.3103 | 2683245.5591 | 1264422.0734 | 2683240.6519 | 1264406.7642
26 | 2683251.9572 | 1264426.6337 | 2683253.1404 | 1264430.8648 | 2683254.7679 | 1264436.7034
27 | 2683249.9341 | 1264463.2036 | 2683253.6685 | 1264474.64 | 2683255.7157 | 1264481.2319
28 | 2683003.1518 | 1264287.4714 | 2682985.1227 | 1264295.4826
29 | 2683003.1518 | 1264287.4714 | 2683019.3755 | 1264280.2616
30 | 2683037.8696 | 1264274.9712 | 2683029.2022 | 1264275.8947 | 2683019.3755 | 1264280.2616
31 | 2682988.1357 | 1264337.6779 | 2682984.782 | 1264333.6066
32 | 2682984.6957 | 1264354.6874 | 2682997.3706 | 1264348.8941 | 2682988.1357 | 1264337.6779
33 | 2682988.1357 | 1264337.6779 | 2682993.9507 | 1264334.9796 | 2683004.0856 | 1264330.2767
34 | 2683038.2085 | 1264280.3357 | 2683037.8696 | 1264274.9712
35 | 2683035.5871 | 1264249.7971 | 2683037.7955 | 1264273.8137 | 2683037.8696 | 1264274.9712
36 | 2682980.0006 | 1264231.5137 | 2682977.582 | 1264234.7823 | 2682965.297 | 1264240.6924 | 2682971.522 | 1264254.4572
37 | 2682980.0006 | 1264231.5137 | 2682988.4145 | 1264230.9424
38 | 2682984.6957 | 1264354.6874 | 2682986.3547 | 1264358.3025
39 | 2682984.6957 | 1264354.6874 | 2682961.6044 | 1264365.2317
40 | 2683026.2546 | 1264319.9897 | 2683004.0856 | 1264330.2767
41 | 2683040.2886 | 1264313.4799 | 2683038.2085 | 1264280.3357
42 | 2683038.2085 | 1264280.3357 | 2683054.5954 | 1264279.0722
43 | 2683035.5871 | 1264249.7971 | 2683053.9879 | 1264248.5552
44 | 2683035.5871 | 1264249.7971 | 2683035.2478 | 1264246.0672
45 | 2682988.4145 | 1264230.9424 | 2683006.9703 | 1264229.6707
46 | 2683033.7943 | 1264227.8325 | 2683006.9703 | 1264229.6707
47 | 2683035.2478 | 1264246.0672 | 2683026.5057 | 1264246.9452 | 2683017.6122 | 1264251.222
48 | 2683035.2478 | 1264246.0672 | 2683034.2217 | 1264234.9329 | 2683033.7943 | 1264227.8325 | 2683033.7943 | 1264227.8325
49 | 2683040.2886 | 1264313.4799 | 2683041.2727 | 1264329.206 | 2683045.1819 | 1264327.593
50 | 2683040.2886 | 1264313.4799 | 2683033.6548 | 1264316.5558 | 2683026.2546 | 1264319.9897
51 | 2683039.6783 | 1264345.6521 | 2683049.687 | 1264340.3885 | 2683046.051 | 1264330.0627 | 2683045.1819 | 1264327.593
52 | 2683045.1819 | 1264327.593 | 2683046.051 | 1264330.0627 | 2683017.4799 | 1264343.6166
53 | 2683045.1819 | 1264327.593 | 2683064.5163 | 1264318.4905
54 | 2682893.2097 | 1264352.7028 | 2682902.48 | 1264374.1952
55 | 2682893.2097 | 1264352.7028 | 2682923.741 | 1264337.9193
56 | 2682909.1195 | 1264389.5882 | 2682902.48 | 1264374.1952
57 | 2682923.741 | 1264337.9193 | 2682930.4236 | 1264333.5095 | 2682930.1302 | 1264315.5451
58 | 2682930.1302 | 1264315.5451 | 2682929.8605 | 1264299.0301 | 2682929.8188 | 1264297.427
59 | 2682909.1195 | 1264389.5882 | 2682920.7797 | 1264384.1696
60 | 2683039.6783 | 1264345.6521 | 2683045.7768 | 1264359.2262 | 2683051.4537 | 1264357.2377 | 2683061.7468 | 1264367.646 | 2683066.9983 | 1264365.9184 | 2683070.8591 | 1264374.8348
61 | 2683017.4799 | 1264343.6166 | 2683026.0609 | 1264363.5481
62 | 2683073.8503 | 1264314.0961 | 2683064.5163 | 1264318.4905
63 | 2682986.3547 | 1264358.3025 | 2682996.8749 | 1264381.2697
64 | 2682961.59 | 1264365.2382 | 2682961.6044 | 1264365.2317
65 | 2683073.8503 | 1264314.0961 | 2683074.7828 | 1264316.3443
66 | 2683074.7828 | 1264316.3443 | 2683092.4403 | 1264307.964
67 | 2683074.7828 | 1264316.3443 | 2683085.6383 | 1264342.4618
68 | 2683073.8503 | 1264314.0961 | 2683093.6358 | 1264304.376
69 | 2683124.5724 | 1264292.7139 | 2683092.4403 | 1264307.964
70 | 2683085.6383 | 1264342.4618 | 2683084.2452 | 1264342.976
71 | 2683071.959 | 1264377.3749 | 2683070.8591 | 1264374.8348
72 | 2683004.9022 | 1264398.7946 | 2682996.8749 | 1264381.2697
73 | 2682961.59 | 1264365.2382 | 2682942.0712 | 1264374.2928
74 | 2683004.9022 | 1264398.7946 | 2683019.1561 | 1264390.155
75 | 2682934.1053 | 1264408.7425 | 2682947.2527 | 1264406.3027
76 | 2682939.3827 | 1264431.4566 | 2682938.1218 | 1264428.9925 | 2682939.8621 | 1264418.2307 | 2682934.1053 | 1264408.7425
77 | 2682920.7797 | 1264384.1696 | 2682923.0273 | 1264388.7826 | 2682928.9375 | 1264400.2189 | 2682934.1053 | 1264408.7425
78 | 2682920.7797 | 1264384.1696 | 2682942.0712 | 1264374.2928
79 | 2682939.3827 | 1264431.4566 | 2682937.3541 | 1264431.6394 | 2682925.6255 | 1264429.5955
80 | 2682939.3827 | 1264431.4566 | 2682954.1881 | 1264434.3109 | 2682956.2008 | 1264435.7959 | 2682958.0384 | 1264440.1028 | 2682959.867 | 1264441.2961 | 2682980.7505 | 1264445.1212
81 | 2683071.959 | 1264377.3749 | 2683077.6522 | 1264389.2308 | 2683075.1466 | 1264390.1186
82 | 2683093.6358 | 1264304.376 | 2683112.7948 | 1264294.9636
83 | 2683082.8862 | 1264404.8166 | 2683075.1466 | 1264390.1186
84 | 2683125.8214 | 1264387.9956 | 2683113.5707 | 1264387.7232 | 2683103.9996 | 1264392.9373 | 2683087.5331 | 1264402.1576 | 2683082.8862 | 1264404.8166
85 | 2683125.8214 | 1264387.9956 | 2683132.6822 | 1264378.4179 | 2683138.7839 | 1264375.6793 | 2683145.6765 | 1264374.0193 | 2683156.1685 | 1264370.8362
86 | 2683125.8214 | 1264387.9956 | 2683132.8194 | 1264388.4722 | 2683148.2212 | 1264405.68 | 2683157.578 | 1264431.646
87 | 2683102.9558 | 1264240.0691 | 2683111.8029 | 1264239.2261 | 2683133.4406 | 1264237.2398 | 2683153.2053 | 1264269.3317 | 2683172.1122 | 1264260.6797 | 2683174.1251 | 1264264.8335
88 | 2683174.1251 | 1264264.8335 | 2683112.7948 | 1264294.9636
89 | 2683097.1998 | 1264242.846 | 2683102.9558 | 1264240.0691
90 | 2683160.2831 | 1264369.5879 | 2683156.1685 | 1264370.8362
91 | 2683238.7733 | 1264429.0244 | 2683228.6809 | 1264398.1174
92 | 2683249.9341 | 1264463.2036 | 2683249.6723 | 1264462.4019
93 | 2683249.6723 | 1264462.4019 | 2683238.7733 | 1264429.0244
94 | 2683170.4021 | 1264464.745 | 2683167.8787 | 1264458.2799
95 | 2683160.8112 | 1264440.173 | 2683167.8787 | 1264458.2799
96 | 2683160.8112 | 1264440.173 | 2683131.4905 | 1264440.2809
97 | 2683160.8112 | 1264440.173 | 2683158.761 | 1264434.929 | 2683157.578 | 1264431.646

## bus_geodata
| x | y | coords
0 | 2683155.2801 | 1264553.8291
1 | 2683148.578 | 1264605.6646
2 | 2683113.5124 | 1264512.8875
3 | 2683106.2155 | 1264505.2901
4 | 2683066.7679 | 1264520.003
5 | 2683126.0691 | 1264496.8989
6 | 2683071.4854 | 1264485.5311
7 | 2683074.3078 | 1264453.6853
8 | 2683058.5743 | 1264493.6783
9 | 2683265.1309 | 1264517.4796
10 | 2683245.9105 | 1264517.42
11 | 2683269.6253 | 1264495.1808
12 | 2683261.2619 | 1264500.3958
13 | 2683225.7696 | 1264516.7745
14 | 2683285.4512 | 1264477.4488
15 | 2683255.6658 | 1264454.3655
16 | 2683055.6649 | 1264420.4132
17 | 2683161.5645 | 1264514.6582
18 | 2683194.8614 | 1264515.784
19 | 2683210.2228 | 1264341.5905
20 | 2683193.3832 | 1264350.1651
21 | 2683221.2651 | 1264375.4068
22 | 2683251.9572 | 1264426.6337
23 | 2683240.6519 | 1264406.7642
24 | 2683254.7679 | 1264436.7034
25 | 2683255.7157 | 1264481.2319
26 | 2683299.004 | 1264449.0965
27 | 2682985.1227 | 1264295.4826
28 | 2683003.1518 | 1264287.4714
29 | 2683019.3755 | 1264280.2616
30 | 2682984.782 | 1264333.6066
31 | 2682988.1357 | 1264337.6779
32 | 2683037.8696 | 1264274.9712
33 | 2682971.522 | 1264254.4572
34 | 2682980.0006 | 1264231.5137
35 | 2682984.6957 | 1264354.6874
36 | 2683004.0856 | 1264330.2767
37 | 2683038.2085 | 1264280.3357
38 | 2683035.5871 | 1264249.7971
39 | 2682988.4145 | 1264230.9424
40 | 2683006.9703 | 1264229.6707
41 | 2683017.6122 | 1264251.222
42 | 2683035.2478 | 1264246.0672
43 | 2683033.7943 | 1264227.8325
44 | 2683053.9879 | 1264248.5552
45 | 2683040.2886 | 1264313.4799
46 | 2683054.5954 | 1264279.0722
47 | 2683045.1819 | 1264327.593
48 | 2683026.2546 | 1264319.9897
49 | 2682893.2097 | 1264352.7028
50 | 2682902.48 | 1264374.1952
51 | 2682923.741 | 1264337.9193
52 | 2682929.8188 | 1264297.427
53 | 2682930.1302 | 1264315.5451
54 | 2682909.1195 | 1264389.5882
55 | 2683039.6783 | 1264345.6521
56 | 2683017.4799 | 1264343.6166
57 | 2683064.5163 | 1264318.4905
58 | 2682986.3547 | 1264358.3025
59 | 2682961.6044 | 1264365.2317
60 | 2683026.0609 | 1264363.5481
61 | 2683074.7828 | 1264316.3443
62 | 2683073.8503 | 1264314.0961
63 | 2683092.4403 | 1264307.964
64 | 2683085.6383 | 1264342.4618
65 | 2683070.8591 | 1264374.8348
66 | 2682996.8749 | 1264381.2697
67 | 2682961.59 | 1264365.2382
68 | 2683019.1561 | 1264390.155
69 | 2683004.9022 | 1264398.7946
70 | 2682947.2527 | 1264406.3027
71 | 2682934.1053 | 1264408.7425
72 | 2682920.7797 | 1264384.1696
73 | 2682942.0712 | 1264374.2928
74 | 2682939.3827 | 1264431.4566
75 | 2683071.959 | 1264377.3749
76 | 2683093.6358 | 1264304.376
77 | 2683124.5724 | 1264292.7139
78 | 2683084.2452 | 1264342.976
79 | 2682925.6255 | 1264429.5955
80 | 2682980.7505 | 1264445.1212
81 | 2683082.8862 | 1264404.8166
82 | 2683075.1466 | 1264390.1186
83 | 2683125.8214 | 1264387.9956
84 | 2683174.1251 | 1264264.8335
85 | 2683102.9558 | 1264240.0691
86 | 2683112.7948 | 1264294.9636
87 | 2683160.2831 | 1264369.5879
88 | 2683228.681 | 1264398.1174
89 | 2683097.1998 | 1264242.846
90 | 2683249.9341 | 1264463.2036
91 | 2683249.6723 | 1264462.4019
92 | 2683238.7733 | 1264429.0244
93 | 2683170.4021 | 1264464.745
94 | 2683167.8787 | 1264458.2799
95 | 2683160.8112 | 1264440.173
96 | 2683131.4905 | 1264440.2809
97 | 2683157.578 | 1264431.646
98 | 2683156.1685 | 1264370.8362
99 | 2683071.959 | 1264377.3749

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1