## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_54-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_54-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_54-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_54-2_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_54-2_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_54-2_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_54-2_0_4_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_54-2_0_4_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_54-2_0_4_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_54-2_0_4_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_54-2_0_4_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_54-2_0_4_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_54-2_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_54-2_0_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_54-2_0_4_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_54-2_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_54-2_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_54-2_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_54-2_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_54-2_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_54-2_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_54-2_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_54-2_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_54-2_0_4_node_78 | 0.4 | n |  | TRUE
24 | bus_LV_54-2_0_4_node_77 | 0.4 | n |  | TRUE
25 | bus_LV_54-2_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_54-2_0_4_node_75 | 0.4 | n |  | TRUE
27 | bus_LV_54-2_0_4_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_54-2_0_4_node_72 | 0.4 | n |  | TRUE
29 | bus_LV_54-2_0_4_node_74 | 0.4 | n |  | TRUE
30 | bus_LV_54-2_0_4_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_54-2_0_4_node_52 | 0.4 | n |  | TRUE
32 | bus_LV_54-2_0_4_node_58 | 0.4 | n |  | TRUE
33 | bus_LV_54-2_0_4_node_59 | 0.4 | n |  | TRUE
34 | bus_LV_54-2_0_4_node_67 | 0.4 | n |  | TRUE
35 | bus_LV_54-2_0_4_node_64 | 0.4 | n |  | TRUE
36 | bus_LV_54-2_0_4_node_82 | 0.4 | n |  | TRUE
37 | bus_LV_54-2_0_4_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_54-2_0_4_node_51 | 0.4 | n |  | TRUE
39 | bus_LV_54-2_0_4_node_60 | 0.4 | n |  | TRUE
40 | bus_LV_54-2_0_4_node_65 | 0.4 | n |  | TRUE
41 | bus_LV_54-2_0_4_node_63 | 0.4 | n |  | TRUE
42 | bus_LV_54-2_0_4_node_53 | 0.4 | n |  | TRUE
43 | bus_LV_54-2_0_4_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_54-2_0_4_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_54-2_0_4_node_76 | 0.4 | n |  | TRUE
46 | bus_LV_54-2_0_4_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_54-2_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_54-2_0_4_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_54-2_0_4_node_79 | 0.4 | n |  | TRUE
50 | bus_LV_54-2_0_4_node_80 | 0.4 | n |  | TRUE
51 | bus_LV_54-2_0_4_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_54-2_0_4_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_54-2_0_4_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_54-2_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_54-2_0_4_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_54-2_0_4_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_54-2_0_4_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_54-2_0_4_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_54-2_0_4_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_54-2_0_4_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_54-2_0_4_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_54-2_0_4_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_54-2_0_4_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_54-2_0_4_node_44 | 0.4 | n |  | TRUE
65 | bus_LV_54-2_0_4_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_54-2_0_4_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_54-2_0_4_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_54-2_0_4_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_54-2_0_4_node_50 | 0.4 | n |  | TRUE
70 | bus_LV_54-2_0_4_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_54-2_0_4_node_81 | 0.4 | n |  | TRUE
72 | bus_LV_54-2_0_4_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_54-2_0_4_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_54-2_0_4_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_54-2_0_4_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_54-2_0_4_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_54-2_0_4_node_70 | 0.4 | n |  | TRUE
78 | bus_MV_504_0_node_39 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_54-2_0_4_load_0 | 0 | 0.029526 | 0.0074 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_54-2_0_4_load_20 | 7 | 0.029608 | 0.0074203 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_54-2_0_4_load_21 | 8 | 0.003888 | 0.00097442 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_54-2_0_4_load_31 | 9 | 0.029226 | 0.0073249 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_54-2_0_4_load_34 | 11 | 0.0078755 | 0.0019738 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_54-2_0_4_load_18 | 12 | 0.0088967 | 0.0022297 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_54-2_0_4_load_17 | 13 | 0.0016555 | 0.00041491 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_54-2_0_4_load_26 | 14 | 0.013295 | 0.003332 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_54-2_0_4_load_6 | 15 | 0.0016387 | 0.00041071 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_54-2_0_4_load_9 | 18 | 0.003973 | 0.00099572 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_54-2_0_4_load_23 | 22 | 0.0031157 | 0.00078086 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_54-2_0_4_load_77 | 24 | 0.013267 | 0.003325 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_54-2_0_4_load_75 | 26 | 0.0098822 | 0.0024767 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_54-2_0_4_load_74 | 29 | 0.0062401 | 0.0015639 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_54-2_0_4_load_52 | 31 | 0.0059362 | 0.0014878 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_54-2_0_4_load_58 | 32 | 0.004956 | 0.0012421 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_54-2_0_4_load_59 | 33 | 0.0049763 | 0.0012472 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_54-2_0_4_load_67 | 34 | 0.0052522 | 0.0013163 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_54-2_0_4_load_64 | 35 | 0.0018866 | 0.00047282 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_54-2_0_4_load_82 | 36 | 0.011632 | 0.0029152 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_54-2_0_4_load_60 | 39 | 0.0051697 | 0.0012956 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_54-2_0_4_load_65 | 40 | 0.0015379 | 0.00038544 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_54-2_0_4_load_63 | 41 | 0.0051983 | 0.0013028 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_54-2_0_4_load_19 | 43 | 0.0098677 | 0.0024731 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_54-2_0_4_load_32 | 44 | 0.0036826 | 0.00092294 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_54-2_0_4_load_76 | 45 | 0.0039736 | 0.00099588 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_54-2_0_4_load_29 | 47 | 0.013077 | 0.0032775 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_54-2_0_4_load_30 | 48 | 0.069716 | 0.017472 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_54-2_0_4_load_79 | 49 | 0.0026046 | 0.00065276 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_54-2_0_4_load_80 | 50 | 0.00012642 | 3.1684e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_54-2_0_4_load_33 | 51 | 0.0079856 | 0.0020014 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_54-2_0_4_load_35 | 52 | 0.0042352 | 0.0010614 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_54-2_0_4_load_47 | 53 | 0.009115 | 0.0022844 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_54-2_0_4_load_36 | 55 | 0.00064542 | 0.00016176 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_54-2_0_4_load_40 | 57 | 0.0084142 | 0.0021088 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_54-2_0_4_load_41 | 58 | 0.013696 | 0.0034325 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_54-2_0_4_load_39 | 59 | 0.00034648 | 8.6837e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_54-2_0_4_load_46 | 62 | 0.0012278 | 0.00030772 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_54-2_0_4_load_44 | 64 | 0.004729 | 0.0011852 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_54-2_0_4_load_57 | 65 | 0.0046273 | 0.0011597 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_54-2_0_4_load_56 | 66 | 0.0047025 | 0.0011786 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_54-2_0_4_load_50 | 69 | 0.0093108 | 0.0023335 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_54-2_0_4_load_81 | 71 | 0.069186 | 0.01734 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_54-2_0_4_load_61 | 72 | 0.0012354 | 0.00030961 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_54-2_0_4_load_68 | 73 | 0.0025623 | 0.00064218 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_54-2_0_4_load_69 | 74 | 0.0017786 | 0.00044576 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_54-2_0_4_load_66 | 75 | 0.0009916 | 0.00024852 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_54-2_0_4_load_71 | 76 | 0.0017718 | 0.00044406 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_54-2_0_4_load_70 | 77 | 0.0012361 | 0.00030981 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_54-2_0_4_line_0 |  | 0 | 1 | 0.031252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_54-2_0_4_line_1 |  | 0 | 2 | 0.029154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_54-2_0_4_line_2 |  | 1 | 3 | 0.00611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_54-2_0_4_line_3 |  | 2 | 4 | 0.015265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_54-2_0_4_line_4 |  | 3 | 6 | 0.013334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_54-2_0_4_line_5 |  | 3 | 9 | 0.02146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_54-2_0_4_line_6 |  | 4 | 10 | 0.018486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_54-2_0_4_line_7 |  | 5 | 6 | 0.00623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_54-2_0_4_line_8 |  | 5 | 7 | 0.04331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_54-2_0_4_line_9 |  | 5 | 8 | 0.019901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_54-2_0_4_line_10 |  | 6 | 11 | 0.052661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_54-2_0_4_line_11 |  | 7 | 12 | 0.0086028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_54-2_0_4_line_12 |  | 8 | 13 | 0.023964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_54-2_0_4_line_13 |  | 10 | 14 | 0.023725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_54-2_0_4_line_14 |  | 11 | 44 | 0.0011049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_54-2_0_4_line_15 |  | 12 | 43 | 0.0033719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_54-2_0_4_line_16 |  | 13 | 17 | 0.021152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_54-2_0_4_line_17 |  | 14 | 46 | 0.0014342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_54-2_0_4_line_18 |  | 15 | 16 | 0.027758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_54-2_0_4_line_19 |  | 15 | 17 | 0.0026808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_54-2_0_4_line_20 |  | 16 | 18 | 0.014616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_54-2_0_4_line_21 |  | 16 | 19 | 0.023918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_54-2_0_4_line_22 |  | 16 | 20 | 0.043078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_54-2_0_4_line_23 |  | 17 | 21 | 0.005892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_54-2_0_4_line_24 |  | 18 | 22 | 0.017614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_54-2_0_4_line_25 |  | 19 | 23 | 0.023993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_54-2_0_4_line_26 |  | 19 | 24 | 0.02124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_54-2_0_4_line_27 |  | 20 | 34 | 0.034568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_54-2_0_4_line_28 |  | 20 | 35 | 0.017721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_54-2_0_4_line_29 |  | 21 | 33 | 0.023289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_54-2_0_4_line_30 |  | 21 | 32 | 0.027941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_54-2_0_4_line_31 |  | 23 | 36 | 0.005369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_54-2_0_4_line_32 |  | 23 | 37 | 0.031828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_54-2_0_4_line_33 |  | 24 | 25 | 0.018342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_54-2_0_4_line_34 |  | 25 | 26 | 0.022258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_54-2_0_4_line_35 |  | 27 | 28 | 0.005513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_54-2_0_4_line_36 |  | 27 | 29 | 0.020471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_54-2_0_4_line_37 |  | 28 | 34 | 0.042676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_54-2_0_4_line_38 |  | 30 | 31 | 0.04621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_54-2_0_4_line_39 |  | 30 | 32 | 0.0071195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_54-2_0_4_line_40 |  | 31 | 38 | 0.032213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_54-2_0_4_line_41 |  | 33 | 39 | 0.017838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_54-2_0_4_line_42 |  | 35 | 40 | 0.02263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_54-2_0_4_line_43 |  | 37 | 45 | 0.021158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_54-2_0_4_line_44 |  | 38 | 42 | 0.005938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_54-2_0_4_line_45 |  | 38 | 69 | 0.0085414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_54-2_0_4_line_46 |  | 40 | 75 | 0.026087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_54-2_0_4_line_47 |  | 41 | 42 | 0.0080911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_54-2_0_4_line_48 |  | 42 | 72 | 0.029874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_54-2_0_4_line_49 |  | 44 | 51 | 0.018555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_54-2_0_4_line_50 |  | 46 | 47 | 0.012786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_54-2_0_4_line_51 |  | 46 | 48 | 0.032054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_54-2_0_4_line_52 |  | 48 | 49 | 0.025246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_54-2_0_4_line_53 |  | 49 | 50 | 0.047751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_54-2_0_4_line_54 |  | 50 | 62 | 0.0046085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_54-2_0_4_line_55 |  | 51 | 52 | 0.011464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_54-2_0_4_line_56 |  | 52 | 53 | 0.0071788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_54-2_0_4_line_57 |  | 53 | 54 | 0.016807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_54-2_0_4_line_58 |  | 54 | 64 | 0.030638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_54-2_0_4_line_59 |  | 55 | 56 | 0.01652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_54-2_0_4_line_60 |  | 56 | 57 | 0.023829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_54-2_0_4_line_61 |  | 56 | 58 | 0.049795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_54-2_0_4_line_62 |  | 57 | 61 | 0.029511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_54-2_0_4_line_63 |  | 59 | 60 | 0.023929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_54-2_0_4_line_64 |  | 60 | 62 | 0.03075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_54-2_0_4_line_65 |  | 61 | 63 | 0.018367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_54-2_0_4_line_66 |  | 61 | 64 | 0.019489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_54-2_0_4_line_67 |  | 63 | 65 | 0.021736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_54-2_0_4_line_68 |  | 63 | 66 | 0.020878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_54-2_0_4_line_69 |  | 67 | 68 | 0.073571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_54-2_0_4_line_70 |  | 67 | 69 | 0.029443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_54-2_0_4_line_71 |  | 68 | 70 | 0.069314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_54-2_0_4_line_72 |  | 70 | 71 | 0.02824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_54-2_0_4_line_73 |  | 73 | 74 | 0.025716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_54-2_0_4_line_74 |  | 74 | 77 | 0.011484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_54-2_0_4_line_75 |  | 75 | 76 | 0.0042904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_54-2_0_4_line_76 |  | 76 | 77 | 0.00089099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_54-2_0_4_trafo_34 | 0.63 MVA 20/0.4 kV | 78 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2689143.5375 | 1253545.9306 | 2689145.1108 | 1253551.692 | 2689169.4074 | 1253544.7095
1 | 2689197.4275 | 1253536.6568 | 2689169.4074 | 1253544.7095
2 | 2689141.9284 | 1253540.0352 | 2689143.5375 | 1253545.9306
3 | 2689193.4843 | 1253521.9083 | 2689197.4275 | 1253536.6568
4 | 2689129.5159 | 1253544.9967 | 2689141.9284 | 1253540.0352
5 | 2689141.9284 | 1253540.0352 | 2689161.8587 | 1253532.0786
6 | 2689211.9122 | 1253519.8731 | 2689193.4843 | 1253521.9083
7 | 2689129.5159 | 1253544.9967 | 2689131.1307 | 1253551.0145
8 | 2689131.1307 | 1253551.0145 | 2689143.7309 | 1253592.4515
9 | 2689131.1307 | 1253551.0145 | 2689112.8198 | 1253558.8087
10 | 2689129.5159 | 1253544.9967 | 2689119.3404 | 1253493.3284
11 | 2689143.7309 | 1253592.4515 | 2689146.2337 | 1253600.6823
12 | 2689112.8198 | 1253558.8087 | 2689090.7701 | 1253568.1944
13 | 2689211.9122 | 1253519.8731 | 2689215.7022 | 1253496.4526
14 | 2689119.1269 | 1253492.2443 | 2689119.3404 | 1253493.3284
15 | 2689146.2337 | 1253600.6823 | 2689147.2147 | 1253603.9084
16 | 2689071.3077 | 1253576.4788 | 2689090.7701 | 1253568.1944
17 | 2689215.9313 | 1253495.0368 | 2689215.7022 | 1253496.4526
18 | 2689055.0253 | 1253597.9282 | 2689060.6022 | 1253595.8883 | 2689059.8555 | 1253589.8502 | 2689063.7441 | 1253581.1575 | 2689069.0278 | 1253577.8891
19 | 2689071.3077 | 1253576.4788 | 2689069.0278 | 1253577.8891
20 | 2689055.0253 | 1253597.9282 | 2689057.6671 | 1253606.4078 | 2689059.3337 | 1253611.895
21 | 2689054.7229 | 1253617.5276 | 2689049.8049 | 1253599.8401 | 2689055.0253 | 1253597.9282
22 | 2689019.8758 | 1253590.4275 | 2689030.5448 | 1253587.986 | 2689032.0473 | 1253592.4453 | 2689039.7773 | 1253591.2495 | 2689045.4855 | 1253593.0255 | 2689049.8049 | 1253599.8401 | 2689055.0253 | 1253597.9282
23 | 2689069.1415 | 1253570.9975 | 2689071.3077 | 1253576.4788
24 | 2689064.4529 | 1253628.7491 | 2689060.8665 | 1253616.9417 | 2689059.3337 | 1253611.895
25 | 2689054.7229 | 1253617.5276 | 2689061.0528 | 1253640.6739
26 | 2689054.7229 | 1253617.5276 | 2689034.0744 | 1253622.5036
27 | 2689019.8758 | 1253590.4275 | 2689009.1142 | 1253594.5134 | 2688987.5595 | 1253602.7001
28 | 2689019.8758 | 1253590.4275 | 2689006.7898 | 1253578.4786
29 | 2689069.1415 | 1253570.9975 | 2689090.5315 | 1253561.7857
30 | 2689069.1415 | 1253570.9975 | 2689067.1057 | 1253565.8741 | 2689062.5099 | 1253566.3943 | 2689057.2676 | 1253565.2479 | 2689052.7924 | 1253562.2673 | 2689049.8934 | 1253555.8299
31 | 2689055.8195 | 1253641.9406 | 2689061.0528 | 1253640.6739
32 | 2689061.0528 | 1253640.6739 | 2689062.749 | 1253640.2769 | 2689071.1353 | 1253669.1807
33 | 2689016.2426 | 1253626.8009 | 2689034.0744 | 1253622.5036
34 | 2689016.2426 | 1253626.8009 | 2689017.3659 | 1253631.8883 | 2689016.1945 | 1253635.0176 | 2689003.0091 | 1253638.7604
35 | 2688947.664 | 1253617.8528 | 2688949.5633 | 1253623.0298
36 | 2688949.5633 | 1253623.0298 | 2688956.6009 | 1253642.2535
37 | 2688947.664 | 1253617.8528 | 2688987.5595 | 1253602.7001
38 | 2689043.057 | 1253557.8175 | 2689041.6903 | 1253552.8598 | 2689036.322 | 1253532.9972 | 2689031.8764 | 1253512.9929
39 | 2689043.057 | 1253557.8175 | 2689049.8934 | 1253555.8299
40 | 2689023.0455 | 1253482.0142 | 2689031.8764 | 1253512.9929
41 | 2689106.9147 | 1253554.7301 | 2689090.5315 | 1253561.7857
42 | 2689006.7898 | 1253578.4786 | 2688997.4031 | 1253569.9075 | 2688990.5844 | 1253562.7037
43 | 2689071.1353 | 1253669.1807 | 2689050.6183 | 1253674.3483
44 | 2689017.1957 | 1253483.1271 | 2689023.0455 | 1253482.0142
45 | 2689023.0455 | 1253482.0142 | 2689020.9989 | 1253473.7216
46 | 2688990.5844 | 1253562.7037 | 2688986.9073 | 1253558.8191 | 2688979.4836 | 1253546.1645 | 2688978.1982 | 1253540.2355
47 | 2689017.1957 | 1253483.1271 | 2689018.4195 | 1253489.5615 | 2689018.8384 | 1253491.0448
48 | 2689017.1957 | 1253483.1271 | 2689015.0021 | 1253471.4296 | 2689010.6796 | 1253453.985
49 | 2689119.1269 | 1253492.2443 | 2689119.1269 | 1253492.2443 | 2689114.1743 | 1253474.3622
50 | 2689215.9313 | 1253495.0368 | 2689217.744 | 1253495.4311 | 2689226.6037 | 1253497.3882 | 2689228.4173 | 1253497.7888
51 | 2689215.9313 | 1253495.0368 | 2689220.1425 | 1253468.9691 | 2689221.1296 | 1253463.4079
52 | 2689225.5419 | 1253438.5508 | 2689221.1296 | 1253463.4079
53 | 2689225.5419 | 1253438.5508 | 2689227.2508 | 1253428.9232 | 2689241.6366 | 1253404.7101 | 2689246.5727 | 1253396.2336
54 | 2689246.5727 | 1253396.2336 | 2689248.8917 | 1253392.2512
55 | 2689114.1743 | 1253474.3622 | 2689111.1146 | 1253463.3145
56 | 2689109.1985 | 1253456.3961 | 2689111.1146 | 1253463.3145
57 | 2689104.7125 | 1253440.1987 | 2689109.1985 | 1253456.3961
58 | 2689104.7125 | 1253440.1987 | 2689134.9282 | 1253435.1271
59 | 2689174.9488 | 1253378.7972 | 2689179.5636 | 1253362.9347
60 | 2689174.9488 | 1253378.7972 | 2689167.6668 | 1253401.486
61 | 2689174.9488 | 1253378.7972 | 2689150.221 | 1253371.197 | 2689126.8757 | 1253376.4325
62 | 2689152.3333 | 1253426.36 | 2689165.3841 | 1253408.5984 | 2689167.6668 | 1253401.486
63 | 2689264.3657 | 1253365.6782 | 2689241.4752 | 1253358.707
64 | 2689264.3657 | 1253365.6782 | 2689248.8917 | 1253392.2512
65 | 2689168.9591 | 1253434.2719 | 2689152.3333 | 1253426.36
66 | 2689152.3333 | 1253426.36 | 2689134.9282 | 1253435.1271
67 | 2689190.3577 | 1253438.4305 | 2689168.9591 | 1253434.2719
68 | 2689168.9591 | 1253434.2719 | 2689171.7941 | 1253454.9561
69 | 2688994.4503 | 1253379.8172 | 2688999.6841 | 1253378.5282 | 2689007.2289 | 1253406.2295 | 2689010.7732 | 1253422.4507 | 2689015.1748 | 1253444.8896
70 | 2689015.1748 | 1253444.8896 | 2689017.3767 | 1253459.0447 | 2689020.9989 | 1253473.7216
71 | 2689022.2969 | 1253367.7041 | 2689019.4954 | 1253352.2724 | 2688994.2028 | 1253356.6291 | 2688999.6841 | 1253378.5282 | 2688994.4503 | 1253379.8172
72 | 2689022.2969 | 1253367.7041 | 2689014.6981 | 1253369.191 | 2689018.9565 | 1253389.2411
73 | 2688969.2186 | 1253498.8162 | 2688974.6673 | 1253523.9487
74 | 2688974.6673 | 1253523.9487 | 2688977.1004 | 1253535.1718
75 | 2688977.2892 | 1253536.0425 | 2688978.1982 | 1253540.2355
76 | 2688977.1004 | 1253535.1718 | 2688977.2892 | 1253536.0425

## bus_geodata
| x | y | coords
0 | 2689169.4074 | 1253544.7095
1 | 2689143.5375 | 1253545.9306
2 | 2689197.4275 | 1253536.6568
3 | 2689141.9284 | 1253540.0352
4 | 2689193.4843 | 1253521.9083
5 | 2689131.1307 | 1253551.0145
6 | 2689129.5159 | 1253544.9967
7 | 2689143.7309 | 1253592.4515
8 | 2689112.8198 | 1253558.8087
9 | 2689161.8587 | 1253532.0786
10 | 2689211.9122 | 1253519.8731
11 | 2689119.3404 | 1253493.3284
12 | 2689146.2337 | 1253600.6823
13 | 2689090.7701 | 1253568.1944
14 | 2689215.7022 | 1253496.4526
15 | 2689069.0278 | 1253577.8891
16 | 2689055.0253 | 1253597.9282
17 | 2689071.3077 | 1253576.4788
18 | 2689059.3337 | 1253611.895
19 | 2689054.7229 | 1253617.5276
20 | 2689019.8758 | 1253590.4275
21 | 2689069.1415 | 1253570.9975
22 | 2689064.4529 | 1253628.7491
23 | 2689061.0528 | 1253640.6739
24 | 2689034.0744 | 1253622.5036
25 | 2689016.2426 | 1253626.8009
26 | 2689003.0091 | 1253638.7604
27 | 2688949.5633 | 1253623.0298
28 | 2688947.664 | 1253617.8528
29 | 2688956.6009 | 1253642.2535
30 | 2689043.057 | 1253557.8175
31 | 2689031.8764 | 1253512.9929
32 | 2689049.8934 | 1253555.8299
33 | 2689090.5315 | 1253561.7857
34 | 2688987.5595 | 1253602.7001
35 | 2689006.7898 | 1253578.4786
36 | 2689055.8195 | 1253641.9406
37 | 2689071.1353 | 1253669.1807
38 | 2689023.0455 | 1253482.0142
39 | 2689106.9147 | 1253554.7301
40 | 2688990.5844 | 1253562.7037
41 | 2689018.8384 | 1253491.0448
42 | 2689017.1957 | 1253483.1271
43 | 2689147.2147 | 1253603.9084
44 | 2689119.1269 | 1253492.2443
45 | 2689050.6183 | 1253674.3483
46 | 2689215.9313 | 1253495.0368
47 | 2689228.4173 | 1253497.7888
48 | 2689221.1296 | 1253463.4079
49 | 2689225.5419 | 1253438.5508
50 | 2689246.5727 | 1253396.2336
51 | 2689114.1743 | 1253474.3622
52 | 2689111.1146 | 1253463.3145
53 | 2689109.1985 | 1253456.3961
54 | 2689104.7125 | 1253440.1987
55 | 2689179.5636 | 1253362.9347
56 | 2689174.9488 | 1253378.7972
57 | 2689167.6668 | 1253401.486
58 | 2689126.8757 | 1253376.4325
59 | 2689241.4752 | 1253358.707
60 | 2689264.3657 | 1253365.6782
61 | 2689152.3333 | 1253426.36
62 | 2689248.8917 | 1253392.2512
63 | 2689168.9591 | 1253434.2719
64 | 2689134.9282 | 1253435.1271
65 | 2689190.3577 | 1253438.4305
66 | 2689171.7941 | 1253454.9561
67 | 2689015.1748 | 1253444.8896
68 | 2688994.4503 | 1253379.8172
69 | 2689020.9989 | 1253473.7216
70 | 2689022.2969 | 1253367.7041
71 | 2689018.9565 | 1253389.2411
72 | 2689010.6796 | 1253453.985
73 | 2688969.2186 | 1253498.8162
74 | 2688974.6673 | 1253523.9487
75 | 2688978.1982 | 1253540.2355
76 | 2688977.2892 | 1253536.0425
77 | 2688977.1004 | 1253535.1718
78 | 2689129.5159 | 1253544.9967

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1