## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5581-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5581-7_0_3_node_84 | 0.4 | n |  | TRUE
2 | bus_LV_5581-7_0_3_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_5581-7_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_5581-7_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_5581-7_0_3_node_41 | 0.4 | n |  | TRUE
6 | bus_LV_5581-7_0_3_node_77 | 0.4 | n |  | TRUE
7 | bus_LV_5581-7_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_5581-7_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_5581-7_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_5581-7_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_5581-7_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_5581-7_0_3_node_104 | 0.4 | n |  | TRUE
13 | bus_LV_5581-7_0_3_node_103 | 0.4 | n |  | TRUE
14 | bus_LV_5581-7_0_3_node_115 | 0.4 | n |  | TRUE
15 | bus_LV_5581-7_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_5581-7_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_5581-7_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_5581-7_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_5581-7_0_3_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_5581-7_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_5581-7_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_5581-7_0_3_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_5581-7_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_5581-7_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_5581-7_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_5581-7_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_5581-7_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_5581-7_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_5581-7_0_3_node_101 | 0.4 | n |  | TRUE
30 | bus_LV_5581-7_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_5581-7_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_5581-7_0_3_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_5581-7_0_3_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_5581-7_0_3_node_212 | 0.4 | n |  | TRUE
35 | bus_LV_5581-7_0_3_node_58 | 0.4 | n |  | TRUE
36 | bus_LV_5581-7_0_3_node_211 | 0.4 | n |  | TRUE
37 | bus_LV_5581-7_0_3_node_141 | 0.4 | n |  | TRUE
38 | bus_LV_5581-7_0_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_5581-7_0_3_node_85 | 0.4 | n |  | TRUE
40 | bus_LV_5581-7_0_3_node_164 | 0.4 | n |  | TRUE
41 | bus_LV_5581-7_0_3_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_5581-7_0_3_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_5581-7_0_3_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_5581-7_0_3_node_98 | 0.4 | n |  | TRUE
45 | bus_LV_5581-7_0_3_node_56 | 0.4 | n |  | TRUE
46 | bus_LV_5581-7_0_3_node_57 | 0.4 | n |  | TRUE
47 | bus_LV_5581-7_0_3_node_59 | 0.4 | n |  | TRUE
48 | bus_LV_5581-7_0_3_node_60 | 0.4 | n |  | TRUE
49 | bus_LV_5581-7_0_3_node_162 | 0.4 | n |  | TRUE
50 | bus_LV_5581-7_0_3_node_215 | 0.4 | n |  | TRUE
51 | bus_LV_5581-7_0_3_node_70 | 0.4 | n |  | TRUE
52 | bus_LV_5581-7_0_3_node_87 | 0.4 | n |  | TRUE
53 | bus_LV_5581-7_0_3_node_72 | 0.4 | n |  | TRUE
54 | bus_LV_5581-7_0_3_node_86 | 0.4 | n |  | TRUE
55 | bus_LV_5581-7_0_3_node_74 | 0.4 | n |  | TRUE
56 | bus_LV_5581-7_0_3_node_75 | 0.4 | n |  | TRUE
57 | bus_LV_5581-7_0_3_node_76 | 0.4 | n |  | TRUE
58 | bus_LV_5581-7_0_3_node_78 | 0.4 | n |  | TRUE
59 | bus_LV_5581-7_0_3_node_79 | 0.4 | n |  | TRUE
60 | bus_LV_5581-7_0_3_node_153 | 0.4 | n |  | TRUE
61 | bus_LV_5581-7_0_3_node_216 | 0.4 | n |  | TRUE
62 | bus_LV_5581-7_0_3_node_194 | 0.4 | n |  | TRUE
63 | bus_LV_5581-7_0_3_node_200 | 0.4 | n |  | TRUE
64 | bus_LV_5581-7_0_3_node_99 | 0.4 | n |  | TRUE
65 | bus_LV_5581-7_0_3_node_100 | 0.4 | n |  | TRUE
66 | bus_LV_5581-7_0_3_node_165 | 0.4 | n |  | TRUE
67 | bus_LV_5581-7_0_3_node_102 | 0.4 | n |  | TRUE
68 | bus_LV_5581-7_0_3_node_218 | 0.4 | n |  | TRUE
69 | bus_LV_5581-7_0_3_node_217 | 0.4 | n |  | TRUE
70 | bus_LV_5581-7_0_3_node_116 | 0.4 | n |  | TRUE
71 | bus_LV_5581-7_0_3_node_144 | 0.4 | n |  | TRUE
72 | bus_LV_5581-7_0_3_node_117 | 0.4 | n |  | TRUE
73 | bus_LV_5581-7_0_3_node_118 | 0.4 | n |  | TRUE
74 | bus_LV_5581-7_0_3_node_119 | 0.4 | n |  | TRUE
75 | bus_LV_5581-7_0_3_node_120 | 0.4 | n |  | TRUE
76 | bus_LV_5581-7_0_3_node_121 | 0.4 | n |  | TRUE
77 | bus_LV_5581-7_0_3_node_122 | 0.4 | n |  | TRUE
78 | bus_LV_5581-7_0_3_node_123 | 0.4 | n |  | TRUE
79 | bus_LV_5581-7_0_3_node_142 | 0.4 | n |  | TRUE
80 | bus_LV_5581-7_0_3_node_140 | 0.4 | n |  | TRUE
81 | bus_LV_5581-7_0_3_node_184 | 0.4 | n |  | TRUE
82 | bus_LV_5581-7_0_3_node_203 | 0.4 | n |  | TRUE
83 | bus_LV_5581-7_0_3_node_143 | 0.4 | n |  | TRUE
84 | bus_LV_5581-7_0_3_node_145 | 0.4 | n |  | TRUE
85 | bus_LV_5581-7_0_3_node_210 | 0.4 | n |  | TRUE
86 | bus_LV_5581-7_0_3_node_208 | 0.4 | n |  | TRUE
87 | bus_LV_5581-7_0_3_node_150 | 0.4 | n |  | TRUE
88 | bus_LV_5581-7_0_3_node_151 | 0.4 | n |  | TRUE
89 | bus_LV_5581-7_0_3_node_152 | 0.4 | n |  | TRUE
90 | bus_LV_5581-7_0_3_node_166 | 0.4 | n |  | TRUE
91 | bus_LV_5581-7_0_3_node_161 | 0.4 | n |  | TRUE
92 | bus_LV_5581-7_0_3_node_163 | 0.4 | n |  | TRUE
93 | bus_LV_5581-7_0_3_node_190 | 0.4 | n |  | TRUE
94 | bus_LV_5581-7_0_3_node_204 | 0.4 | n |  | TRUE
95 | bus_LV_5581-7_0_3_node_202 | 0.4 | n |  | TRUE
96 | bus_LV_5581-7_0_3_node_183 | 0.4 | n |  | TRUE
97 | bus_LV_5581-7_0_3_node_185 | 0.4 | n |  | TRUE
98 | bus_LV_5581-7_0_3_node_186 | 0.4 | n |  | TRUE
99 | bus_LV_5581-7_0_3_node_196 | 0.4 | n |  | TRUE
100 | bus_LV_5581-7_0_3_node_188 | 0.4 | n |  | TRUE
101 | bus_LV_5581-7_0_3_node_209 | 0.4 | n |  | TRUE
102 | bus_LV_5581-7_0_3_node_223 | 0.4 | n |  | TRUE
103 | bus_LV_5581-7_0_3_node_221 | 0.4 | n |  | TRUE
104 | bus_LV_5581-7_0_3_node_222 | 0.4 | n |  | TRUE
105 | bus_MV_620_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5581-7_0_3_load_0 | 0 | 0.003564 | 0.00089322 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5581-7_0_3_load_84 | 1 | 0.002973 | 0.0007451 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5581-7_0_3_load_3 | 4 | 0.0028767 | 0.00072096 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5581-7_0_3_load_41 | 5 | 0.0036515 | 0.00091516 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5581-7_0_3_load_4 | 7 | 0.0024268 | 0.00060821 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5581-7_0_3_load_5 | 8 | 0.0034275 | 0.00085901 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5581-7_0_3_load_6 | 9 | 0.0046264 | 0.0011595 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5581-7_0_3_load_8 | 11 | 0.0060434 | 0.0015146 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5581-7_0_3_load_104 | 12 | 0.0028054 | 0.00070311 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5581-7_0_3_load_103 | 13 | 0.0040074 | 0.0010044 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5581-7_0_3_load_9 | 15 | 0.0036047 | 0.00090342 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5581-7_0_3_load_10 | 16 | 0.0028004 | 0.00070185 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5581-7_0_3_load_11 | 17 | 0.0021376 | 0.00053573 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5581-7_0_3_load_12 | 18 | 0.0020381 | 0.00051079 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5581-7_0_3_load_22 | 19 | 0.003441 | 0.00086241 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5581-7_0_3_load_14 | 20 | 0.0078435 | 0.0019658 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5581-7_0_3_load_15 | 21 | 0.0087102 | 0.002183 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5581-7_0_3_load_34 | 22 | 0.0031975 | 0.00080137 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5581-7_0_3_load_16 | 23 | 0.0078529 | 0.0019681 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5581-7_0_3_load_17 | 24 | 0.0023408 | 0.00058666 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5581-7_0_3_load_18 | 25 | 0.0026728 | 0.00066987 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5581-7_0_3_load_20 | 27 | 0.0038324 | 0.00096048 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5581-7_0_3_load_21 | 28 | 0.0048401 | 0.001213 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5581-7_0_3_load_23 | 30 | 0.0041852 | 0.0010489 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5581-7_0_3_load_212 | 34 | 0.0021995 | 0.00055125 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5581-7_0_3_load_211 | 36 | 0.0025502 | 0.00063914 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5581-7_0_3_load_32 | 38 | 0.0087289 | 0.0021877 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5581-7_0_3_load_85 | 39 | 0.0031912 | 0.0007998 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5581-7_0_3_load_43 | 42 | 0.0025056 | 0.00062797 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5581-7_0_3_load_44 | 43 | 0.0020501 | 0.00051381 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5581-7_0_3_load_98 | 44 | 0.0026613 | 0.000667 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5581-7_0_3_load_56 | 45 | 0.0042572 | 0.0010669 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5581-7_0_3_load_57 | 46 | 0.0033935 | 0.0008505 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5581-7_0_3_load_59 | 47 | 0.0035932 | 0.00090054 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5581-7_0_3_load_215 | 50 | 0.0021675 | 0.00054322 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5581-7_0_3_load_70 | 51 | 0.0033628 | 0.00084279 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5581-7_0_3_load_87 | 52 | 0.0040443 | 0.0010136 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5581-7_0_3_load_86 | 54 | 0.0027875 | 0.00069863 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5581-7_0_3_load_74 | 55 | 0.0019124 | 0.0004793 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5581-7_0_3_load_75 | 56 | 0.0027297 | 0.00068413 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5581-7_0_3_load_78 | 58 | 0.0034593 | 0.00086698 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5581-7_0_3_load_79 | 59 | 0.0039473 | 0.00098929 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5581-7_0_3_load_153 | 60 | 0.0023753 | 0.0005953 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5581-7_0_3_load_216 | 61 | 0.0014746 | 0.00036956 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5581-7_0_3_load_194 | 62 | 0.00097377 | 0.00024405 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5581-7_0_3_load_200 | 63 | 0.004638 | 0.0011624 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5581-7_0_3_load_165 | 66 | 0.0021163 | 0.00053041 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5581-7_0_3_load_217 | 69 | 0.0060305 | 0.0015114 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5581-7_0_3_load_116 | 70 | 0.0052385 | 0.0013129 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5581-7_0_3_load_144 | 71 | 0.0041052 | 0.0010289 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5581-7_0_3_load_117 | 72 | 0.0025296 | 0.00063398 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5581-7_0_3_load_121 | 76 | 0.0030877 | 0.00077385 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5581-7_0_3_load_122 | 77 | 0.0048439 | 0.001214 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5581-7_0_3_load_123 | 78 | 0.0019393 | 0.00048604 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5581-7_0_3_load_140 | 80 | 0.0030883 | 0.000774 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5581-7_0_3_load_184 | 81 | 0.0034923 | 0.00087526 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5581-7_0_3_load_145 | 84 | 0.0032906 | 0.0008247 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5581-7_0_3_load_210 | 85 | 0.0031337 | 0.00078537 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5581-7_0_3_load_208 | 86 | 0.0034132 | 0.00085542 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5581-7_0_3_load_150 | 87 | 0.0021404 | 0.00053643 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5581-7_0_3_load_161 | 91 | 0.0052801 | 0.0013233 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5581-7_0_3_load_163 | 92 | 0.0078192 | 0.0019597 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5581-7_0_3_load_204 | 94 | 0.0017905 | 0.00044874 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5581-7_0_3_load_202 | 95 | 0.0025659 | 0.00064306 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5581-7_0_3_load_183 | 96 | 0.0047121 | 0.001181 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5581-7_0_3_load_185 | 97 | 0.0053713 | 0.0013462 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5581-7_0_3_load_186 | 98 | 0.0015052 | 0.00037724 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5581-7_0_3_load_196 | 99 | 0.00088376 | 0.00022149 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5581-7_0_3_load_188 | 100 | 0.00055358 | 0.00013874 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5581-7_0_3_load_209 | 101 | 0.00189 | 0.00047367 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5581-7_0_3_load_223 | 102 | 0.0047299 | 0.0011854 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5581-7_0_3_load_222 | 104 | 0.0029521 | 0.00073987 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5581-7_0_3_line_0 |  | 0 | 1 | 0.030798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5581-7_0_3_line_1 |  | 1 | 6 | 0.013007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5581-7_0_3_line_2 |  | 2 | 3 | 0.002613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5581-7_0_3_line_3 |  | 2 | 4 | 0.024597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5581-7_0_3_line_4 |  | 3 | 5 | 0.014173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5581-7_0_3_line_5 |  | 4 | 6 | 0.011018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5581-7_0_3_line_6 |  | 5 | 41 | 0.03058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5581-7_0_3_line_7 |  | 6 | 56 | 0.021016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5581-7_0_3_line_8 |  | 7 | 8 | 0.03485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5581-7_0_3_line_9 |  | 7 | 9 | 0.0061034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5581-7_0_3_line_10 |  | 8 | 10 | 0.006033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5581-7_0_3_line_11 |  | 9 | 11 | 0.030021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5581-7_0_3_line_12 |  | 10 | 12 | 0.0087816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5581-7_0_3_line_13 |  | 10 | 13 | 0.049906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5581-7_0_3_line_14 |  | 11 | 14 | 0.030749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5581-7_0_3_line_15 |  | 13 | 29 | 0.013073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5581-7_0_3_line_16 |  | 14 | 70 | 0.014605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5581-7_0_3_line_17 |  | 15 | 16 | 0.023746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5581-7_0_3_line_18 |  | 15 | 17 | 0.026256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5581-7_0_3_line_19 |  | 16 | 18 | 0.031781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5581-7_0_3_line_20 |  | 18 | 19 | 0.024153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5581-7_0_3_line_21 |  | 19 | 26 | 0.011513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5581-7_0_3_line_22 |  | 20 | 21 | 0.021657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5581-7_0_3_line_23 |  | 20 | 22 | 0.027272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5581-7_0_3_line_24 |  | 21 | 23 | 0.019561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5581-7_0_3_line_25 |  | 22 | 40 | 0.037333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5581-7_0_3_line_26 |  | 24 | 25 | 0.02424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5581-7_0_3_line_27 |  | 24 | 26 | 0.026107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5581-7_0_3_line_28 |  | 25 | 27 | 0.00055762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5581-7_0_3_line_29 |  | 26 | 28 | 0.013947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5581-7_0_3_line_30 |  | 28 | 29 | 0.0065556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5581-7_0_3_line_31 |  | 29 | 67 | 0.047402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5581-7_0_3_line_32 |  | 30 | 31 | 0.024059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5581-7_0_3_line_33 |  | 31 | 32 | 0.026491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_5581-7_0_3_line_34 |  | 31 | 33 | 0.010802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_5581-7_0_3_line_35 |  | 32 | 34 | 0.017965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5581-7_0_3_line_36 |  | 32 | 35 | 0.019929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_5581-7_0_3_line_37 |  | 33 | 36 | 0.063589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5581-7_0_3_line_38 |  | 33 | 37 | 0.013269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_5581-7_0_3_line_39 |  | 35 | 48 | 0.006327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5581-7_0_3_line_40 |  | 35 | 45 | 0.045621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_5581-7_0_3_line_41 |  | 36 | 100 | 0.086532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5581-7_0_3_line_42 |  | 37 | 83 | 0.026805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5581-7_0_3_line_43 |  | 37 | 80 | 0.0056964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_5581-7_0_3_line_44 |  | 38 | 39 | 0.047267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5581-7_0_3_line_45 |  | 39 | 53 | 0.011748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5581-7_0_3_line_46 |  | 40 | 93 | 0.014354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5581-7_0_3_line_47 |  | 40 | 49 | 0.04779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5581-7_0_3_line_48 |  | 41 | 42 | 0.018633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5581-7_0_3_line_49 |  | 43 | 44 | 0.0088705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5581-7_0_3_line_50 |  | 44 | 64 | 0.01646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5581-7_0_3_line_51 |  | 45 | 46 | 0.027088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5581-7_0_3_line_52 |  | 46 | 47 | 0.0018421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5581-7_0_3_line_53 |  | 47 | 49 | 0.034853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5581-7_0_3_line_54 |  | 48 | 50 | 0.013098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5581-7_0_3_line_55 |  | 49 | 91 | 0.012442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5581-7_0_3_line_56 |  | 51 | 52 | 0.035503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5581-7_0_3_line_57 |  | 52 | 53 | 0.018035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5581-7_0_3_line_58 |  | 53 | 54 | 0.016483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5581-7_0_3_line_59 |  | 54 | 63 | 0.051263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5581-7_0_3_line_60 |  | 55 | 56 | 0.013237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5581-7_0_3_line_61 |  | 55 | 57 | 0.024597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5581-7_0_3_line_62 |  | 57 | 58 | 0.002759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5581-7_0_3_line_63 |  | 57 | 59 | 0.016505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5581-7_0_3_line_64 |  | 58 | 60 | 0.028282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5581-7_0_3_line_65 |  | 58 | 61 | 0.061949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5581-7_0_3_line_66 |  | 59 | 62 | 0.0033251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5581-7_0_3_line_67 |  | 60 | 88 | 0.016642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5581-7_0_3_line_68 |  | 63 | 93 | 0.024261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5581-7_0_3_line_69 |  | 64 | 65 | 0.049283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5581-7_0_3_line_70 |  | 65 | 66 | 0.008623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5581-7_0_3_line_71 |  | 66 | 89 | 0.013245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5581-7_0_3_line_72 |  | 67 | 68 | 0.007584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5581-7_0_3_line_73 |  | 67 | 69 | 0.020081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5581-7_0_3_line_74 |  | 68 | 102 | 0.006872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5581-7_0_3_line_75 |  | 68 | 103 | 0.02744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5581-7_0_3_line_76 |  | 70 | 71 | 0.012772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5581-7_0_3_line_77 |  | 71 | 79 | 0.040522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5581-7_0_3_line_78 |  | 72 | 73 | 0.024342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5581-7_0_3_line_79 |  | 72 | 74 | 0.020939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5581-7_0_3_line_80 |  | 73 | 75 | 0.008136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5581-7_0_3_line_81 |  | 73 | 76 | 0.028443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5581-7_0_3_line_82 |  | 74 | 77 | 0.016912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5581-7_0_3_line_83 |  | 74 | 78 | 0.023233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5581-7_0_3_line_84 |  | 75 | 79 | 0.019781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_5581-7_0_3_line_85 |  | 75 | 80 | 0.03428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_5581-7_0_3_line_86 |  | 76 | 81 | 0.0035837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_5581-7_0_3_line_87 |  | 78 | 82 | 0.049089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5581-7_0_3_line_88 |  | 79 | 84 | 0.015125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_5581-7_0_3_line_89 |  | 81 | 96 | 0.02281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5581-7_0_3_line_90 |  | 82 | 95 | 0.056049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5581-7_0_3_line_91 |  | 83 | 85 | 0.034621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5581-7_0_3_line_92 |  | 83 | 86 | 0.011475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5581-7_0_3_line_93 |  | 86 | 101 | 0.018842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5581-7_0_3_line_94 |  | 87 | 88 | 0.021666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5581-7_0_3_line_95 |  | 88 | 89 | 0.035588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5581-7_0_3_line_96 |  | 89 | 90 | 0.01891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5581-7_0_3_line_97 |  | 90 | 94 | 0.016139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5581-7_0_3_line_98 |  | 90 | 95 | 0.015636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5581-7_0_3_line_99 |  | 91 | 92 | 0.0052702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5581-7_0_3_line_100 |  | 96 | 97 | 0.01167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5581-7_0_3_line_101 |  | 98 | 99 | 0.078385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5581-7_0_3_line_102 |  | 99 | 100 | 0.0019133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5581-7_0_3_line_103 |  | 103 | 104 | 0.016834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5581-7_0_3_trafo_56 | 0.63 MVA 20/0.4 kV | 105 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2542663.5235 | 1152753.9171 | 2542657.8267 | 1152723.6504
1 | 2542663.5235 | 1152753.9171 | 2542669.1527 | 1152765.6475
2 | 2542704.4524 | 1152768.2123 | 2542704.4313 | 1152770.825
3 | 2542704.4524 | 1152768.2123 | 2542680.0405 | 1152765.1976
4 | 2542704.4313 | 1152770.825 | 2542704.3156 | 1152784.9975
5 | 2542669.1527 | 1152765.6475 | 2542675.1203 | 1152764.59 | 2542680.0405 | 1152765.1976
6 | 2542700.743 | 1152815.3618 | 2542704.3074 | 1152786.001 | 2542704.3156 | 1152784.9975
7 | 2542669.1527 | 1152765.6475 | 2542650.1465 | 1152770.5981 | 2542649.4522 | 1152771.7856
8 | 2542296.2409 | 1152821.6134 | 2542283.4429 | 1152812.8748 | 2542267.9751 | 1152801.243
9 | 2542296.2409 | 1152821.6134 | 2542301.2814 | 1152825.0551
10 | 2542263.1533 | 1152797.6171 | 2542267.9751 | 1152801.243
11 | 2542326.0746 | 1152841.984 | 2542301.2814 | 1152825.0551
12 | 2542263.1533 | 1152797.6171 | 2542259.6517 | 1152789.5638
13 | 2542263.1533 | 1152797.6171 | 2542222.7967 | 1152826.9761
14 | 2542353.8482 | 1152854.5771 | 2542335.094 | 1152848.1425 | 2542326.0746 | 1152841.984
15 | 2542222.7967 | 1152826.9761 | 2542212.7718 | 1152835.3992
16 | 2542353.8482 | 1152854.5771 | 2542367.1413 | 1152854.8609 | 2542368.4425 | 1152854.7182
17 | 2542299.3362 | 1152904.4055 | 2542278.5916 | 1152892.8499
18 | 2542299.3362 | 1152904.4055 | 2542318.4635 | 1152915.06 | 2542321.5638 | 1152918.1272
19 | 2542278.5916 | 1152892.8499 | 2542260.6653 | 1152882.8644 | 2542252.6638 | 1152874.9407
20 | 2542235.5022 | 1152857.946 | 2542252.6638 | 1152874.9407
21 | 2542227.3215 | 1152849.8448 | 2542235.5022 | 1152857.946
22 | 2542278.9379 | 1152725.6922 | 2542260.4964 | 1152714.3362
23 | 2542278.9379 | 1152725.6922 | 2542287.5724 | 1152699.8235
24 | 2542260.4964 | 1152714.3362 | 2542253.9114 | 1152710.2813 | 2542245.1766 | 1152702.3063
25 | 2542321.4633 | 1152715.1798 | 2542291.8251 | 1152702.9133 | 2542287.5724 | 1152699.8235
26 | 2542226.8742 | 1152875.5212 | 2542231.4564 | 1152899.3237
27 | 2542227.3215 | 1152849.8448 | 2542224.7376 | 1152864.4219 | 2542226.8742 | 1152875.5212
28 | 2542231.4564 | 1152899.3237 | 2542231.5618 | 1152899.8713
29 | 2542227.3215 | 1152849.8448 | 2542217.4239 | 1152840.018
30 | 2542212.7718 | 1152835.3992 | 2542217.4239 | 1152840.018
31 | 2542179.177 | 1152801.8709 | 2542187.0424 | 1152809.8551 | 2542212.7718 | 1152835.3992
32 | 2542445.0568 | 1152790.7134 | 2542450.1419 | 1152787.2629 | 2542463.0548 | 1152774.8465
33 | 2542445.0568 | 1152790.7134 | 2542429.6183 | 1152769.1608
34 | 2542447.8042 | 1152801.1594 | 2542445.0568 | 1152790.7134
35 | 2542417.8857 | 1152782.7916 | 2542429.6183 | 1152769.1608
36 | 2542414.9397 | 1152755.6387 | 2542429.6183 | 1152769.1608
37 | 2542498.013 | 1152769.2062 | 2542483.8717 | 1152768.5078 | 2542474.2128 | 1152773.5363 | 2542461.4811 | 1152791.0342 | 2542447.8042 | 1152801.1594
38 | 2542447.8042 | 1152801.1594 | 2542448.2381 | 1152814.4179
39 | 2542414.9397 | 1152755.6387 | 2542409.3025 | 1152752.7355
40 | 2542414.9397 | 1152755.6387 | 2542407.4553 | 1152778.5782 | 2542403.5378 | 1152783.7629 | 2542395.6946 | 1152787.6735 | 2542389.5143 | 1152786.8954
41 | 2542498.013 | 1152769.2062 | 2542558.8639 | 1152707.6836
42 | 2542448.2381 | 1152814.4179 | 2542451.2631 | 1152815.3894 | 2542470.9867 | 1152828.4966
43 | 2542448.2381 | 1152814.4179 | 2542447.2311 | 1152820.0245
44 | 2542336.9198 | 1152663.6613 | 2542290.3274 | 1152671.6162
45 | 2542343.8218 | 1152654.1549 | 2542336.9198 | 1152663.6613
46 | 2542321.4633 | 1152715.1798 | 2542334.7607 | 1152720.6774
47 | 2542321.4633 | 1152715.1798 | 2542322.4964 | 1152722.874 | 2542325.8542 | 1152735.3263 | 2542327.2206 | 1152747.3752 | 2542327.8164 | 1152752.6834 | 2542331.9289 | 1152761.4264
48 | 2542700.743 | 1152815.3618 | 2542694.1257 | 1152815.8696 | 2542690.484 | 1152818.628 | 2542687.1021 | 1152825.2749
49 | 2542691.2329 | 1152865.6365 | 2542689.6174 | 1152874.1771 | 2542689.6135 | 1152874.3555
50 | 2542689.2619 | 1152890.8116 | 2542689.6135 | 1152874.3555
51 | 2542363.4058 | 1152780.2071 | 2542379.0383 | 1152785.5765 | 2542389.5143 | 1152786.8954
52 | 2542363.4058 | 1152780.2071 | 2542361.6635 | 1152779.6087
53 | 2542361.6635 | 1152779.6087 | 2542331.9289 | 1152761.4264
54 | 2542403.1209 | 1152764.2898 | 2542409.3025 | 1152752.7355
55 | 2542331.9289 | 1152761.4264 | 2542320.7093 | 1152766.8054
56 | 2542361.0826 | 1152658.9956 | 2542369.3902 | 1152624.4785
57 | 2542343.8218 | 1152654.1549 | 2542350.3332 | 1152656.9829 | 2542361.0826 | 1152658.9956
58 | 2542343.8218 | 1152654.1549 | 2542345.5834 | 1152660.2079 | 2542349.5181 | 1152669.5974
59 | 2542349.5181 | 1152669.5974 | 2542354.6561 | 1152720.6026
60 | 2542645.0434 | 1152784.1076 | 2542646.7867 | 1152776.3444 | 2542649.4522 | 1152771.7856
61 | 2542639.6543 | 1152808.1072 | 2542645.0434 | 1152784.1076
62 | 2542639.6543 | 1152808.1072 | 2542639.1229 | 1152810.8146
63 | 2542639.6543 | 1152808.1072 | 2542656.0775 | 1152809.7455
64 | 2542633.676 | 1152838.5669 | 2542639.1229 | 1152810.8146
65 | 2542639.1229 | 1152810.8146 | 2542577.1757 | 1152810.4049
66 | 2542659.3862 | 1152810.0755 | 2542656.0775 | 1152809.7455
67 | 2542630.4708 | 1152854.8976 | 2542633.676 | 1152838.5669
68 | 2542334.7607 | 1152720.6774 | 2542336.8471 | 1152715.7881 | 2542339.8167 | 1152714.9814 | 2542354.6561 | 1152720.6026
69 | 2542639.9813 | 1152894.6059 | 2542689.2619 | 1152890.8116
70 | 2542639.9813 | 1152894.6059 | 2542638.7504 | 1152888.6478 | 2542636.6194 | 1152887.2673
71 | 2542623.622 | 1152889.815 | 2542636.6194 | 1152887.2673
72 | 2542179.177 | 1152801.8709 | 2542173.8456 | 1152796.4638
73 | 2542194.5062 | 1152788.8499 | 2542179.177 | 1152801.8709
74 | 2542175.3388 | 1152789.7569 | 2542173.8456 | 1152796.4638
75 | 2542155.9654 | 1152775.6469 | 2542168.1344 | 1152790.6712 | 2542173.8456 | 1152796.4638
76 | 2542368.4425 | 1152854.7182 | 2542381.1383 | 1152853.3259 | 2542381.1383 | 1152853.3259
77 | 2542420.3941 | 1152847.5689 | 2542409.6941 | 1152845.6259 | 2542398.8007 | 1152847.5313 | 2542381.1383 | 1152853.3259
78 | 2542445.0447 | 1152859.1391 | 2542452.6011 | 1152866.9487 | 2542462.7719 | 1152875.7877
79 | 2542478.5768 | 1152889.5232 | 2542462.7719 | 1152875.7877
80 | 2542445.0447 | 1152859.1391 | 2542439.3869 | 1152853.279
81 | 2542445.0447 | 1152859.1391 | 2542443.8399 | 1152860.7403 | 2542433.6945 | 1152885.1559
82 | 2542478.5768 | 1152889.5232 | 2542474.6441 | 1152893.1183 | 2542471.4282 | 1152904.2551
83 | 2542478.5768 | 1152889.5232 | 2542482.3361 | 1152892.6556 | 2542497.7215 | 1152902.6366
84 | 2542420.3941 | 1152847.5689 | 2542428.4274 | 1152849.8821 | 2542439.3869 | 1152853.279
85 | 2542439.3869 | 1152853.279 | 2542443.0294 | 1152843.4166 | 2542447.2311 | 1152820.0245
86 | 2542433.6945 | 1152885.1559 | 2542432.3194 | 1152888.4652
87 | 2542541.4229 | 1152919.3159 | 2542534.9185 | 1152921.1902 | 2542523.7609 | 1152919.5293 | 2542497.7215 | 1152902.6366
88 | 2542420.3941 | 1152847.5689 | 2542411.8642 | 1152835.0662
89 | 2542421.0277 | 1152905.6717 | 2542421.0277 | 1152905.6717 | 2542426.345 | 1152904.8315 | 2542431.1041 | 1152891.3898 | 2542432.3194 | 1152888.4652
90 | 2542541.4229 | 1152919.3159 | 2542595.0786 | 1152903.1137
91 | 2542499.1484 | 1152837.3207 | 2542494.899 | 1152842.3085 | 2542491.9998 | 1152842.4585 | 2542470.9867 | 1152828.4966
92 | 2542470.9867 | 1152828.4966 | 2542478.314 | 1152819.666
93 | 2542490.346 | 1152805.1655 | 2542478.314 | 1152819.666
94 | 2542630.4708 | 1152854.8976 | 2542651.5907 | 1152859.7303
95 | 2542630.4708 | 1152854.8976 | 2542623.622 | 1152889.815
96 | 2542610.0472 | 1152898.5937 | 2542622.4146 | 1152895.9631 | 2542623.622 | 1152889.815
97 | 2542610.0472 | 1152898.5937 | 2542611.2901 | 1152882.5066
98 | 2542610.0472 | 1152898.5937 | 2542595.0786 | 1152903.1137
99 | 2542315.957 | 1152769.0837 | 2542320.7093 | 1152766.8054
100 | 2542410.9499 | 1152899.7873 | 2542421.0277 | 1152905.6717
101 | 2542560.7132 | 1152708.1742 | 2542592.3 | 1152636.4356
102 | 2542560.7132 | 1152708.1742 | 2542558.8639 | 1152707.6836
103 | 2542158.2871 | 1152759.3602 | 2542158.1882 | 1152771.401 | 2542155.9654 | 1152775.6469

## bus_geodata
| x | y | coords
0 | 2542657.8267 | 1152723.6504
1 | 2542663.5235 | 1152753.9171
2 | 2542704.4524 | 1152768.2123
3 | 2542704.4313 | 1152770.825
4 | 2542680.0405 | 1152765.1976
5 | 2542704.3156 | 1152784.9975
6 | 2542669.1527 | 1152765.6475
7 | 2542296.2409 | 1152821.6134
8 | 2542267.9751 | 1152801.243
9 | 2542301.2814 | 1152825.0551
10 | 2542263.1533 | 1152797.6171
11 | 2542326.0746 | 1152841.984
12 | 2542259.6517 | 1152789.5638
13 | 2542222.7967 | 1152826.9761
14 | 2542353.8482 | 1152854.5771
15 | 2542299.3362 | 1152904.4055
16 | 2542278.5916 | 1152892.8499
17 | 2542321.5638 | 1152918.1272
18 | 2542252.6638 | 1152874.9407
19 | 2542235.5022 | 1152857.946
20 | 2542278.9379 | 1152725.6922
21 | 2542260.4964 | 1152714.3362
22 | 2542287.5724 | 1152699.8235
23 | 2542245.1766 | 1152702.3063
24 | 2542226.8742 | 1152875.5212
25 | 2542231.4564 | 1152899.3237
26 | 2542227.3215 | 1152849.8448
27 | 2542231.5618 | 1152899.8713
28 | 2542217.4239 | 1152840.018
29 | 2542212.7718 | 1152835.3992
30 | 2542463.0548 | 1152774.8465
31 | 2542445.0568 | 1152790.7134
32 | 2542429.6183 | 1152769.1608
33 | 2542447.8042 | 1152801.1594
34 | 2542417.8857 | 1152782.7916
35 | 2542414.9397 | 1152755.6387
36 | 2542498.013 | 1152769.2062
37 | 2542448.2381 | 1152814.4179
38 | 2542290.3274 | 1152671.6162
39 | 2542336.9198 | 1152663.6613
40 | 2542321.4633 | 1152715.1798
41 | 2542700.743 | 1152815.3618
42 | 2542687.1021 | 1152825.2749
43 | 2542691.2329 | 1152865.6365
44 | 2542689.6135 | 1152874.3555
45 | 2542389.5143 | 1152786.8954
46 | 2542363.4058 | 1152780.2071
47 | 2542361.6635 | 1152779.6087
48 | 2542409.3025 | 1152752.7355
49 | 2542331.9289 | 1152761.4264
50 | 2542403.1209 | 1152764.2898
51 | 2542369.3902 | 1152624.4785
52 | 2542361.0826 | 1152658.9956
53 | 2542343.8218 | 1152654.1549
54 | 2542349.5181 | 1152669.5974
55 | 2542645.0434 | 1152784.1075
56 | 2542649.4522 | 1152771.7856
57 | 2542639.6543 | 1152808.1072
58 | 2542639.1229 | 1152810.8145
59 | 2542656.0775 | 1152809.7455
60 | 2542633.676 | 1152838.5669
61 | 2542577.1757 | 1152810.4049
62 | 2542659.3862 | 1152810.0755
63 | 2542354.6561 | 1152720.6026
64 | 2542689.2619 | 1152890.8116
65 | 2542639.9813 | 1152894.6059
66 | 2542636.6194 | 1152887.2673
67 | 2542179.177 | 1152801.8709
68 | 2542173.8456 | 1152796.4638
69 | 2542194.5062 | 1152788.8499
70 | 2542368.4425 | 1152854.7182
71 | 2542381.1383 | 1152853.3259
72 | 2542462.7719 | 1152875.7877
73 | 2542445.0447 | 1152859.1391
74 | 2542478.5768 | 1152889.5232
75 | 2542439.3869 | 1152853.279
76 | 2542433.6945 | 1152885.1559
77 | 2542471.4282 | 1152904.2551
78 | 2542497.7215 | 1152902.6366
79 | 2542420.3941 | 1152847.5689
80 | 2542447.2311 | 1152820.0245
81 | 2542432.3194 | 1152888.4652
82 | 2542541.4229 | 1152919.3159
83 | 2542470.9867 | 1152828.4966
84 | 2542411.8642 | 1152835.0662
85 | 2542499.1484 | 1152837.3207
86 | 2542478.314 | 1152819.666
87 | 2542651.5907 | 1152859.7303
88 | 2542630.4708 | 1152854.8976
89 | 2542623.622 | 1152889.815
90 | 2542610.0472 | 1152898.5937
91 | 2542320.7093 | 1152766.8054
92 | 2542315.957 | 1152769.0837
93 | 2542334.7607 | 1152720.6774
94 | 2542611.2901 | 1152882.5066
95 | 2542595.0786 | 1152903.1137
96 | 2542421.0277 | 1152905.6717
97 | 2542410.9499 | 1152899.7873
98 | 2542592.3 | 1152636.4356
99 | 2542560.7132 | 1152708.1742
100 | 2542558.8639 | 1152707.6836
101 | 2542490.346 | 1152805.1655
102 | 2542175.3387 | 1152789.7569
103 | 2542155.9654 | 1152775.6469
104 | 2542158.2871 | 1152759.3602
105 | 2542347.1417 | 1152774.6209

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1