## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5586-147_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5586-147_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5586-147_0_5_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_5586-147_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_5586-147_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_5586-147_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_5586-147_0_5_node_187 | 0.4 | n |  | TRUE
7 | bus_LV_5586-147_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_5586-147_0_5_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_5586-147_0_5_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_5586-147_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_5586-147_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_5586-147_0_5_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_5586-147_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_5586-147_0_5_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_5586-147_0_5_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_5586-147_0_5_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_5586-147_0_5_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_5586-147_0_5_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_5586-147_0_5_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_5586-147_0_5_node_97 | 0.4 | n |  | TRUE
21 | bus_LV_5586-147_0_5_node_173 | 0.4 | n |  | TRUE
22 | bus_LV_5586-147_0_5_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_5586-147_0_5_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_5586-147_0_5_node_98 | 0.4 | n |  | TRUE
25 | bus_LV_5586-147_0_5_node_100 | 0.4 | n |  | TRUE
26 | bus_LV_5586-147_0_5_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_5586-147_0_5_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_5586-147_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_5586-147_0_5_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_5586-147_0_5_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_5586-147_0_5_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_5586-147_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_5586-147_0_5_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_5586-147_0_5_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_5586-147_0_5_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_5586-147_0_5_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_5586-147_0_5_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_5586-147_0_5_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_5586-147_0_5_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_5586-147_0_5_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_5586-147_0_5_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_5586-147_0_5_node_55 | 0.4 | n |  | TRUE
43 | bus_LV_5586-147_0_5_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_5586-147_0_5_node_171 | 0.4 | n |  | TRUE
45 | bus_LV_5586-147_0_5_node_172 | 0.4 | n |  | TRUE
46 | bus_LV_5586-147_0_5_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_5586-147_0_5_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_5586-147_0_5_node_163 | 0.4 | n |  | TRUE
49 | bus_LV_5586-147_0_5_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_5586-147_0_5_node_101 | 0.4 | n |  | TRUE
51 | bus_LV_5586-147_0_5_node_102 | 0.4 | n |  | TRUE
52 | bus_LV_5586-147_0_5_node_164 | 0.4 | n |  | TRUE
53 | bus_LV_5586-147_0_5_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_5586-147_0_5_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_5586-147_0_5_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_5586-147_0_5_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_5586-147_0_5_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_5586-147_0_5_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_5586-147_0_5_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_5586-147_0_5_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_5586-147_0_5_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_5586-147_0_5_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_5586-147_0_5_node_80 | 0.4 | n |  | TRUE
64 | bus_LV_5586-147_0_5_node_82 | 0.4 | n |  | TRUE
65 | bus_LV_5586-147_0_5_node_78 | 0.4 | n |  | TRUE
66 | bus_LV_5586-147_0_5_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_5586-147_0_5_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_5586-147_0_5_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_5586-147_0_5_node_178 | 0.4 | n |  | TRUE
70 | bus_LV_5586-147_0_5_node_110 | 0.4 | n |  | TRUE
71 | bus_LV_5586-147_0_5_node_115 | 0.4 | n |  | TRUE
72 | bus_LV_5586-147_0_5_node_81 | 0.4 | n |  | TRUE
73 | bus_LV_5586-147_0_5_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_5586-147_0_5_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_5586-147_0_5_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_5586-147_0_5_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_5586-147_0_5_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_5586-147_0_5_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_5586-147_0_5_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_5586-147_0_5_node_116 | 0.4 | n |  | TRUE
81 | bus_LV_5586-147_0_5_node_109 | 0.4 | n |  | TRUE
82 | bus_LV_5586-147_0_5_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_5586-147_0_5_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_5586-147_0_5_node_117 | 0.4 | n |  | TRUE
85 | bus_LV_5586-147_0_5_node_132 | 0.4 | n |  | TRUE
86 | bus_LV_5586-147_0_5_node_129 | 0.4 | n |  | TRUE
87 | bus_LV_5586-147_0_5_node_130 | 0.4 | n |  | TRUE
88 | bus_LV_5586-147_0_5_node_68 | 0.4 | n |  | TRUE
89 | bus_LV_5586-147_0_5_node_71 | 0.4 | n |  | TRUE
90 | bus_LV_5586-147_0_5_node_67 | 0.4 | n |  | TRUE
91 | bus_LV_5586-147_0_5_node_106 | 0.4 | n |  | TRUE
92 | bus_LV_5586-147_0_5_node_107 | 0.4 | n |  | TRUE
93 | bus_LV_5586-147_0_5_node_64 | 0.4 | n |  | TRUE
94 | bus_LV_5586-147_0_5_node_114 | 0.4 | n |  | TRUE
95 | bus_LV_5586-147_0_5_node_111 | 0.4 | n |  | TRUE
96 | bus_LV_5586-147_0_5_node_112 | 0.4 | n |  | TRUE
97 | bus_LV_5586-147_0_5_node_66 | 0.4 | n |  | TRUE
98 | bus_LV_5586-147_0_5_node_72 | 0.4 | n |  | TRUE
99 | bus_LV_5586-147_0_5_node_69 | 0.4 | n |  | TRUE
100 | bus_LV_5586-147_0_5_node_131 | 0.4 | n |  | TRUE
101 | bus_LV_5586-147_0_5_node_73 | 0.4 | n |  | TRUE
102 | bus_LV_5586-147_0_5_node_145 | 0.4 | n |  | TRUE
103 | bus_LV_5586-147_0_5_node_136 | 0.4 | n |  | TRUE
104 | bus_LV_5586-147_0_5_node_138 | 0.4 | n |  | TRUE
105 | bus_LV_5586-147_0_5_node_144 | 0.4 | n |  | TRUE
106 | bus_LV_5586-147_0_5_node_146 | 0.4 | n |  | TRUE
107 | bus_LV_5586-147_0_5_node_74 | 0.4 | n |  | TRUE
108 | bus_LV_5586-147_0_5_node_75 | 0.4 | n |  | TRUE
109 | bus_LV_5586-147_0_5_node_91 | 0.4 | n |  | TRUE
110 | bus_LV_5586-147_0_5_node_76 | 0.4 | n |  | TRUE
111 | bus_LV_5586-147_0_5_node_77 | 0.4 | n |  | TRUE
112 | bus_LV_5586-147_0_5_node_90 | 0.4 | n |  | TRUE
113 | bus_LV_5586-147_0_5_node_179 | 0.4 | n |  | TRUE
114 | bus_LV_5586-147_0_5_node_180 | 0.4 | n |  | TRUE
115 | bus_LV_5586-147_0_5_node_181 | 0.4 | n |  | TRUE
116 | bus_LV_5586-147_0_5_node_182 | 0.4 | n |  | TRUE
117 | bus_LV_5586-147_0_5_node_79 | 0.4 | n |  | TRUE
118 | bus_LV_5586-147_0_5_node_83 | 0.4 | n |  | TRUE
119 | bus_LV_5586-147_0_5_node_84 | 0.4 | n |  | TRUE
120 | bus_LV_5586-147_0_5_node_85 | 0.4 | n |  | TRUE
121 | bus_LV_5586-147_0_5_node_86 | 0.4 | n |  | TRUE
122 | bus_LV_5586-147_0_5_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_5586-147_0_5_node_87 | 0.4 | n |  | TRUE
124 | bus_LV_5586-147_0_5_node_103 | 0.4 | n |  | TRUE
125 | bus_LV_5586-147_0_5_node_99 | 0.4 | n |  | TRUE
126 | bus_LV_5586-147_0_5_node_88 | 0.4 | n |  | TRUE
127 | bus_LV_5586-147_0_5_node_89 | 0.4 | n |  | TRUE
128 | bus_LV_5586-147_0_5_node_104 | 0.4 | n |  | TRUE
129 | bus_LV_5586-147_0_5_node_92 | 0.4 | n |  | TRUE
130 | bus_LV_5586-147_0_5_node_177 | 0.4 | n |  | TRUE
131 | bus_LV_5586-147_0_5_node_95 | 0.4 | n |  | TRUE
132 | bus_LV_5586-147_0_5_node_93 | 0.4 | n |  | TRUE
133 | bus_LV_5586-147_0_5_node_94 | 0.4 | n |  | TRUE
134 | bus_LV_5586-147_0_5_node_96 | 0.4 | n |  | TRUE
135 | bus_LV_5586-147_0_5_node_168 | 0.4 | n |  | TRUE
136 | bus_LV_5586-147_0_5_node_108 | 0.4 | n |  | TRUE
137 | bus_LV_5586-147_0_5_node_174 | 0.4 | n |  | TRUE
138 | bus_LV_5586-147_0_5_node_124 | 0.4 | n |  | TRUE
139 | bus_LV_5586-147_0_5_node_121 | 0.4 | n |  | TRUE
140 | bus_LV_5586-147_0_5_node_128 | 0.4 | n |  | TRUE
141 | bus_LV_5586-147_0_5_node_119 | 0.4 | n |  | TRUE
142 | bus_LV_5586-147_0_5_node_191 | 0.4 | n |  | TRUE
143 | bus_LV_5586-147_0_5_node_189 | 0.4 | n |  | TRUE
144 | bus_LV_5586-147_0_5_node_113 | 0.4 | n |  | TRUE
145 | bus_LV_5586-147_0_5_node_118 | 0.4 | n |  | TRUE
146 | bus_LV_5586-147_0_5_node_120 | 0.4 | n |  | TRUE
147 | bus_LV_5586-147_0_5_node_122 | 0.4 | n |  | TRUE
148 | bus_LV_5586-147_0_5_node_123 | 0.4 | n |  | TRUE
149 | bus_LV_5586-147_0_5_node_125 | 0.4 | n |  | TRUE
150 | bus_LV_5586-147_0_5_node_126 | 0.4 | n |  | TRUE
151 | bus_LV_5586-147_0_5_node_127 | 0.4 | n |  | TRUE
152 | bus_LV_5586-147_0_5_node_175 | 0.4 | n |  | TRUE
153 | bus_LV_5586-147_0_5_node_166 | 0.4 | n |  | TRUE
154 | bus_LV_5586-147_0_5_node_176 | 0.4 | n |  | TRUE
155 | bus_LV_5586-147_0_5_node_183 | 0.4 | n |  | TRUE
156 | bus_LV_5586-147_0_5_node_184 | 0.4 | n |  | TRUE
157 | bus_LV_5586-147_0_5_node_185 | 0.4 | n |  | TRUE
158 | bus_LV_5586-147_0_5_node_190 | 0.4 | n |  | TRUE
159 | bus_LV_5586-147_0_5_node_188 | 0.4 | n |  | TRUE
160 | bus_LV_5586-147_0_5_node_133 | 0.4 | n |  | TRUE
161 | bus_LV_5586-147_0_5_node_135 | 0.4 | n |  | TRUE
162 | bus_LV_5586-147_0_5_node_153 | 0.4 | n |  | TRUE
163 | bus_LV_5586-147_0_5_node_134 | 0.4 | n |  | TRUE
164 | bus_LV_5586-147_0_5_node_154 | 0.4 | n |  | TRUE
165 | bus_LV_5586-147_0_5_node_137 | 0.4 | n |  | TRUE
166 | bus_LV_5586-147_0_5_node_152 | 0.4 | n |  | TRUE
167 | bus_LV_5586-147_0_5_node_155 | 0.4 | n |  | TRUE
168 | bus_LV_5586-147_0_5_node_139 | 0.4 | n |  | TRUE
169 | bus_LV_5586-147_0_5_node_151 | 0.4 | n |  | TRUE
170 | bus_LV_5586-147_0_5_node_140 | 0.4 | n |  | TRUE
171 | bus_LV_5586-147_0_5_node_150 | 0.4 | n |  | TRUE
172 | bus_LV_5586-147_0_5_node_141 | 0.4 | n |  | TRUE
173 | bus_LV_5586-147_0_5_node_149 | 0.4 | n |  | TRUE
174 | bus_LV_5586-147_0_5_node_142 | 0.4 | n |  | TRUE
175 | bus_LV_5586-147_0_5_node_147 | 0.4 | n |  | TRUE
176 | bus_LV_5586-147_0_5_node_148 | 0.4 | n |  | TRUE
177 | bus_LV_5586-147_0_5_node_143 | 0.4 | n |  | TRUE
178 | bus_LV_5586-147_0_5_node_192 | 0.4 | n |  | TRUE
179 | bus_LV_5586-147_0_5_node_193 | 0.4 | n |  | TRUE
180 | bus_LV_5586-147_0_5_node_161 | 0.4 | n |  | TRUE
181 | bus_LV_5586-147_0_5_node_160 | 0.4 | n |  | TRUE
182 | bus_LV_5586-147_0_5_node_156 | 0.4 | n |  | TRUE
183 | bus_LV_5586-147_0_5_node_157 | 0.4 | n |  | TRUE
184 | bus_LV_5586-147_0_5_node_158 | 0.4 | n |  | TRUE
185 | bus_LV_5586-147_0_5_node_162 | 0.4 | n |  | TRUE
186 | bus_LV_5586-147_0_5_node_159 | 0.4 | n |  | TRUE
187 | bus_LV_5586-147_0_5_node_167 | 0.4 | n |  | TRUE
188 | bus_LV_5586-147_0_5_node_170 | 0.4 | n |  | TRUE
189 | bus_MV_625_0_node_175 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5586-147_0_5_load_0 | 0 | 0.013081 | 0.0032785 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5586-147_0_5_load_1 | 1 | 0.0025529 | 0.00063981 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5586-147_0_5_load_6 | 2 | 0.0017867 | 0.00044778 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5586-147_0_5_load_3 | 4 | 0.0029396 | 0.00073672 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5586-147_0_5_load_4 | 5 | 0.0029974 | 0.00075121 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5586-147_0_5_load_187 | 6 | 0.015186 | 0.0038059 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5586-147_0_5_load_7 | 7 | 0.0019253 | 0.00048252 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5586-147_0_5_load_24 | 8 | 0.0017371 | 0.00043535 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5586-147_0_5_load_8 | 10 | 0.0042584 | 0.0010672 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5586-147_0_5_load_9 | 11 | 0.0059744 | 0.0014973 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5586-147_0_5_load_13 | 15 | 0.002953 | 0.0007401 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5586-147_0_5_load_14 | 16 | 0.0038415 | 0.00096278 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5586-147_0_5_load_15 | 17 | 0.016401 | 0.0041105 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5586-147_0_5_load_33 | 19 | 0.0035487 | 0.00088938 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5586-147_0_5_load_173 | 21 | 0.0026156 | 0.00065552 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5586-147_0_5_load_34 | 23 | 0.0026219 | 0.0006571 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5586-147_0_5_load_98 | 24 | 0.0044934 | 0.0011262 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5586-147_0_5_load_16 | 26 | 0.0052723 | 0.0013214 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5586-147_0_5_load_21 | 29 | 0.0067635 | 0.0016951 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5586-147_0_5_load_26 | 31 | 0.0035467 | 0.00088888 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5586-147_0_5_load_23 | 32 | 0.010466 | 0.0026231 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5586-147_0_5_load_38 | 33 | 0.0022154 | 0.00055523 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5586-147_0_5_load_37 | 34 | 0.0030607 | 0.00076708 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5586-147_0_5_load_36 | 35 | 0.0041012 | 0.0010279 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5586-147_0_5_load_27 | 36 | 0.0048807 | 0.0012232 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5586-147_0_5_load_55 | 42 | 0.0030636 | 0.00076781 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5586-147_0_5_load_42 | 43 | 0.0039548 | 0.00099117 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5586-147_0_5_load_171 | 44 | 0.0025574 | 0.00064094 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5586-147_0_5_load_172 | 45 | 0.01061 | 0.002659 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5586-147_0_5_load_39 | 46 | 0.0015147 | 0.00037963 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5586-147_0_5_load_163 | 48 | 0.001662 | 0.00041653 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5586-147_0_5_load_35 | 49 | 0.001882 | 0.00047168 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5586-147_0_5_load_101 | 50 | 0.0014651 | 0.00036719 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5586-147_0_5_load_102 | 51 | 0.0015092 | 0.00037824 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5586-147_0_5_load_164 | 52 | 0.007562 | 0.0018952 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5586-147_0_5_load_40 | 53 | 0.0031668 | 0.00079367 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5586-147_0_5_load_43 | 54 | 0.003952 | 0.00099045 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5586-147_0_5_load_51 | 55 | 0.002922 | 0.00073233 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5586-147_0_5_load_50 | 56 | 0.0044626 | 0.0011184 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5586-147_0_5_load_44 | 57 | 0.0022667 | 0.00056809 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5586-147_0_5_load_45 | 58 | 0.0029873 | 0.00074868 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5586-147_0_5_load_46 | 59 | 0.0027576 | 0.00069112 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5586-147_0_5_load_47 | 60 | 0.0022594 | 0.00056627 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5586-147_0_5_load_49 | 62 | 0.0034888 | 0.00087438 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5586-147_0_5_load_82 | 64 | 0.0019502 | 0.00048876 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5586-147_0_5_load_78 | 65 | 0.001784 | 0.0004471 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5586-147_0_5_load_53 | 67 | 0.0019495 | 0.00048858 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5586-147_0_5_load_178 | 69 | 0.0027103 | 0.00067927 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5586-147_0_5_load_115 | 71 | 0.0010577 | 0.00026508 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5586-147_0_5_load_56 | 73 | 0.0020671 | 0.00051807 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5586-147_0_5_load_57 | 74 | 0.0015492 | 0.00038826 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5586-147_0_5_load_59 | 76 | 0.0022994 | 0.00057627 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5586-147_0_5_load_116 | 80 | 0.0040059 | 0.001004 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5586-147_0_5_load_62 | 83 | 0.001898 | 0.00047569 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5586-147_0_5_load_117 | 84 | 0.0038599 | 0.00096738 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5586-147_0_5_load_132 | 85 | 0.0033874 | 0.00084897 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5586-147_0_5_load_129 | 86 | 0.0028588 | 0.00071648 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5586-147_0_5_load_130 | 87 | 0.0036351 | 0.00091105 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5586-147_0_5_load_67 | 90 | 0.006271 | 0.0015717 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5586-147_0_5_load_106 | 91 | 0.0036712 | 0.00092008 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5586-147_0_5_load_64 | 93 | 0.0037133 | 0.00093063 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5586-147_0_5_load_114 | 94 | 0.0023295 | 0.00058382 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5586-147_0_5_load_111 | 95 | 0.004444 | 0.0011138 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5586-147_0_5_load_112 | 96 | 0.0013891 | 0.00034814 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5586-147_0_5_load_66 | 97 | 0.0025476 | 0.00063849 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5586-147_0_5_load_69 | 99 | 0.0021042 | 0.00052736 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5586-147_0_5_load_131 | 100 | 0.0025801 | 0.00064662 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5586-147_0_5_load_138 | 104 | 0.013482 | 0.0033788 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5586-147_0_5_load_144 | 105 | 0.013139 | 0.0032929 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5586-147_0_5_load_74 | 107 | 0.0018121 | 0.00045416 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5586-147_0_5_load_91 | 109 | 0.0015505 | 0.00038859 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5586-147_0_5_load_90 | 112 | 0.0030771 | 0.0007712 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5586-147_0_5_load_179 | 113 | 0.0027023 | 0.00067726 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5586-147_0_5_load_180 | 114 | 0.0029843 | 0.00074793 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5586-147_0_5_load_181 | 115 | 0.0014478 | 0.00036285 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5586-147_0_5_load_182 | 116 | 0.0031309 | 0.00078467 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5586-147_0_5_load_79 | 117 | 0.0023652 | 0.00059277 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5586-147_0_5_load_83 | 118 | 0.0059087 | 0.0014809 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5586-147_0_5_load_84 | 119 | 0.0033608 | 0.0008423 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5586-147_0_5_load_105 | 122 | 0.0024228 | 0.00060721 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5586-147_0_5_load_87 | 123 | 0.0033475 | 0.00083897 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5586-147_0_5_load_103 | 124 | 0.0031517 | 0.00078989 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5586-147_0_5_load_88 | 126 | 0.001739 | 0.00043582 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5586-147_0_5_load_92 | 129 | 0.0032961 | 0.00082609 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5586-147_0_5_load_177 | 130 | 0.0019718 | 0.00049418 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5586-147_0_5_load_93 | 132 | 0.0021561 | 0.00054036 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5586-147_0_5_load_168 | 135 | 0.00587 | 0.0014712 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5586-147_0_5_load_174 | 137 | 0.0027194 | 0.00068154 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5586-147_0_5_load_124 | 138 | 0.005809 | 0.0014559 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5586-147_0_5_load_121 | 139 | 0.0041114 | 0.0010304 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5586-147_0_5_load_128 | 140 | 0.0024182 | 0.00060605 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5586-147_0_5_load_119 | 141 | 0.0058134 | 0.001457 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5586-147_0_5_load_191 | 142 | 0.0067699 | 0.0016967 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5586-147_0_5_load_113 | 144 | 0.0019402 | 0.00048626 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5586-147_0_5_load_118 | 145 | 0.0017587 | 0.00044077 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5586-147_0_5_load_122 | 147 | 0.0055199 | 0.0013834 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5586-147_0_5_load_123 | 148 | 0.0089458 | 0.002242 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5586-147_0_5_load_126 | 150 | 0.0054784 | 0.001373 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5586-147_0_5_load_175 | 152 | 0.0054029 | 0.0013541 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5586-147_0_5_load_183 | 155 | 0.01243 | 0.0031152 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5586-147_0_5_load_184 | 156 | 0.0078385 | 0.0019645 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5586-147_0_5_load_185 | 157 | 0.041362 | 0.010366 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5586-147_0_5_load_190 | 158 | 0.0036873 | 0.00092412 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5586-147_0_5_load_188 | 159 | 0.0068246 | 0.0017104 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5586-147_0_5_load_133 | 160 | 0.012358 | 0.0030972 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5586-147_0_5_load_153 | 162 | 0.0049441 | 0.0012391 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5586-147_0_5_load_134 | 163 | 0.011404 | 0.0028581 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_5586-147_0_5_load_154 | 164 | 0.0048935 | 0.0012264 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_5586-147_0_5_load_137 | 165 | 0.0024754 | 0.00062039 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_5586-147_0_5_load_152 | 166 | 0.0023786 | 0.00059614 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_5586-147_0_5_load_155 | 167 | 0.0029757 | 0.00074578 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_5586-147_0_5_load_139 | 168 | 0.0031303 | 0.00078452 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_5586-147_0_5_load_151 | 169 | 0.0023042 | 0.00057749 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_5586-147_0_5_load_140 | 170 | 0.0066221 | 0.0016596 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_5586-147_0_5_load_150 | 171 | 0.0022837 | 0.00057235 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_5586-147_0_5_load_149 | 173 | 0.0023583 | 0.00059105 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_5586-147_0_5_load_147 | 175 | 0.0023171 | 0.00058073 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_5586-147_0_5_load_148 | 176 | 0.0023497 | 0.0005889 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_5586-147_0_5_load_143 | 177 | 0.0025805 | 0.00064675 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_5586-147_0_5_load_192 | 178 | 0.017001 | 0.0042609 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_5586-147_0_5_load_193 | 179 | 0.010808 | 0.0027087 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_5586-147_0_5_load_161 | 180 | 0.0029002 | 0.00072686 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_5586-147_0_5_load_160 | 181 | 0.0029826 | 0.00074751 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_5586-147_0_5_load_156 | 182 | 0.0029434 | 0.00073769 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_5586-147_0_5_load_157 | 183 | 0.0121 | 0.0030325 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_5586-147_0_5_load_162 | 185 | 0.0043292 | 0.001085 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_5586-147_0_5_load_159 | 186 | 0.0029103 | 0.00072939 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_5586-147_0_5_load_167 | 187 | 0.011171 | 0.0027996 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_5586-147_0_5_load_170 | 188 | 0.0038083 | 0.00095445 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 84 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5586-147_0_5_line_0 |  | 0 | 1 | 0.01305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5586-147_0_5_line_1 |  | 1 | 2 | 0.079404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5586-147_0_5_line_2 |  | 2 | 3 | 0.028393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5586-147_0_5_line_3 |  | 3 | 7 | 0.030323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5586-147_0_5_line_4 |  | 3 | 4 | 0.034649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5586-147_0_5_line_5 |  | 4 | 5 | 0.003697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5586-147_0_5_line_6 |  | 5 | 6 | 0.077725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5586-147_0_5_line_7 |  | 7 | 8 | 0.00065085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5586-147_0_5_line_8 |  | 8 | 9 | 0.011858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5586-147_0_5_line_9 |  | 9 | 32 | 0.01528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5586-147_0_5_line_10 |  | 10 | 11 | 0.014301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5586-147_0_5_line_11 |  | 10 | 12 | 0.024035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5586-147_0_5_line_12 |  | 11 | 13 | 0.0063846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5586-147_0_5_line_13 |  | 12 | 14 | 0.012226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5586-147_0_5_line_14 |  | 12 | 15 | 0.0056806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5586-147_0_5_line_15 |  | 13 | 16 | 0.016922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5586-147_0_5_line_16 |  | 13 | 17 | 0.033015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5586-147_0_5_line_17 |  | 14 | 18 | 0.040831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5586-147_0_5_line_18 |  | 14 | 19 | 0.030625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5586-147_0_5_line_19 |  | 15 | 20 | 0.0030583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5586-147_0_5_line_20 |  | 18 | 21 | 0.016607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5586-147_0_5_line_21 |  | 18 | 22 | 0.029022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5586-147_0_5_line_22 |  | 19 | 23 | 0.0086436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5586-147_0_5_line_23 |  | 20 | 24 | 0.01043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5586-147_0_5_line_24 |  | 20 | 25 | 0.04883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5586-147_0_5_line_25 |  | 22 | 31 | 0.027673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5586-147_0_5_line_26 |  | 22 | 32 | 0.016997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5586-147_0_5_line_27 |  | 22 | 27 | 0.008151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5586-147_0_5_line_28 |  | 23 | 49 | 0.023874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5586-147_0_5_line_29 |  | 25 | 137 | 0.022952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5586-147_0_5_line_30 |  | 26 | 27 | 0.019588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5586-147_0_5_line_31 |  | 26 | 28 | 0.020671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5586-147_0_5_line_32 |  | 28 | 29 | 0.012801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5586-147_0_5_line_33 |  | 28 | 30 | 0.014623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5586-147_0_5_line_34 |  | 30 | 33 | 0.015184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5586-147_0_5_line_35 |  | 30 | 34 | 0.029357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5586-147_0_5_line_36 |  | 31 | 35 | 0.007031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5586-147_0_5_line_37 |  | 36 | 37 | 0.013425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5586-147_0_5_line_38 |  | 36 | 38 | 0.019586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5586-147_0_5_line_39 |  | 37 | 39 | 0.075967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5586-147_0_5_line_40 |  | 37 | 40 | 0.039507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5586-147_0_5_line_41 |  | 38 | 41 | 0.060324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5586-147_0_5_line_42 |  | 39 | 42 | 0.01259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5586-147_0_5_line_43 |  | 39 | 43 | 0.013836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5586-147_0_5_line_44 |  | 40 | 44 | 0.008385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5586-147_0_5_line_45 |  | 40 | 45 | 0.067499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5586-147_0_5_line_46 |  | 41 | 46 | 0.018442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5586-147_0_5_line_47 |  | 43 | 47 | 0.015048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5586-147_0_5_line_48 |  | 46 | 48 | 0.0010804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5586-147_0_5_line_49 |  | 47 | 54 | 0.021161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5586-147_0_5_line_50 |  | 47 | 53 | 0.016902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5586-147_0_5_line_51 |  | 48 | 52 | 0.0036328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5586-147_0_5_line_52 |  | 49 | 50 | 0.025389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_5586-147_0_5_line_53 |  | 50 | 51 | 0.01833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_5586-147_0_5_line_54 |  | 51 | 64 | 0.024831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_5586-147_0_5_line_55 |  | 54 | 55 | 0.014375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5586-147_0_5_line_56 |  | 55 | 56 | 0.022567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5586-147_0_5_line_57 |  | 56 | 66 | 0.0077489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5586-147_0_5_line_58 |  | 57 | 58 | 0.014479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5586-147_0_5_line_59 |  | 57 | 59 | 0.03656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5586-147_0_5_line_60 |  | 58 | 60 | 0.017421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5586-147_0_5_line_61 |  | 58 | 61 | 0.030289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5586-147_0_5_line_62 |  | 60 | 62 | 0.047298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5586-147_0_5_line_63 |  | 61 | 63 | 0.014168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5586-147_0_5_line_64 |  | 63 | 64 | 0.0098238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_5586-147_0_5_line_65 |  | 63 | 65 | 0.012694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_5586-147_0_5_line_66 |  | 65 | 117 | 0.026804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_5586-147_0_5_line_67 |  | 66 | 67 | 0.019539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5586-147_0_5_line_68 |  | 66 | 68 | 0.023251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5586-147_0_5_line_69 |  | 68 | 69 | 0.016096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5586-147_0_5_line_70 |  | 68 | 70 | 0.01403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5586-147_0_5_line_71 |  | 70 | 71 | 0.0089106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_5586-147_0_5_line_72 |  | 70 | 72 | 0.026069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_5586-147_0_5_line_73 |  | 71 | 82 | 0.020329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_5586-147_0_5_line_74 |  | 72 | 117 | 0.029842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_5586-147_0_5_line_75 |  | 72 | 110 | 0.03251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5586-147_0_5_line_76 |  | 73 | 74 | 0.013121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5586-147_0_5_line_77 |  | 73 | 75 | 0.023811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5586-147_0_5_line_78 |  | 74 | 76 | 0.03016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5586-147_0_5_line_79 |  | 75 | 77 | 0.03269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_5586-147_0_5_line_80 |  | 75 | 78 | 0.014528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_5586-147_0_5_line_81 |  | 77 | 79 | 0.018214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_5586-147_0_5_line_82 |  | 77 | 80 | 0.016541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_5586-147_0_5_line_83 |  | 78 | 81 | 0.002971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_5586-147_0_5_line_84 |  | 79 | 82 | 0.026417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_5586-147_0_5_line_85 |  | 79 | 83 | 0.043098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5586-147_0_5_line_86 |  | 80 | 84 | 0.020493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_5586-147_0_5_line_87 |  | 81 | 85 | 0.036221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5586-147_0_5_line_88 |  | 81 | 86 | 0.010183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_5586-147_0_5_line_89 |  | 81 | 87 | 0.027763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_5586-147_0_5_line_90 |  | 82 | 94 | 0.029979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5586-147_0_5_line_91 |  | 82 | 95 | 0.011972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5586-147_0_5_line_92 |  | 83 | 93 | 0.015356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5586-147_0_5_line_93 |  | 85 | 142 | 0.01377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5586-147_0_5_line_94 |  | 85 | 143 | 0.024268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5586-147_0_5_line_95 |  | 86 | 140 | 0.027286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_5586-147_0_5_line_96 |  | 87 | 98 | 0.040734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_5586-147_0_5_line_97 |  | 88 | 89 | 0.02393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5586-147_0_5_line_98 |  | 88 | 90 | 0.015455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5586-147_0_5_line_99 |  | 89 | 98 | 0.003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5586-147_0_5_line_100 |  | 89 | 99 | 0.010998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5586-147_0_5_line_101 |  | 90 | 97 | 0.0011249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5586-147_0_5_line_102 |  | 91 | 92 | 0.040771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5586-147_0_5_line_103 |  | 92 | 136 | 0.016201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_5586-147_0_5_line_104 |  | 92 | 134 | 0.024059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_5586-147_0_5_line_105 |  | 95 | 96 | 0.0030004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_5586-147_0_5_line_106 |  | 96 | 144 | 0.01905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_5586-147_0_5_line_107 |  | 98 | 100 | 0.010037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_5586-147_0_5_line_108 |  | 100 | 101 | 0.0080554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_5586-147_0_5_line_109 |  | 101 | 102 | 0.049242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_5586-147_0_5_line_110 |  | 102 | 106 | 0.018255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_5586-147_0_5_line_111 |  | 102 | 105 | 0.032171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_5586-147_0_5_line_112 |  | 103 | 104 | 0.047464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_5586-147_0_5_line_113 |  | 103 | 105 | 0.016691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_5586-147_0_5_line_114 |  | 106 | 178 | 0.021643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_5586-147_0_5_line_115 |  | 106 | 179 | 0.008541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_5586-147_0_5_line_116 |  | 107 | 108 | 0.026934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_5586-147_0_5_line_117 |  | 107 | 109 | 0.042004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_5586-147_0_5_line_118 |  | 108 | 110 | 0.030791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_5586-147_0_5_line_119 |  | 108 | 111 | 0.006961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_5586-147_0_5_line_120 |  | 109 | 112 | 0.019396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_5586-147_0_5_line_121 |  | 110 | 113 | 0.019266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_5586-147_0_5_line_122 |  | 111 | 114 | 0.020621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_5586-147_0_5_line_123 |  | 111 | 115 | 0.028347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_5586-147_0_5_line_124 |  | 111 | 116 | 0.018482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_5586-147_0_5_line_125 |  | 112 | 127 | 0.0072687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_5586-147_0_5_line_126 |  | 118 | 119 | 0.026965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_5586-147_0_5_line_127 |  | 118 | 120 | 0.0024717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_5586-147_0_5_line_128 |  | 119 | 121 | 0.03638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_5586-147_0_5_line_129 |  | 119 | 122 | 0.036909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_5586-147_0_5_line_130 |  | 120 | 123 | 0.028352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_5586-147_0_5_line_131 |  | 121 | 126 | 0.014901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_5586-147_0_5_line_132 |  | 121 | 127 | 0.004949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_5586-147_0_5_line_133 |  | 122 | 128 | 0.013415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_5586-147_0_5_line_134 |  | 124 | 125 | 0.014823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_5586-147_0_5_line_135 |  | 125 | 128 | 0.025904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_5586-147_0_5_line_136 |  | 127 | 129 | 0.01319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_5586-147_0_5_line_137 |  | 129 | 130 | 0.022357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_5586-147_0_5_line_138 |  | 130 | 131 | 0.030619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_5586-147_0_5_line_139 |  | 131 | 133 | 0.048669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_5586-147_0_5_line_140 |  | 132 | 133 | 0.042957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_5586-147_0_5_line_141 |  | 134 | 135 | 0.037663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_5586-147_0_5_line_142 |  | 136 | 138 | 0.038542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
143 | LV_5586-147_0_5_line_143 |  | 136 | 139 | 0.018693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_5586-147_0_5_line_144 |  | 138 | 140 | 0.045661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
145 | LV_5586-147_0_5_line_145 |  | 139 | 141 | 0.00094706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_5586-147_0_5_line_146 |  | 141 | 145 | 0.014805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_5586-147_0_5_line_147 |  | 143 | 158 | 0.016069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_5586-147_0_5_line_148 |  | 143 | 159 | 0.015007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_5586-147_0_5_line_149 |  | 145 | 146 | 0.017099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_5586-147_0_5_line_150 |  | 146 | 147 | 0.047145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_5586-147_0_5_line_151 |  | 146 | 148 | 0.041034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_5586-147_0_5_line_152 |  | 148 | 149 | 0.016696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_5586-147_0_5_line_153 |  | 149 | 150 | 0.026724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_5586-147_0_5_line_154 |  | 149 | 151 | 0.016743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_5586-147_0_5_line_155 |  | 151 | 152 | 0.021766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_5586-147_0_5_line_156 |  | 151 | 153 | 0.050113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_5586-147_0_5_line_157 |  | 153 | 157 | 0.015239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_5586-147_0_5_line_158 |  | 153 | 154 | 0.058904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_5586-147_0_5_line_159 |  | 154 | 155 | 0.018165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_5586-147_0_5_line_160 |  | 154 | 156 | 0.016782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_5586-147_0_5_line_161 |  | 155 | 188 | 0.046588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_5586-147_0_5_line_162 |  | 160 | 161 | 0.039983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_5586-147_0_5_line_163 |  | 160 | 162 | 0.02046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_5586-147_0_5_line_164 |  | 161 | 165 | 0.013016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_5586-147_0_5_line_165 |  | 162 | 164 | 0.026987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_5586-147_0_5_line_166 |  | 162 | 166 | 0.0079166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_5586-147_0_5_line_167 |  | 163 | 164 | 0.032137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_5586-147_0_5_line_168 |  | 164 | 167 | 0.02193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_5586-147_0_5_line_169 |  | 165 | 168 | 0.02038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_5586-147_0_5_line_170 |  | 166 | 169 | 0.0079709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_5586-147_0_5_line_171 |  | 167 | 182 | 0.0032056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_5586-147_0_5_line_172 |  | 168 | 170 | 0.036964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_5586-147_0_5_line_173 |  | 169 | 171 | 0.024689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_5586-147_0_5_line_174 |  | 170 | 172 | 0.022415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_5586-147_0_5_line_175 |  | 171 | 173 | 0.0075639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_5586-147_0_5_line_176 |  | 172 | 174 | 0.03524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_5586-147_0_5_line_177 |  | 173 | 176 | 0.0076436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_5586-147_0_5_line_178 |  | 174 | 177 | 0.0090193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_5586-147_0_5_line_179 |  | 175 | 176 | 0.0076993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_5586-147_0_5_line_180 |  | 179 | 180 | 0.037708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_5586-147_0_5_line_181 |  | 180 | 181 | 0.0076186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_5586-147_0_5_line_182 |  | 181 | 186 | 0.0025619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_5586-147_0_5_line_183 |  | 182 | 183 | 0.011725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_5586-147_0_5_line_184 |  | 183 | 184 | 0.0093472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_5586-147_0_5_line_185 |  | 184 | 185 | 0.011715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_5586-147_0_5_line_186 |  | 184 | 186 | 0.018337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_5586-147_0_5_line_187 |  | 185 | 187 | 0.027962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5586-147_0_5_trafo_117 | 0.63 MVA 20/0.4 kV | 189 | 84 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2540491.8526 | 1153235.4835 | 2540479.326 | 1153239.141 | 2540479.326 | 1153239.141
1 | 2540400.0653 | 1153243.9178 | 2540479.326 | 1153239.141
2 | 2540372.915 | 1153242.8198 | 2540380.6749 | 1153240.7528 | 2540388.0636 | 1153239.9346 | 2540395.6539 | 1153240.8821 | 2540400.0653 | 1153243.9178
3 | 2540372.915 | 1153242.8198 | 2540367.192 | 1153252.9709 | 2540365.7279 | 1153259.2999 | 2540365.6292 | 1153271.4731
4 | 2540372.915 | 1153242.8198 | 2540376.2421 | 1153238.6512 | 2540378.7178 | 1153236.0586 | 2540395.3592 | 1153230.5128 | 2540396.7846 | 1153228.0084 | 2540396.6595 | 1153222.7016
5 | 2540396.5725 | 1153219.0056 | 2540396.6595 | 1153222.7016
6 | 2540396.5725 | 1153219.0056 | 2540334.3801 | 1153172.3864
7 | 2540365.624 | 1153272.1239 | 2540365.6292 | 1153271.4731
8 | 2540365.5279 | 1153283.9819 | 2540365.624 | 1153272.1239
9 | 2540365.5279 | 1153283.9819 | 2540358.0556 | 1153294.1504 | 2540357.9299 | 1153296.8082
10 | 2540275.9635 | 1153273.3654 | 2540275.9635 | 1153273.3654 | 2540275.6592 | 1153287.6633
11 | 2540274.6409 | 1153311.6658 | 2540275.315 | 1153303.8327 | 2540275.6592 | 1153287.6633
12 | 2540277.3672 | 1153267.1369 | 2540275.9635 | 1153273.3654
13 | 2540286.879 | 1153312.4224 | 2540274.6409 | 1153311.6658
14 | 2540274.6409 | 1153311.6658 | 2540268.9714 | 1153311.3103
15 | 2540268.4014 | 1153255.9533 | 2540273.5372 | 1153256.2136 | 2540276.7716 | 1153262.029 | 2540277.3672 | 1153267.1369
16 | 2540292.7962 | 1153239.2131 | 2540290.7165 | 1153251.5293 | 2540282.3767 | 1153260.8727 | 2540277.3672 | 1153267.1369
17 | 2540286.879 | 1153312.4224 | 2540327.8218 | 1153313.2162
18 | 2540286.879 | 1153312.4224 | 2540284.927 | 1153342.985
19 | 2540265.919 | 1153311.1188 | 2540268.9714 | 1153311.3103
20 | 2540327.8218 | 1153313.2162 | 2540327.2424 | 1153329.8087
21 | 2540356.923 | 1153313.7722 | 2540327.8218 | 1153313.2162
22 | 2540284.927 | 1153342.985 | 2540284.376 | 1153351.6111
23 | 2540265.919 | 1153311.1188 | 2540265.8461 | 1153300.6917
24 | 2540219.4353 | 1153298.652 | 2540230.9916 | 1153304.14 | 2540245.7575 | 1153309.863 | 2540265.919 | 1153311.1188
25 | 2540356.923 | 1153313.7722 | 2540356.2532 | 1153318.9594 | 2540357.6939 | 1153335.0093 | 2540356.505 | 1153341.2244
26 | 2540356.923 | 1153313.7722 | 2540357.377 | 1153308.4982 | 2540357.9299 | 1153296.8082
27 | 2540365.0963 | 1153313.9356 | 2540356.923 | 1153313.7722
28 | 2540284.376 | 1153351.6111 | 2540282.8543 | 1153375.4367
29 | 2540219.4353 | 1153298.652 | 2540218.3035 | 1153304.433 | 2540219.158 | 1153317.0536 | 2540222.4331 | 1153320.0115
30 | 2540365.0963 | 1153313.9356 | 2540384.6829 | 1153314.1415
31 | 2540405.3525 | 1153314.3588 | 2540384.6829 | 1153314.1415
32 | 2540405.3525 | 1153314.3588 | 2540405.7096 | 1153327.1511
33 | 2540419.8888 | 1153316.2935 | 2540405.3525 | 1153314.3588
34 | 2540419.3087 | 1153301.1245 | 2540419.8888 | 1153316.2935
35 | 2540419.8888 | 1153316.2935 | 2540432.4231 | 1153322.9396 | 2540442.2092 | 1153334.53
36 | 2540351.1873 | 1153345.8241 | 2540356.505 | 1153341.2244
37 | 2540466.0288 | 1153473.7656 | 2540474.797 | 1153473.6009 | 2540479.3629 | 1153472.6917
38 | 2540498.1119 | 1153467.1555 | 2540495.0993 | 1153468.2081 | 2540485.3722 | 1153471.4951 | 2540479.3629 | 1153472.6917
39 | 2540392.7476 | 1153476.1598 | 2540421.7481 | 1153466.645 | 2540429.5778 | 1153465.4556 | 2540437.2674 | 1153465.6128 | 2540457.2788 | 1153472.6739 | 2540466.0288 | 1153473.7656
40 | 2540446.8729 | 1153439.2146 | 2540454.2991 | 1153452.2814 | 2540466.0288 | 1153473.7656
41 | 2540498.1119 | 1153467.1555 | 2540475.3688 | 1153411.2728
42 | 2540392.7476 | 1153476.1598 | 2540390.5264 | 1153468.0442 | 2540391.2606 | 1153463.9347
43 | 2540392.7476 | 1153476.1598 | 2540379.7527 | 1153480.9102
44 | 2540446.8729 | 1153439.2146 | 2540439.3368 | 1153442.9357
45 | 2540411.7962 | 1153381.5089 | 2540440.1963 | 1153427.4744 | 2540446.8729 | 1153439.2146
46 | 2540475.3688 | 1153411.2728 | 2540465.2367 | 1153416.287 | 2540458.6268 | 1153413.5954 | 2540458.6268 | 1153413.5954
47 | 2540365.6707 | 1153486.2116 | 2540369.9274 | 1153484.5018 | 2540379.7527 | 1153480.9102
48 | 2540458.6268 | 1153413.5954 | 2540458.3052 | 1153412.564
49 | 2540365.6707 | 1153486.2116 | 2540361.1007 | 1153488.0468 | 2540349.5724 | 1153494.6092 | 2540347.2255 | 1153496.4307
50 | 2540365.6707 | 1153486.2116 | 2540365.7749 | 1153480.4741 | 2540374.4515 | 1153473.449
51 | 2540457.2241 | 1153409.0958 | 2540458.3052 | 1153412.564
52 | 2540282.8543 | 1153375.4367 | 2540281.236 | 1153400.7736
53 | 2540281.236 | 1153400.7736 | 2540280.0676 | 1153419.0668
54 | 2540280.0676 | 1153419.0668 | 2540278.4849 | 1153443.8471
55 | 2540347.2255 | 1153496.4307 | 2540337.2682 | 1153504.1587 | 2540335.905 | 1153505.2888
56 | 2540318.5317 | 1153519.6917 | 2540335.905 | 1153505.2888
57 | 2540312.5663 | 1153524.6372 | 2540318.5317 | 1153519.6917
58 | 2540321.0069 | 1153438.9739 | 2540319.284 | 1153433.1434 | 2540316.6413 | 1153425.1703
59 | 2540313.313 | 1153391.2801 | 2540308.6893 | 1153397.7629 | 2540309.9187 | 1153404.8878 | 2540316.6413 | 1153425.1703
60 | 2540321.0069 | 1153438.9739 | 2540337.4568 | 1153433.2392
61 | 2540292.3335 | 1153448.9751 | 2540321.0069 | 1153438.9739
62 | 2540374.6844 | 1153412.5936 | 2540374.8181 | 1153417.5617 | 2540372.7491 | 1153422.4626 | 2540357.7857 | 1153427.725 | 2540349.6957 | 1153428.9726 | 2540337.4568 | 1153433.2392
63 | 2540278.922 | 1153453.6553 | 2540292.3335 | 1153448.9751
64 | 2540278.922 | 1153453.6553 | 2540278.4269 | 1153444.7554 | 2540278.4849 | 1153443.8471
65 | 2540278.922 | 1153453.6553 | 2540279.6295 | 1153466.3296
66 | 2540279.6295 | 1153466.3296 | 2540281.1235 | 1153493.092
67 | 2540312.5663 | 1153524.6372 | 2540312.9768 | 1153527.3457 | 2540313.485 | 1153532.9325 | 2540311.7299 | 1153543.9842
68 | 2540294.9782 | 1153539.8423 | 2540303.0968 | 1153532.9913 | 2540312.5663 | 1153524.6372
69 | 2540294.9782 | 1153539.8423 | 2540296.9859 | 1153542.6683 | 2540302.018 | 1153548.7327 | 2540304.1472 | 1153552.9916
70 | 2540284.2423 | 1153548.9093 | 2540294.9782 | 1153539.8423
71 | 2540284.2423 | 1153548.9093 | 2540277.8907 | 1153555.1588
72 | 2540284.2423 | 1153548.9093 | 2540282.7867 | 1153522.8876
73 | 2540263.4003 | 1153569.4164 | 2540277.8907 | 1153555.1588
74 | 2540282.7867 | 1153522.8876 | 2540281.1235 | 1153493.092
75 | 2540282.7867 | 1153522.8876 | 2540277.7676 | 1153521.2254 | 2540253.8969 | 1153507.9888
76 | 2540228.9798 | 1153630.2021 | 2540241.2219 | 1153634.9235
77 | 2540206.6326 | 1153622.0092 | 2540212.6822 | 1153623.9167 | 2540228.9798 | 1153630.2021
78 | 2540269.3615 | 1153645.7761 | 2540241.2219 | 1153634.9235
79 | 2540231.021 | 1153600.1659 | 2540206.6326 | 1153622.0092
80 | 2540195.92 | 1153631.8544 | 2540206.6326 | 1153622.0092
81 | 2540231.021 | 1153600.1659 | 2540241.9948 | 1153590.3404 | 2540244.588 | 1153588.0134
82 | 2540231.021 | 1153600.1659 | 2540219.8182 | 1153587.9957
83 | 2540195.92 | 1153631.8544 | 2540193.6218 | 1153633.7449
84 | 2540244.588 | 1153588.0134 | 2540263.4003 | 1153569.4164
85 | 2540244.588 | 1153588.0134 | 2540246.9608 | 1153590.5356 | 2540261.0217 | 1153606.4489 | 2540267.8748 | 1153615.0854 | 2540273.4309 | 1153619.9346
86 | 2540210.9143 | 1153569.6272 | 2540218.6496 | 1153586.7262 | 2540219.8182 | 1153587.9957
87 | 2540165.6012 | 1153656.7918 | 2540193.6218 | 1153633.7449
88 | 2540193.6218 | 1153633.7449 | 2540188.0736 | 1153625.2064
89 | 2540193.6218 | 1153633.7449 | 2540195.7568 | 1153637.0366 | 2540208.5614 | 1153657.1451
90 | 2540263.4003 | 1153569.4164 | 2540266.0015 | 1153571.7585 | 2540277.7606 | 1153581.4913 | 2540287.4695 | 1153587.209
91 | 2540263.4003 | 1153569.4164 | 2540256.7998 | 1153559.4286
92 | 2540287.8261 | 1153623.0804 | 2540283.5605 | 1153623.8899 | 2540274.9024 | 1153621.2189 | 2540273.4309 | 1153619.9346
93 | 2540153.9226 | 1153649.7487 | 2540160.7184 | 1153652.627 | 2540165.6012 | 1153656.7918
94 | 2540165.6012 | 1153656.7918 | 2540146.5396 | 1153671.8786
95 | 2540172.962 | 1153602.5042 | 2540174.7887 | 1153604.7612 | 2540188.0736 | 1153625.2064
96 | 2540230.2888 | 1153691.6003 | 2540221.6997 | 1153678.1229 | 2540212.2106 | 1153662.8757 | 2540208.5614 | 1153657.1451
97 | 2540220.2252 | 1153669.4996 | 2540232.7654 | 1153689.897
98 | 2540220.2252 | 1153669.4996 | 2540224.3531 | 1153667.2017 | 2540233.4484 | 1153661.5068
99 | 2540232.7654 | 1153689.897 | 2540230.2888 | 1153691.6003
100 | 2540232.7654 | 1153689.897 | 2540238.5219 | 1153699.2686
101 | 2540234.4018 | 1153660.9099 | 2540233.4484 | 1153661.5068
102 | 2540122.4455 | 1153552.2985 | 2540136.3744 | 1153562.6209 | 2540153.1799 | 1153576.7389 | 2540154.2384 | 1153577.7817
103 | 2540122.4455 | 1153552.2985 | 2540110.4148 | 1153546.1262 | 2540109.2496 | 1153548.5391
104 | 2540122.4455 | 1153552.2985 | 2540121.5845 | 1153528.2608
105 | 2540255.1456 | 1153556.9254 | 2540256.7998 | 1153559.4286
106 | 2540244.6424 | 1153541.032 | 2540255.1456 | 1153556.9254
107 | 2540230.2888 | 1153691.6003 | 2540222.0055 | 1153697.2693
108 | 2540216.4124 | 1153702.6998 | 2540217.4482 | 1153700.3883 | 2540222.0055 | 1153697.2693
109 | 2540216.4124 | 1153702.6998 | 2540181.2788 | 1153737.2013
110 | 2540181.2788 | 1153737.2013 | 2540172.0168 | 1153739.3724 | 2540163.981 | 1153742.9321
111 | 2540181.2788 | 1153737.2013 | 2540190.482 | 1153768.0274
112 | 2540193.2554 | 1153784.2186 | 2540192.8808 | 1153788.2022 | 2540194.8218 | 1153799.7558 | 2540192.0242 | 1153803.1188 | 2540167.7638 | 1153815.7951
113 | 2540193.2554 | 1153784.2186 | 2540193.7478 | 1153778.9664 | 2540190.482 | 1153768.0274
114 | 2540163.981 | 1153742.9321 | 2540155.6468 | 1153761.2138 | 2540154.1911 | 1153760.6502
115 | 2540163.981 | 1153742.9321 | 2540156.1589 | 1153739.4526
116 | 2540227.5655 | 1153491.9086 | 2540230.9101 | 1153486.4502 | 2540236.085 | 1153477.5384 | 2540236.6716 | 1153472.4965 | 2540235.3337 | 1153467.5223
117 | 2540235.3337 | 1153467.5223 | 2540222.3677 | 1153427.5701
118 | 2540227.5655 | 1153491.9086 | 2540253.8969 | 1153507.9888
119 | 2540221.3874 | 1153488.6683 | 2540227.5655 | 1153491.9086
120 | 2540203.9322 | 1153421.6169 | 2540206.1986 | 1153422.6838 | 2540222.3677 | 1153427.5701
121 | 2540251.9729 | 1153526.6958 | 2540251.1516 | 1153519.7113 | 2540251.5628 | 1153513.226 | 2540253.8969 | 1153507.9888
122 | 2540221.3874 | 1153488.6683 | 2540213.4967 | 1153487.5795 | 2540200.8063 | 1153488.3729
123 | 2540221.3874 | 1153488.6683 | 2540214.0669 | 1153490.909 | 2540205.0732 | 1153493.8556 | 2540200.5643 | 1153497.9693 | 2540199.0098 | 1153502.9097
124 | 2540221.3874 | 1153488.6683 | 2540219.8516 | 1153494.7091 | 2540218.6456 | 1153501.5136 | 2540218.6987 | 1153506.8493
125 | 2540202.5803 | 1153414.5265 | 2540203.0966 | 1153419.3796 | 2540203.9322 | 1153421.6169
126 | 2540194.3415 | 1153352.2107 | 2540197.0409 | 1153352.1258 | 2540200.6497 | 1153353.1571 | 2540201.7115 | 1153356.5373 | 2540200.0529 | 1153373.4245
127 | 2540191.871 | 1153352.2884 | 2540194.3415 | 1153352.2107
128 | 2540202.0556 | 1153409.6069 | 2540199.1617 | 1153382.4988 | 2540200.0529 | 1153373.4245
129 | 2540236.8825 | 1153375.8482 | 2540200.0529 | 1153373.4245
130 | 2540191.871 | 1153352.2884 | 2540163.5342 | 1153353.2235
131 | 2540202.0556 | 1153409.6069 | 2540205.8607 | 1153409.5468 | 2540216.9888 | 1153409.0358
132 | 2540202.0556 | 1153409.6069 | 2540202.5803 | 1153414.5265
133 | 2540240.0153 | 1153362.8042 | 2540236.8825 | 1153375.8482
134 | 2540242.7593 | 1153337.0519 | 2540235.7345 | 1153335.8655 | 2540228.1185 | 1153334.7371
135 | 2540240.0153 | 1153362.8042 | 2540242.7593 | 1153337.0519
136 | 2540202.5803 | 1153414.5265 | 2540195.948 | 1153415.771 | 2540189.515 | 1153416.1105
137 | 2540168.0152 | 1153409.9791 | 2540189.515 | 1153416.1105
138 | 2540143.2603 | 1153422.0543 | 2540145.6692 | 1153422.0192 | 2540155.98 | 1153421.1049 | 2540162.8405 | 1153418.9021 | 2540167.5289 | 1153413.5415 | 2540168.0152 | 1153409.9791
139 | 2540118.6434 | 1153445.6456 | 2540117.8136 | 1153422.4413 | 2540143.2603 | 1153422.0543
140 | 2540118.6434 | 1153445.6456 | 2540125.4309 | 1153445.3556 | 2540161.5753 | 1153444.1791
141 | 2540121.5845 | 1153528.2608 | 2540123.7557 | 1153528.2503 | 2540155.2907 | 1153526.7576 | 2540159.2338 | 1153525.9179
142 | 2540109.2496 | 1153548.5391 | 2540111.6149 | 1153550.2942 | 2540114.8411 | 1153551.4405 | 2540126.2283 | 1153558.4753 | 2540141.198 | 1153569.8283
143 | 2540109.2496 | 1153548.5391 | 2540101.12 | 1153565.3718
144 | 2540172.962 | 1153602.5042 | 2540171.495 | 1153600.6917 | 2540169.8405 | 1153598.6516 | 2540162.8991 | 1153590.4051 | 2540151.2842 | 1153578.9924 | 2540143.2288 | 1153571.3685 | 2540141.198 | 1153569.8283
145 | 2540100.7081 | 1153566.2246 | 2540101.12 | 1153565.3718
146 | 2540094.2693 | 1153579.5565 | 2540100.7081 | 1153566.2246
147 | 2540146.5396 | 1153671.8786 | 2540147.4979 | 1153684.1201 | 2540149.7228 | 1153687.1885
148 | 2540134.5039 | 1153662.8713 | 2540146.5396 | 1153671.8786
149 | 2540086.8327 | 1153594.9542 | 2540094.2693 | 1153579.5565
150 | 2540086.8327 | 1153594.9542 | 2540086.7725 | 1153602.759 | 2540088.5273 | 1153612.5467 | 2540091.6168 | 1153619.2084 | 2540098.2971 | 1153625.1228 | 2540104.8378 | 1153627.0365 | 2540110.9665 | 1153625.33
151 | 2540086.8327 | 1153594.9542 | 2540083.1342 | 1153602.6063 | 2540076.7024 | 1153621.614 | 2540069.7673 | 1153631.9759
152 | 2540061.7678 | 1153646.6097 | 2540067.7137 | 1153635.0441 | 2540069.7673 | 1153631.9759
153 | 2540061.7678 | 1153646.6097 | 2540067.4088 | 1153646.7757 | 2540078.4691 | 1153646.4319 | 2540088.142 | 1153649.3037
154 | 2540054.1059 | 1153661.5052 | 2540061.7678 | 1153646.6097
155 | 2540054.1059 | 1153661.5052 | 2540075.0811 | 1153667.5327
156 | 2540021.2008 | 1153684.0012 | 2540021.526 | 1153679.6845 | 2540021.7286 | 1153676.9254 | 2540033.793 | 1153678.0279 | 2540046.3307 | 1153678.1251 | 2540047.3609 | 1153675.2577 | 2540052.7361 | 1153664.1759 | 2540054.1059 | 1153661.5052
157 | 2540020.4397 | 1153699.217 | 2540021.2008 | 1153684.0012
158 | 2540021.2008 | 1153684.0012 | 2540021.526 | 1153679.6845 | 2540021.7286 | 1153676.9254 | 2540033.793 | 1153678.0279 | 2540049.9982 | 1153714.2635
159 | 2540049.9982 | 1153714.2635 | 2540049.7139 | 1153720.3697 | 2540047.2988 | 1153728.9984 | 2540045.4747 | 1153731.4957
160 | 2540049.9982 | 1153714.2635 | 2540066.4009 | 1153718.0242
161 | 2540045.4747 | 1153731.4957 | 2540007.2094 | 1153758.0696
162 | 2540093.0534 | 1153854.8323 | 2540085.861 | 1153834.4708 | 2540097.7372 | 1153823.6577 | 2540099.8214 | 1153822.622
163 | 2540082.515 | 1153811.7088 | 2540099.8214 | 1153822.622
164 | 2540093.0534 | 1153854.8323 | 2540090.5042 | 1153856.1695 | 2540081.5199 | 1153860.8653
165 | 2540082.515 | 1153811.7088 | 2540093.953 | 1153807.3199 | 2540096.6254 | 1153802.1794 | 2540096.5874 | 1153793.2371
166 | 2540075.1238 | 1153814.5448 | 2540082.515 | 1153811.7088
167 | 2540096.5874 | 1153793.2371 | 2540128.48 | 1153797.1919
168 | 2540096.5874 | 1153793.2371 | 2540096.5172 | 1153776.7112 | 2540095.6287 | 1153771.3805
169 | 2540081.5199 | 1153860.8653 | 2540068.8205 | 1153867.5029 | 2540065.2146 | 1153870.5739 | 2540064.5035 | 1153871.6788
170 | 2540067.682 | 1153817.4003 | 2540075.1238 | 1153814.5448
171 | 2540095.6287 | 1153771.3805 | 2540095.1016 | 1153768.2185
172 | 2540064.5035 | 1153871.6788 | 2540052.7714 | 1153889.9084 | 2540045.3958 | 1153903.297
173 | 2540044.2835 | 1153825.1753 | 2540054.8666 | 1153822.3177 | 2540067.682 | 1153817.4003
174 | 2540034.5804 | 1153922.9299 | 2540045.3958 | 1153903.297
175 | 2540044.2835 | 1153825.1753 | 2540036.9811 | 1153827.147
176 | 2540034.5804 | 1153922.9299 | 2539999.8305 | 1153916.5065
177 | 2540036.9811 | 1153827.147 | 2540029.6018 | 1153829.1395
178 | 2539999.8305 | 1153916.5065 | 2539990.9213 | 1153915.1017
179 | 2540022.1687 | 1153831.1465 | 2540029.6018 | 1153829.1395
180 | 2540118.4607 | 1153738.6037 | 2540156.1589 | 1153739.4526
181 | 2540118.4607 | 1153738.6037 | 2540111.7935 | 1153742.2904
182 | 2540109.5515 | 1153743.5301 | 2540111.7935 | 1153742.2904
183 | 2540095.1016 | 1153768.2185 | 2540093.1739 | 1153756.653
184 | 2540091.6372 | 1153747.4329 | 2540093.1739 | 1153756.653
185 | 2540089.7113 | 1153735.8792 | 2540091.6372 | 1153747.4329
186 | 2540091.6372 | 1153747.4329 | 2540094.3331 | 1153746.9614 | 2540109.5515 | 1153743.5301 | 2540109.5515 | 1153743.5301
187 | 2540089.7113 | 1153735.8792 | 2540087.1479 | 1153736.5718 | 2540065.3966 | 1153740.4018 | 2540062.2711 | 1153739.3436

## bus_geodata
| x | y | coords
0 | 2540491.8526 | 1153235.4835
1 | 2540479.326 | 1153239.141
2 | 2540400.0653 | 1153243.9178
3 | 2540372.915 | 1153242.8198
4 | 2540396.6595 | 1153222.7016
5 | 2540396.5725 | 1153219.0056
6 | 2540334.3801 | 1153172.3864
7 | 2540365.6292 | 1153271.4731
8 | 2540365.624 | 1153272.1239
9 | 2540365.5279 | 1153283.9819
10 | 2540275.6592 | 1153287.6633
11 | 2540275.9635 | 1153273.3654
12 | 2540274.6409 | 1153311.6658
13 | 2540277.3672 | 1153267.1369
14 | 2540286.879 | 1153312.4224
15 | 2540268.9714 | 1153311.3103
16 | 2540268.4014 | 1153255.9533
17 | 2540292.7962 | 1153239.2131
18 | 2540327.8218 | 1153313.2162
19 | 2540284.927 | 1153342.985
20 | 2540265.919 | 1153311.1188
21 | 2540327.2424 | 1153329.8087
22 | 2540356.923 | 1153313.7722
23 | 2540284.376 | 1153351.6111
24 | 2540265.8461 | 1153300.6917
25 | 2540219.4353 | 1153298.652
26 | 2540384.6829 | 1153314.1415
27 | 2540365.0963 | 1153313.9356
28 | 2540405.3525 | 1153314.3588
29 | 2540405.7096 | 1153327.1511
30 | 2540419.8888 | 1153316.2935
31 | 2540356.505 | 1153341.2244
32 | 2540357.9299 | 1153296.8082
33 | 2540419.3087 | 1153301.1245
34 | 2540442.2092 | 1153334.53
35 | 2540351.1873 | 1153345.8241
36 | 2540479.3629 | 1153472.6917
37 | 2540466.0288 | 1153473.7656
38 | 2540498.1119 | 1153467.1555
39 | 2540392.7476 | 1153476.1598
40 | 2540446.8729 | 1153439.2146
41 | 2540475.3688 | 1153411.2728
42 | 2540391.2606 | 1153463.9347
43 | 2540379.7527 | 1153480.9102
44 | 2540439.3368 | 1153442.9357
45 | 2540411.7962 | 1153381.5089
46 | 2540458.6268 | 1153413.5954
47 | 2540365.6707 | 1153486.2116
48 | 2540458.3052 | 1153412.564
49 | 2540282.8543 | 1153375.4367
50 | 2540281.236 | 1153400.7736
51 | 2540280.0676 | 1153419.0668
52 | 2540457.2241 | 1153409.0958
53 | 2540374.4515 | 1153473.449
54 | 2540347.2255 | 1153496.4307
55 | 2540335.905 | 1153505.2888
56 | 2540318.5317 | 1153519.6917
57 | 2540316.6413 | 1153425.1703
58 | 2540321.0069 | 1153438.9739
59 | 2540313.313 | 1153391.2801
60 | 2540337.4568 | 1153433.2392
61 | 2540292.3335 | 1153448.9751
62 | 2540374.6844 | 1153412.5936
63 | 2540278.922 | 1153453.6553
64 | 2540278.4849 | 1153443.8471
65 | 2540279.6295 | 1153466.3296
66 | 2540312.5663 | 1153524.6372
67 | 2540311.7299 | 1153543.9842
68 | 2540294.9782 | 1153539.8423
69 | 2540304.1472 | 1153552.9916
70 | 2540284.2423 | 1153548.9093
71 | 2540277.8907 | 1153555.1588
72 | 2540282.7867 | 1153522.8876
73 | 2540228.9798 | 1153630.2021
74 | 2540241.2219 | 1153634.9235
75 | 2540206.6326 | 1153622.0092
76 | 2540269.3615 | 1153645.7761
77 | 2540231.021 | 1153600.1659
78 | 2540195.92 | 1153631.8544
79 | 2540244.588 | 1153588.0134
80 | 2540219.8182 | 1153587.9957
81 | 2540193.6218 | 1153633.7449
82 | 2540263.4003 | 1153569.4164
83 | 2540273.4309 | 1153619.9346
84 | 2540210.9143 | 1153569.6272
85 | 2540165.6012 | 1153656.7918
86 | 2540188.0736 | 1153625.2064
87 | 2540208.5614 | 1153657.1451
88 | 2540220.2252 | 1153669.4996
89 | 2540232.7654 | 1153689.897
90 | 2540233.4484 | 1153661.5068
91 | 2540154.2384 | 1153577.7817
92 | 2540122.4455 | 1153552.2985
93 | 2540287.8261 | 1153623.0804
94 | 2540287.4695 | 1153587.209
95 | 2540256.7998 | 1153559.4286
96 | 2540255.1456 | 1153556.9254
97 | 2540234.4018 | 1153660.9099
98 | 2540230.2888 | 1153691.6003
99 | 2540238.5219 | 1153699.2686
100 | 2540222.0055 | 1153697.2693
101 | 2540216.4124 | 1153702.6998
102 | 2540181.2788 | 1153737.2013
103 | 2540193.2554 | 1153784.2186
104 | 2540167.7638 | 1153815.7951
105 | 2540190.482 | 1153768.0274
106 | 2540163.981 | 1153742.9321
107 | 2540235.3337 | 1153467.5223
108 | 2540227.5655 | 1153491.9086
109 | 2540222.3677 | 1153427.5701
110 | 2540253.8969 | 1153507.9888
111 | 2540221.3874 | 1153488.6683
112 | 2540203.9322 | 1153421.6169
113 | 2540251.9729 | 1153526.6958
114 | 2540200.8063 | 1153488.3729
115 | 2540199.0098 | 1153502.9097
116 | 2540218.6987 | 1153506.8493
117 | 2540281.1235 | 1153493.092
118 | 2540194.3415 | 1153352.2107
119 | 2540200.0529 | 1153373.4245
120 | 2540191.871 | 1153352.2884
121 | 2540202.0556 | 1153409.6069
122 | 2540236.8825 | 1153375.8482
123 | 2540163.5342 | 1153353.2235
124 | 2540228.1185 | 1153334.7371
125 | 2540242.7593 | 1153337.0519
126 | 2540216.9888 | 1153409.0358
127 | 2540202.5803 | 1153414.5265
128 | 2540240.0153 | 1153362.8042
129 | 2540189.515 | 1153416.1105
130 | 2540168.0152 | 1153409.9791
131 | 2540143.2603 | 1153422.0543
132 | 2540161.5753 | 1153444.1791
133 | 2540118.6434 | 1153445.6456
134 | 2540121.5845 | 1153528.2608
135 | 2540159.2338 | 1153525.9179
136 | 2540109.2496 | 1153548.5391
137 | 2540222.4331 | 1153320.0115
138 | 2540141.198 | 1153569.8283
139 | 2540101.12 | 1153565.3718
140 | 2540172.962 | 1153602.5042
141 | 2540100.7081 | 1153566.2246
142 | 2540153.9226 | 1153649.7487
143 | 2540146.5396 | 1153671.8786
144 | 2540244.6424 | 1153541.032
145 | 2540094.2693 | 1153579.5565
146 | 2540086.8327 | 1153594.9542
147 | 2540110.9665 | 1153625.33
148 | 2540069.7673 | 1153631.9759
149 | 2540061.7678 | 1153646.6097
150 | 2540088.142 | 1153649.3037
151 | 2540054.1059 | 1153661.5052
152 | 2540075.0811 | 1153667.5327
153 | 2540021.2008 | 1153684.0012
154 | 2540049.9982 | 1153714.2635
155 | 2540045.4747 | 1153731.4957
156 | 2540066.4009 | 1153718.0242
157 | 2540020.4397 | 1153699.217
158 | 2540149.7228 | 1153687.1885
159 | 2540134.5039 | 1153662.8714
160 | 2540099.8214 | 1153822.622
161 | 2540093.0534 | 1153854.8323
162 | 2540082.515 | 1153811.7088
163 | 2540128.48 | 1153797.1919
164 | 2540096.5874 | 1153793.2371
165 | 2540081.5199 | 1153860.8653
166 | 2540075.1238 | 1153814.5448
167 | 2540095.6287 | 1153771.3805
168 | 2540064.5034 | 1153871.6788
169 | 2540067.682 | 1153817.4003
170 | 2540045.3958 | 1153903.297
171 | 2540044.2835 | 1153825.1753
172 | 2540034.5804 | 1153922.9299
173 | 2540036.9811 | 1153827.147
174 | 2539999.8305 | 1153916.5065
175 | 2540022.1687 | 1153831.1465
176 | 2540029.6018 | 1153829.1395
177 | 2539990.9213 | 1153915.1017
178 | 2540154.1911 | 1153760.6502
179 | 2540156.1589 | 1153739.4526
180 | 2540118.4607 | 1153738.6037
181 | 2540111.7935 | 1153742.2904
182 | 2540095.1016 | 1153768.2185
183 | 2540093.1739 | 1153756.653
184 | 2540091.6372 | 1153747.4329
185 | 2540089.7113 | 1153735.8792
186 | 2540109.5515 | 1153743.5301
187 | 2540062.2711 | 1153739.3436
188 | 2540007.2094 | 1153758.0696
189 | 2540231.021 | 1153600.1659

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1