## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5586-156_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5586-156_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5586-156_0_4_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_5586-156_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_5586-156_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5586-156_0_4_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_5586-156_0_4_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_5586-156_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_5586-156_0_4_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_5586-156_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_5586-156_0_4_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_5586-156_0_4_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_5586-156_0_4_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_5586-156_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_5586-156_0_4_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_5586-156_0_4_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_5586-156_0_4_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_5586-156_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_5586-156_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_5586-156_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_5586-156_0_4_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_5586-156_0_4_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_5586-156_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_5586-156_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_5586-156_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_5586-156_0_4_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_5586-156_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_5586-156_0_4_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_5586-156_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_5586-156_0_4_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_5586-156_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_5586-156_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_5586-156_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_5586-156_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_5586-156_0_4_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_5586-156_0_4_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_5586-156_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_5586-156_0_4_node_30 | 0.4 | n |  | TRUE
38 | bus_MV_628_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5586-156_0_4_load_0 | 0 | 0.011062 | 0.0027724 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5586-156_0_4_load_36 | 5 | 0.048144 | 0.012066 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5586-156_0_4_load_21 | 8 | 0.041545 | 0.010412 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5586-156_0_4_load_35 | 10 | 0.005321 | 0.0013336 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5586-156_0_4_load_33 | 11 | 0.0049739 | 0.0012466 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5586-156_0_4_load_11 | 13 | 0.010476 | 0.0026256 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5586-156_0_4_load_29 | 15 | 0.014934 | 0.0037429 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5586-156_0_4_load_34 | 16 | 0.011311 | 0.0028348 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5586-156_0_4_load_17 | 17 | 0.011003 | 0.0027577 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5586-156_0_4_load_13 | 18 | 0.014969 | 0.0037516 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5586-156_0_4_load_10 | 19 | 0.015602 | 0.0039103 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5586-156_0_4_load_9 | 20 | 0.01175 | 0.0029448 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5586-156_0_4_load_31 | 21 | 0.013498 | 0.0033828 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5586-156_0_4_load_16 | 24 | 0.01484 | 0.0037193 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5586-156_0_4_load_26 | 25 | 0.018597 | 0.0046609 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5586-156_0_4_load_18 | 26 | 0.011496 | 0.0028811 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5586-156_0_4_load_27 | 27 | 0.01231 | 0.0030851 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5586-156_0_4_load_19 | 28 | 0.025522 | 0.0063963 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5586-156_0_4_load_32 | 29 | 0.010837 | 0.002716 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5586-156_0_4_load_20 | 30 | 0.012332 | 0.0030908 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5586-156_0_4_load_23 | 31 | 0.012506 | 0.0031343 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5586-156_0_4_load_24 | 32 | 0.0036132 | 0.00090555 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5586-156_0_4_load_25 | 33 | 0.0087066 | 0.0021821 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5586-156_0_4_load_39 | 34 | 0.0099702 | 0.0024988 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5586-156_0_4_load_28 | 36 | 0.010603 | 0.0026575 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5586-156_0_4_load_30 | 37 | 0.023338 | 0.0058489 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5586-156_0_4_line_0 |  | 0 | 1 | 0.016329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5586-156_0_4_line_1 |  | 1 | 2 | 0.26294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5586-156_0_4_line_2 |  | 2 | 12 | 0.017138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5586-156_0_4_line_3 |  | 2 | 13 | 0.021429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5586-156_0_4_line_4 |  | 3 | 4 | 0.011514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5586-156_0_4_line_5 |  | 3 | 5 | 0.059623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5586-156_0_4_line_6 |  | 4 | 6 | 0.020863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_5586-156_0_4_line_7 |  | 4 | 7 | 0.21234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5586-156_0_4_line_8 |  | 4 | 8 | 0.031542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5586-156_0_4_line_9 |  | 5 | 14 | 0.022731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5586-156_0_4_line_10 |  | 6 | 15 | 0.025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_5586-156_0_4_line_11 |  | 7 | 11 | 0.014321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5586-156_0_4_line_12 |  | 7 | 9 | 0.00272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5586-156_0_4_line_13 |  | 9 | 10 | 0.013599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5586-156_0_4_line_14 |  | 11 | 16 | 0.022307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5586-156_0_4_line_15 |  | 12 | 17 | 0.019648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5586-156_0_4_line_16 |  | 12 | 18 | 0.020021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5586-156_0_4_line_17 |  | 13 | 19 | 0.021756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5586-156_0_4_line_18 |  | 14 | 35 | 0.033063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5586-156_0_4_line_19 |  | 15 | 23 | 0.011087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_5586-156_0_4_line_20 |  | 17 | 21 | 0.0156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5586-156_0_4_line_21 |  | 18 | 22 | 0.0156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5586-156_0_4_line_22 |  | 19 | 20 | 0.021941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5586-156_0_4_line_23 |  | 21 | 29 | 0.0057079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5586-156_0_4_line_24 |  | 22 | 23 | 0.003019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_5586-156_0_4_line_25 |  | 22 | 24 | 0.028406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_5586-156_0_4_line_26 |  | 23 | 25 | 0.01877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5586-156_0_4_line_27 |  | 24 | 26 | 0.018769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5586-156_0_4_line_28 |  | 25 | 27 | 0.013286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5586-156_0_4_line_29 |  | 26 | 28 | 0.010144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5586-156_0_4_line_30 |  | 27 | 36 | 0.0057967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5586-156_0_4_line_31 |  | 28 | 30 | 0.01569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5586-156_0_4_line_32 |  | 31 | 32 | 0.0056204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5586-156_0_4_line_33 |  | 32 | 33 | 0.015054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5586-156_0_4_line_34 |  | 33 | 34 | 0.0021517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5586-156_0_4_line_35 |  | 34 | 35 | 0.012201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5586-156_0_4_line_36 |  | 36 | 37 | 0.014058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5586-156_0_4_trafo_16 | 0.63 MVA 20/0.4 kV | 38 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22
0 | 2537604.9089 | 1153147.428 | 2537611.9617 | 1153149.0112 | 2537617.5744 | 1153153.0552 | 2537618.7554 | 1153154.8912
1 | 2537604.9089 | 1153147.428 | 2537608.7361 | 1153151.6906 | 2537610.6034 | 1153158.6083 | 2537610.2643 | 1153164.3705 | 2537607.852 | 1153169.2649 | 2537600.2947 | 1153173.768 | 2537618.0012 | 1153189.7262 | 2537622.6776 | 1153194.4914 | 2537628.7778 | 1153195.9845 | 2537635.0621 | 1153196.7197 | 2537639.2967 | 1153199.5884 | 2537642.2725 | 1153204.6269 | 2537662.2997 | 1153200.9728 | 2537662.7992 | 1153204.0026 | 2537664.0103 | 1153211.2718 | 2537678.8185 | 1153208.2277 | 2537690.0278 | 1153205.1654 | 2537701.4927 | 1153200.8442 | 2537727.0966 | 1153188.8835 | 2537737.5279 | 1153184.0395 | 2537734.7593 | 1153173.0622 | 2537720.957 | 1153145.1012 | 2537710.3916 | 1153123.6879
2 | 2537702.8428 | 1153108.3022 | 2537708.6748 | 1153120.1815 | 2537710.3916 | 1153123.6879
3 | 2537710.3916 | 1153123.6879 | 2537691.1777 | 1153133.1769
4 | 2537660.8692 | 1153022.4129 | 2537658.5399 | 1153017.5677 | 2537655.698 | 1153012.1276
5 | 2537655.698 | 1153012.1276 | 2537604.0196 | 1153041.8646
6 | 2537660.8692 | 1153022.4129 | 2537665.9668 | 1153033.0102 | 2537669.9193 | 1153041.2181
7 | 2537660.8692 | 1153022.4129 | 2537658.5399 | 1153017.5677 | 2537684.2178 | 1153003.7829 | 2537702.8982 | 1152993.7616 | 2537712.2537 | 1152988.7398 | 2537727.6764 | 1152978.2965 | 2537739.0169 | 1152970.0746 | 2537765.2937 | 1153011.8586 | 2537778.627 | 1153031.5757 | 2537797.5789 | 1153067.0321
8 | 2537660.8692 | 1153022.4129 | 2537633.2601 | 1153037.6644
9 | 2537584.3175 | 1153053.2017 | 2537604.0196 | 1153041.8646
10 | 2537669.9193 | 1153041.2181 | 2537680.9325 | 1153063.6619
11 | 2537797.5789 | 1153067.0321 | 2537789.4418 | 1153071.1519 | 2537784.2629 | 1153071.6203
12 | 2537798.8621 | 1153069.4313 | 2537797.5789 | 1153067.0321
13 | 2537798.8621 | 1153069.4313 | 2537805.2737 | 1153081.4242
14 | 2537764.0969 | 1153078.5516 | 2537768.3475 | 1153074.0718 | 2537776.6701 | 1153072.3069 | 2537784.2629 | 1153071.6203
15 | 2537702.8428 | 1153108.3022 | 2537720.4747 | 1153099.6334
16 | 2537702.8428 | 1153108.3022 | 2537694.0222 | 1153090.3293
17 | 2537671.6705 | 1153142.8107 | 2537691.1777 | 1153133.1769
18 | 2537584.3175 | 1153053.2017 | 2537572.7005 | 1153059.8926 | 2537576.1018 | 1153066.7277 | 2537581.4621 | 1153077.489
19 | 2537685.8168 | 1153073.6154 | 2537680.9325 | 1153063.6619
20 | 2537720.4747 | 1153099.6334 | 2537734.4737 | 1153092.7507
21 | 2537687.1493 | 1153076.3253 | 2537694.0222 | 1153090.3293
22 | 2537651.9979 | 1153152.5262 | 2537671.6705 | 1153142.8107
23 | 2537734.4737 | 1153092.7507 | 2537739.5961 | 1153090.2322
24 | 2537687.1493 | 1153076.3253 | 2537685.8168 | 1153073.6154
25 | 2537687.1493 | 1153076.3253 | 2537661.74 | 1153089.0246
26 | 2537685.8168 | 1153073.6154 | 2537702.4915 | 1153064.9968
27 | 2537661.74 | 1153089.0246 | 2537644.9515 | 1153097.4154
28 | 2537702.4915 | 1153064.9968 | 2537714.294 | 1153058.8965
29 | 2537635.8779 | 1153101.9503 | 2537644.9515 | 1153097.4154
30 | 2537714.294 | 1153058.8965 | 2537719.4435 | 1153056.2349
31 | 2537621.8433 | 1153108.9647 | 2537635.8779 | 1153101.9503
32 | 2537594.5593 | 1153103.8177 | 2537597.0625 | 1153108.8498
33 | 2537594.5593 | 1153103.8177 | 2537587.8546 | 1153090.3396
34 | 2537587.8546 | 1153090.3396 | 2537586.8963 | 1153088.4131
35 | 2537581.4621 | 1153077.489 | 2537586.8963 | 1153088.4131
36 | 2537731.9317 | 1153049.7802 | 2537719.4435 | 1153056.2349

## bus_geodata
| x | y | coords
0 | 2537618.7554 | 1153154.8912
1 | 2537604.9089 | 1153147.428
2 | 2537710.3916 | 1153123.6879
3 | 2537655.698 | 1153012.1276
4 | 2537660.8692 | 1153022.4129
5 | 2537604.0196 | 1153041.8646
6 | 2537669.9193 | 1153041.2181
7 | 2537797.5789 | 1153067.0321
8 | 2537633.2601 | 1153037.6644
9 | 2537798.8621 | 1153069.4313
10 | 2537805.2737 | 1153081.4242
11 | 2537784.2629 | 1153071.6203
12 | 2537702.8428 | 1153108.3022
13 | 2537691.1777 | 1153133.1769
14 | 2537584.3175 | 1153053.2017
15 | 2537680.9325 | 1153063.6619
16 | 2537764.0969 | 1153078.5516
17 | 2537720.4747 | 1153099.6334
18 | 2537694.0222 | 1153090.3293
19 | 2537671.6705 | 1153142.8107
20 | 2537651.9979 | 1153152.5262
21 | 2537734.4737 | 1153092.7507
22 | 2537687.1493 | 1153076.3253
23 | 2537685.8168 | 1153073.6154
24 | 2537661.74 | 1153089.0246
25 | 2537702.4915 | 1153064.9968
26 | 2537644.9515 | 1153097.4154
27 | 2537714.294 | 1153058.8965
28 | 2537635.8779 | 1153101.9503
29 | 2537739.5961 | 1153090.2322
30 | 2537621.8433 | 1153108.9647
31 | 2537597.0625 | 1153108.8498
32 | 2537594.5593 | 1153103.8177
33 | 2537587.8546 | 1153090.3396
34 | 2537586.8963 | 1153088.4131
35 | 2537581.4621 | 1153077.489
36 | 2537719.4435 | 1153056.2349
37 | 2537731.9317 | 1153049.7802
38 | 2537687.1493 | 1153076.3253

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1