## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5586-194_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5586-194_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5586-194_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5586-194_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5586-194_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5586-194_0_6_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_5586-194_0_6_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_5586-194_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_5586-194_0_6_node_46 | 0.4 | n |  | TRUE
9 | bus_LV_5586-194_0_6_node_54 | 0.4 | n |  | TRUE
10 | bus_LV_5586-194_0_6_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_5586-194_0_6_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_5586-194_0_6_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_5586-194_0_6_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_5586-194_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_5586-194_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_5586-194_0_6_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_5586-194_0_6_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_5586-194_0_6_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_5586-194_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_5586-194_0_6_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_5586-194_0_6_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_5586-194_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_5586-194_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_5586-194_0_6_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_5586-194_0_6_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_5586-194_0_6_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_5586-194_0_6_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_5586-194_0_6_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_5586-194_0_6_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_5586-194_0_6_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_5586-194_0_6_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_5586-194_0_6_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_5586-194_0_6_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_5586-194_0_6_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_5586-194_0_6_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_5586-194_0_6_node_58 | 0.4 | n |  | TRUE
37 | bus_LV_5586-194_0_6_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_5586-194_0_6_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_5586-194_0_6_node_59 | 0.4 | n |  | TRUE
40 | bus_LV_5586-194_0_6_node_60 | 0.4 | n |  | TRUE
41 | bus_LV_5586-194_0_6_node_61 | 0.4 | n |  | TRUE
42 | bus_LV_5586-194_0_6_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_5586-194_0_6_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_5586-194_0_6_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_5586-194_0_6_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_5586-194_0_6_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_5586-194_0_6_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_5586-194_0_6_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_5586-194_0_6_node_75 | 0.4 | n |  | TRUE
50 | bus_LV_5586-194_0_6_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_5586-194_0_6_node_66 | 0.4 | n |  | TRUE
52 | bus_LV_5586-194_0_6_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_5586-194_0_6_node_72 | 0.4 | n |  | TRUE
54 | bus_LV_5586-194_0_6_node_69 | 0.4 | n |  | TRUE
55 | bus_LV_5586-194_0_6_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_5586-194_0_6_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_5586-194_0_6_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_5586-194_0_6_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_5586-194_0_6_node_70 | 0.4 | n |  | TRUE
60 | bus_LV_5586-194_0_6_node_71 | 0.4 | n |  | TRUE
61 | bus_LV_5586-194_0_6_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_5586-194_0_6_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_5586-194_0_6_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_5586-194_0_6_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_5586-194_0_6_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_5586-194_0_6_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_5586-194_0_6_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_5586-194_0_6_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_5586-194_0_6_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_5586-194_0_6_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_5586-194_0_6_node_67 | 0.4 | n |  | TRUE
72 | bus_LV_5586-194_0_6_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_5586-194_0_6_node_73 | 0.4 | n |  | TRUE
74 | bus_MV_627_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5586-194_0_6_load_0 | 0 | 0.011262 | 0.0028224 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5586-194_0_6_load_1 | 1 | 0.010917 | 0.0027361 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5586-194_0_6_load_3 | 3 | 0.011582 | 0.0029027 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5586-194_0_6_load_4 | 4 | 0.015885 | 0.0039812 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5586-194_0_6_load_23 | 6 | 0.016017 | 0.0040141 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5586-194_0_6_load_54 | 9 | 0.011988 | 0.0030046 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5586-194_0_6_load_44 | 12 | 0.010238 | 0.0025658 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5586-194_0_6_load_6 | 13 | 0.034229 | 0.0085786 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5586-194_0_6_load_7 | 14 | 0.0046891 | 0.0011752 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5586-194_0_6_load_10 | 16 | 0.0037432 | 0.00093813 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5586-194_0_6_load_11 | 17 | 0.0047403 | 0.001188 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5586-194_0_6_load_36 | 18 | 0.0058551 | 0.0014674 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5586-194_0_6_load_12 | 19 | 0.014109 | 0.003536 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5586-194_0_6_load_35 | 20 | 0.0043509 | 0.0010905 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5586-194_0_6_load_14 | 21 | 0.01515 | 0.003797 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5586-194_0_6_load_15 | 22 | 0.010293 | 0.0025798 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5586-194_0_6_load_16 | 23 | 0.0042074 | 0.0010545 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5586-194_0_6_load_17 | 24 | 0.0036003 | 0.00090231 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5586-194_0_6_load_18 | 25 | 0.0051245 | 0.0012843 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5586-194_0_6_load_20 | 26 | 0.0067005 | 0.0016793 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5586-194_0_6_load_32 | 27 | 0.0034653 | 0.00086848 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5586-194_0_6_load_19 | 28 | 0.0064929 | 0.0016273 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5586-194_0_6_load_31 | 29 | 0.0045211 | 0.0011331 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5586-194_0_6_load_21 | 30 | 0.0088592 | 0.0022203 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5586-194_0_6_load_22 | 31 | 0.0047526 | 0.0011911 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5586-194_0_6_load_28 | 32 | 0.01157 | 0.0028998 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5586-194_0_6_load_26 | 35 | 0.0083555 | 0.0020941 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5586-194_0_6_load_58 | 36 | 0.021064 | 0.005279 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5586-194_0_6_load_27 | 37 | 0.016953 | 0.0042488 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5586-194_0_6_load_59 | 39 | 0.0060334 | 0.0015121 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5586-194_0_6_load_60 | 40 | 0.015038 | 0.0037688 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5586-194_0_6_load_37 | 44 | 0.0060526 | 0.0015169 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5586-194_0_6_load_39 | 45 | 0.0067399 | 0.0016892 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5586-194_0_6_load_40 | 46 | 0.015401 | 0.0038598 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5586-194_0_6_load_75 | 49 | 0.0046798 | 0.0011729 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5586-194_0_6_load_66 | 51 | 0.017776 | 0.004455 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5586-194_0_6_load_65 | 52 | 0.033978 | 0.0085158 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5586-194_0_6_load_45 | 56 | 0.011042 | 0.0027675 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5586-194_0_6_load_47 | 57 | 0.009948 | 0.0024932 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5586-194_0_6_load_48 | 58 | 0.013715 | 0.0034374 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5586-194_0_6_load_70 | 59 | 0.016859 | 0.0042252 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5586-194_0_6_load_71 | 60 | 0.010376 | 0.0026005 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5586-194_0_6_load_49 | 61 | 0.0051735 | 0.0012966 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5586-194_0_6_load_50 | 62 | 0.005198 | 0.0013027 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5586-194_0_6_load_51 | 63 | 0.008709 | 0.0021827 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5586-194_0_6_load_52 | 64 | 0.016653 | 0.0041737 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5586-194_0_6_load_64 | 66 | 0.0098022 | 0.0024567 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5586-194_0_6_load_63 | 67 | 0.012178 | 0.0030522 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5586-194_0_6_load_56 | 68 | 0.01633 | 0.0040926 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5586-194_0_6_load_57 | 69 | 0.013245 | 0.0033195 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5586-194_0_6_load_62 | 70 | 0.0062335 | 0.0015623 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5586-194_0_6_load_67 | 71 | 0.0078886 | 0.0019771 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5586-194_0_6_load_73 | 73 | 0.018688 | 0.0046836 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5586-194_0_6_line_0 |  | 0 | 1 | 0.01651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_5586-194_0_6_line_1 |  | 0 | 2 | 0.037837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_5586-194_0_6_line_2 |  | 1 | 3 | 0.016373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_5586-194_0_6_line_3 |  | 2 | 4 | 0.016557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_5586-194_0_6_line_4 |  | 3 | 5 | 0.017168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_5586-194_0_6_line_5 |  | 4 | 6 | 0.0015257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_5586-194_0_6_line_6 |  | 5 | 10 | 0.091469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5586-194_0_6_line_7 |  | 5 | 7 | 0.05473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5586-194_0_6_line_8 |  | 6 | 11 | 0.037823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_5586-194_0_6_line_9 |  | 7 | 8 | 0.024057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5586-194_0_6_line_10 |  | 7 | 9 | 0.044819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5586-194_0_6_line_11 |  | 8 | 12 | 0.049209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5586-194_0_6_line_12 |  | 10 | 17 | 0.018515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5586-194_0_6_line_13 |  | 10 | 14 | 0.01491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5586-194_0_6_line_14 |  | 11 | 34 | 0.033595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_5586-194_0_6_line_15 |  | 11 | 35 | 0.0167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5586-194_0_6_line_16 |  | 12 | 56 | 0.036769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5586-194_0_6_line_17 |  | 13 | 14 | 0.043291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5586-194_0_6_line_18 |  | 13 | 15 | 0.019355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5586-194_0_6_line_19 |  | 15 | 16 | 0.057948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5586-194_0_6_line_20 |  | 16 | 18 | 0.0019989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5586-194_0_6_line_21 |  | 17 | 19 | 0.0038467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5586-194_0_6_line_22 |  | 18 | 20 | 0.013025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5586-194_0_6_line_23 |  | 20 | 44 | 0.032614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5586-194_0_6_line_24 |  | 21 | 22 | 0.0063932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5586-194_0_6_line_25 |  | 21 | 23 | 0.043843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5586-194_0_6_line_26 |  | 22 | 24 | 0.021055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5586-194_0_6_line_27 |  | 23 | 25 | 0.0097156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5586-194_0_6_line_28 |  | 24 | 26 | 0.0024941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5586-194_0_6_line_29 |  | 25 | 27 | 0.015172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5586-194_0_6_line_30 |  | 26 | 28 | 0.022836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5586-194_0_6_line_31 |  | 27 | 29 | 0.016521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5586-194_0_6_line_32 |  | 28 | 30 | 0.024871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5586-194_0_6_line_33 |  | 30 | 31 | 0.0039265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5586-194_0_6_line_34 |  | 31 | 32 | 0.017576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5586-194_0_6_line_35 |  | 32 | 33 | 0.032195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5586-194_0_6_line_36 |  | 33 | 38 | 0.015607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_5586-194_0_6_line_37 |  | 33 | 34 | 0.060884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_5586-194_0_6_line_38 |  | 34 | 36 | 0.044267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5586-194_0_6_line_39 |  | 35 | 37 | 0.0022331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5586-194_0_6_line_40 |  | 36 | 39 | 0.0080166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5586-194_0_6_line_41 |  | 38 | 40 | 0.040612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_5586-194_0_6_line_42 |  | 40 | 41 | 0.020499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_5586-194_0_6_line_43 |  | 41 | 70 | 0.017453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_5586-194_0_6_line_44 |  | 42 | 43 | 0.036642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5586-194_0_6_line_45 |  | 42 | 44 | 0.0097784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5586-194_0_6_line_46 |  | 43 | 45 | 0.054238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5586-194_0_6_line_47 |  | 46 | 47 | 0.017577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5586-194_0_6_line_48 |  | 47 | 48 | 0.019416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5586-194_0_6_line_49 |  | 48 | 49 | 0.002101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5586-194_0_6_line_50 |  | 49 | 53 | 0.032525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5586-194_0_6_line_51 |  | 50 | 51 | 0.015902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5586-194_0_6_line_52 |  | 50 | 52 | 0.013161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5586-194_0_6_line_53 |  | 51 | 54 | 0.0025998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5586-194_0_6_line_54 |  | 52 | 55 | 0.010743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5586-194_0_6_line_55 |  | 53 | 73 | 0.02988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5586-194_0_6_line_56 |  | 53 | 60 | 0.016902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5586-194_0_6_line_57 |  | 54 | 72 | 0.01353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5586-194_0_6_line_58 |  | 55 | 66 | 0.011816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5586-194_0_6_line_59 |  | 55 | 67 | 0.02047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5586-194_0_6_line_60 |  | 56 | 57 | 0.0016006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5586-194_0_6_line_61 |  | 57 | 58 | 0.016037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5586-194_0_6_line_62 |  | 58 | 59 | 0.012888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5586-194_0_6_line_63 |  | 59 | 60 | 0.0043692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5586-194_0_6_line_64 |  | 61 | 62 | 0.009129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5586-194_0_6_line_65 |  | 61 | 63 | 0.016094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5586-194_0_6_line_66 |  | 62 | 64 | 0.023723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5586-194_0_6_line_67 |  | 64 | 65 | 0.021253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5586-194_0_6_line_68 |  | 65 | 68 | 0.0090644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5586-194_0_6_line_69 |  | 65 | 69 | 0.011344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5586-194_0_6_line_70 |  | 67 | 69 | 0.0026287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5586-194_0_6_line_71 |  | 70 | 71 | 0.0097793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_5586-194_0_6_line_72 |  | 71 | 72 | 0.0052619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5586-194_0_6_trafo_23 | 0.63 MVA 20/0.4 kV | 74 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2536682.0899 | 1152117.0607 | 2536666.767 | 1152123.2067
1 | 2536687.7361 | 1152086.6397 | 2536693.5601 | 1152108.4013 | 2536691.0578 | 1152113.4638 | 2536682.0899 | 1152117.0607
2 | 2536666.767 | 1152123.2067 | 2536651.5704 | 1152129.302
3 | 2536687.7361 | 1152086.6397 | 2536703.4682 | 1152081.4795
4 | 2536635.6365 | 1152135.693 | 2536651.5704 | 1152129.302
5 | 2536703.4682 | 1152081.4795 | 2536704.9178 | 1152081.004
6 | 2536635.6365 | 1152135.693 | 2536640.2799 | 1152147.3726 | 2536643.4475 | 1152149.3626 | 2536654.5989 | 1152163.9641 | 2536655.2082 | 1152164.9805 | 2536655.3616 | 1152166.4241 | 2536655.0481 | 1152168.7175 | 2536654.2889 | 1152170.9601 | 2536653.3091 | 1152172.6491 | 2536644.6762 | 1152182.9234 | 2536650.169 | 1152190.0027 | 2536662.2658 | 1152177.8131 | 2536664.8032 | 1152176.0854 | 2536667.2905 | 1152175.4256 | 2536669.6073 | 1152175.3456
7 | 2536631.4968 | 1152098.2718 | 2536622.568 | 1152097.9657 | 2536622.3655 | 1152102.7705 | 2536621.2893 | 1152106.2504 | 2536618.2433 | 1152109.9623 | 2536627.9158 | 1152116.0303 | 2536635.6365 | 1152135.693
8 | 2536741.8197 | 1152072.8852 | 2536723.5368 | 1152076.335 | 2536710.6729 | 1152079.1163 | 2536704.9178 | 1152081.004
9 | 2536607.6029 | 1152095.8001 | 2536612.1006 | 1152096.5753 | 2536622.568 | 1152097.9657 | 2536631.4968 | 1152098.2718
10 | 2536631.4968 | 1152098.2718 | 2536631.1544 | 1152090.549 | 2536631.1505 | 1152085.8131 | 2536633.2574 | 1152081.0994 | 2536639.5959 | 1152077.3973 | 2536658.4436 | 1152071.1731
11 | 2536607.6029 | 1152095.8001 | 2536608.5269 | 1152088.8199 | 2536609.7714 | 1152081.6584 | 2536623.1608 | 1152074.8469 | 2536641.9622 | 1152068.3984
12 | 2536669.6073 | 1152175.3456 | 2536674.2153 | 1152169.8385 | 2536683.2945 | 1152163.0528
13 | 2536669.6073 | 1152175.3456 | 2536673.4681 | 1152176.1275 | 2536676.7231 | 1152178.4056 | 2536681.9095 | 1152183.1033
14 | 2536741.8197 | 1152072.8852 | 2536775.354 | 1152069.6196
15 | 2536741.8197 | 1152072.8852 | 2536743.761 | 1152080.1354 | 2536746.33 | 1152088.9636
16 | 2536641.9622 | 1152068.3984 | 2536665.6318 | 1152060.2803 | 2536666.8572 | 1152055.6649 | 2536663.9697 | 1152049.3201
17 | 2536674.9675 | 1152219.529 | 2536687.5671 | 1152200.9926 | 2536688.8782 | 1152197.966 | 2536689.2865 | 1152194.4709 | 2536689.0464 | 1152192.0722 | 2536688.2813 | 1152190.1125 | 2536686.3078 | 1152187.0872 | 2536681.9095 | 1152183.1033
18 | 2536664.0868 | 1152235.5365 | 2536674.9675 | 1152219.529
19 | 2536664.0868 | 1152235.5365 | 2536673.5461 | 1152230.1339 | 2536702.8578 | 1152210.0476 | 2536712.123 | 1152207.3375 | 2536713.9901 | 1152207.3681
20 | 2536713.9901 | 1152207.3681 | 2536715.9887 | 1152207.4008
21 | 2536686.3757 | 1152160.7499 | 2536683.2945 | 1152163.0528
22 | 2536729.0121 | 1152207.6141 | 2536715.9887 | 1152207.4008
23 | 2536729.0121 | 1152207.6141 | 2536731.1281 | 1152207.6488 | 2536749.6508 | 1152208.0653 | 2536757.5724 | 1152209.6717 | 2536761.1513 | 1152211.19
24 | 2536738.0511 | 1152138.1938 | 2536733.2415 | 1152142.4059
25 | 2536741.2456 | 1152165.5653 | 2536740.9461 | 1152165.6004 | 2536733.2792 | 1152165.581 | 2536728.3269 | 1152163.91 | 2536724.1199 | 1152160.8637 | 2536720.1401 | 1152153.8796 | 2536733.2415 | 1152142.4059
26 | 2536753.8904 | 1152124.3224 | 2536738.0511 | 1152138.1938
27 | 2536750.4467 | 1152162.8751 | 2536745.9437 | 1152165.0142 | 2536741.2456 | 1152165.5653
28 | 2536753.8904 | 1152124.3224 | 2536755.7666 | 1152122.6792
29 | 2536763.9287 | 1152155.9298 | 2536756.6421 | 1152159.9322 | 2536750.4467 | 1152162.8751
30 | 2536774.2019 | 1152109.2714 | 2536760.9604 | 1152118.1307 | 2536755.7666 | 1152122.6792
31 | 2536778.4095 | 1152147.9759 | 2536763.9287 | 1152155.9298
32 | 2536795.107 | 1152095.8072 | 2536786.5361 | 1152101.0191 | 2536774.2019 | 1152109.2714
33 | 2536795.107 | 1152095.8072 | 2536798.4619 | 1152093.7671
34 | 2536813.4796 | 1152084.6349 | 2536798.4619 | 1152093.7671
35 | 2536836.1543 | 1152063.9997 | 2536834.8613 | 1152069.4941 | 2536834.1193 | 1152071.1806 | 2536831.4825 | 1152073.6874 | 2536813.4796 | 1152084.6349
36 | 2536851.7504 | 1152062.6685 | 2536836.1543 | 1152063.9997
37 | 2536836.1543 | 1152063.9997 | 2536825.5031 | 1152064.8343 | 2536810.2223 | 1152066.229 | 2536775.354 | 1152069.6196
38 | 2536775.354 | 1152069.6196 | 2536772.4772 | 1152038.3662 | 2536783.0365 | 1152037.5436 | 2536785.3195 | 1152037.3664
39 | 2536746.954 | 1152091.1078 | 2536746.33 | 1152088.9636
40 | 2536793.3121 | 1152036.7462 | 2536785.3195 | 1152037.3664
41 | 2536851.7504 | 1152062.6685 | 2536848.5638 | 1152052.2852 | 2536843.2914 | 1152047.9049 | 2536824.4032 | 1152034.9645
42 | 2536807.4924 | 1152023.3788 | 2536824.4032 | 1152034.9645
43 | 2536807.4924 | 1152023.3788 | 2536793.0932 | 1152013.5167
44 | 2536770.1531 | 1152215.0089 | 2536771.6582 | 1152216.5495 | 2536773.1375 | 1152218.5684 | 2536776.8675 | 1152224.4212 | 2536783.9626 | 1152241.5782 | 2536785.9768 | 1152247.7493
45 | 2536770.1531 | 1152215.0089 | 2536761.1513 | 1152211.19
46 | 2536785.9768 | 1152247.7493 | 2536778.1014 | 1152246.876 | 2536767.2274 | 1152248.3912 | 2536754.93 | 1152254.6573 | 2536738.2993 | 1152268.336
47 | 2536692.2954 | 1151981.0676 | 2536695.4687 | 1151988.6938 | 2536699.1732 | 1151997.2427
48 | 2536674.5042 | 1151988.9592 | 2536692.2954 | 1151981.0676
49 | 2536674.5042 | 1151988.9592 | 2536672.5625 | 1151989.7615
50 | 2536642.5021 | 1152002.1813 | 2536672.5625 | 1151989.7615
51 | 2536752.1714 | 1151990.3536 | 2536766.3111 | 1151997.629
52 | 2536752.1714 | 1151990.3536 | 2536745.8212 | 1152001.8813
53 | 2536768.6228 | 1151998.8185 | 2536766.3111 | 1151997.629
54 | 2536738.9915 | 1152009.8028 | 2536742.9687 | 1152007.0595 | 2536745.8212 | 1152001.8813
55 | 2536642.5021 | 1152002.1813 | 2536636.0299 | 1152004.8621 | 2536621.4655 | 1152010.8855 | 2536614.8103 | 1152013.3997
56 | 2536642.5021 | 1152002.1813 | 2536649.5074 | 1152017.5632
57 | 2536780.6836 | 1152005.0173 | 2536768.6228 | 1151998.8185
58 | 2536738.9915 | 1152009.8028 | 2536729.4245 | 1152002.833
59 | 2536738.9915 | 1152009.8028 | 2536743.3208 | 1152029.8097
60 | 2536663.9697 | 1152049.3201 | 2536663.3067 | 1152047.8632
61 | 2536663.3067 | 1152047.8632 | 2536663.0153 | 1152047.223 | 2536656.66 | 1152033.2684
62 | 2536651.3183 | 1152021.5395 | 2536656.66 | 1152033.2684
63 | 2536651.3183 | 1152021.5395 | 2536649.5074 | 1152017.5632
64 | 2536703.8891 | 1152033.9965 | 2536703.8891 | 1152033.9965 | 2536702.6091 | 1152037.7898 | 2536704.8534 | 1152042.3979
65 | 2536703.8891 | 1152033.9965 | 2536717.1405 | 1152024.8632
66 | 2536725.1489 | 1152045.7757 | 2536707.4411 | 1152047.711 | 2536704.8534 | 1152042.3979
67 | 2536746.276 | 1152043.4667 | 2536725.1489 | 1152045.7757
68 | 2536746.276 | 1152043.4667 | 2536755.286 | 1152042.4753
69 | 2536746.276 | 1152043.4667 | 2536743.8767 | 1152032.379
70 | 2536743.8767 | 1152032.379 | 2536743.3208 | 1152029.8097
71 | 2536785.0248 | 1152007.9906 | 2536793.0932 | 1152013.5167
72 | 2536780.6836 | 1152005.0173 | 2536785.0248 | 1152007.9906

## bus_geodata
| x | y | coords
0 | 2536682.0899 | 1152117.0607
1 | 2536666.767 | 1152123.2067
2 | 2536687.7361 | 1152086.6397
3 | 2536651.5704 | 1152129.302
4 | 2536703.4682 | 1152081.4795
5 | 2536635.6365 | 1152135.693
6 | 2536704.9178 | 1152081.004
7 | 2536631.4968 | 1152098.2718
8 | 2536607.6029 | 1152095.8001
9 | 2536658.4436 | 1152071.1731
10 | 2536669.6073 | 1152175.3456
11 | 2536741.8197 | 1152072.8852
12 | 2536641.9622 | 1152068.3984
13 | 2536674.9675 | 1152219.529
14 | 2536681.9095 | 1152183.1034
15 | 2536664.0868 | 1152235.5365
16 | 2536713.9901 | 1152207.3681
17 | 2536683.2945 | 1152163.0528
18 | 2536715.9887 | 1152207.4008
19 | 2536686.3757 | 1152160.7499
20 | 2536729.0121 | 1152207.6141
21 | 2536733.2415 | 1152142.4059
22 | 2536738.0511 | 1152138.1938
23 | 2536741.2456 | 1152165.5653
24 | 2536753.8904 | 1152124.3224
25 | 2536750.4467 | 1152162.8751
26 | 2536755.7666 | 1152122.6792
27 | 2536763.9287 | 1152155.9298
28 | 2536774.2019 | 1152109.2714
29 | 2536778.4095 | 1152147.9759
30 | 2536795.107 | 1152095.8072
31 | 2536798.4619 | 1152093.7671
32 | 2536813.4796 | 1152084.6349
33 | 2536836.1543 | 1152063.9997
34 | 2536775.354 | 1152069.6196
35 | 2536746.33 | 1152088.9636
36 | 2536785.3195 | 1152037.3664
37 | 2536746.954 | 1152091.1078
38 | 2536851.7504 | 1152062.6685
39 | 2536793.3121 | 1152036.7462
40 | 2536824.4032 | 1152034.9645
41 | 2536807.4924 | 1152023.3788
42 | 2536770.1531 | 1152215.0089
43 | 2536785.9768 | 1152247.7493
44 | 2536761.1513 | 1152211.19
45 | 2536738.2993 | 1152268.336
46 | 2536699.1732 | 1151997.2427
47 | 2536692.2954 | 1151981.0676
48 | 2536674.5042 | 1151988.9592
49 | 2536672.5625 | 1151989.7615
50 | 2536752.1714 | 1151990.3536
51 | 2536766.3111 | 1151997.629
52 | 2536745.8212 | 1152001.8813
53 | 2536642.5021 | 1152002.1813
54 | 2536768.6228 | 1151998.8185
55 | 2536738.9915 | 1152009.8028
56 | 2536663.9697 | 1152049.3201
57 | 2536663.3067 | 1152047.8632
58 | 2536656.66 | 1152033.2684
59 | 2536651.3183 | 1152021.5395
60 | 2536649.5074 | 1152017.5632
61 | 2536703.8891 | 1152033.9965
62 | 2536704.8534 | 1152042.3979
63 | 2536717.1405 | 1152024.8632
64 | 2536725.1489 | 1152045.7757
65 | 2536746.276 | 1152043.4667
66 | 2536729.4245 | 1152002.833
67 | 2536743.3208 | 1152029.8097
68 | 2536755.286 | 1152042.4753
69 | 2536743.8767 | 1152032.379
70 | 2536793.0932 | 1152013.5167
71 | 2536785.0248 | 1152007.9906
72 | 2536780.6836 | 1152005.0173
73 | 2536614.8103 | 1152013.3997
74 | 2536687.7361 | 1152086.6397

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1