## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5590-32_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5590-32_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_5590-32_0_6_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_5590-32_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5590-32_0_6_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_5590-32_0_6_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_5590-32_0_6_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_5590-32_0_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_5590-32_0_6_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_5590-32_0_6_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_5590-32_0_6_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_5590-32_0_6_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_5590-32_0_6_node_57 | 0.4 | n |  | TRUE
13 | bus_LV_5590-32_0_6_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_5590-32_0_6_node_56 | 0.4 | n |  | TRUE
15 | bus_LV_5590-32_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_5590-32_0_6_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_5590-32_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_5590-32_0_6_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_5590-32_0_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_5590-32_0_6_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_5590-32_0_6_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_5590-32_0_6_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_5590-32_0_6_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_5590-32_0_6_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_5590-32_0_6_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_5590-32_0_6_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_5590-32_0_6_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_5590-32_0_6_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_5590-32_0_6_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_5590-32_0_6_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_5590-32_0_6_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_5590-32_0_6_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_5590-32_0_6_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_5590-32_0_6_node_51 | 0.4 | n |  | TRUE
35 | bus_LV_5590-32_0_6_node_52 | 0.4 | n |  | TRUE
36 | bus_LV_5590-32_0_6_node_53 | 0.4 | n |  | TRUE
37 | bus_LV_5590-32_0_6_node_59 | 0.4 | n |  | TRUE
38 | bus_LV_5590-32_0_6_node_61 | 0.4 | n |  | TRUE
39 | bus_LV_5590-32_0_6_node_55 | 0.4 | n |  | TRUE
40 | bus_LV_5590-32_0_6_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_5590-32_0_6_node_60 | 0.4 | n |  | TRUE
42 | bus_LV_5590-32_0_6_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_5590-32_0_6_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_5590-32_0_6_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_5590-32_0_6_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_5590-32_0_6_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_5590-32_0_6_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_5590-32_0_6_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_5590-32_0_6_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_5590-32_0_6_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_5590-32_0_6_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_5590-32_0_6_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_5590-32_0_6_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_5590-32_0_6_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_5590-32_0_6_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_5590-32_0_6_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_5590-32_0_6_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_5590-32_0_6_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_5590-32_0_6_node_54 | 0.4 | n |  | TRUE
60 | bus_MV_619_0_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5590-32_0_6_load_0 | 0 | 0.0092152 | 0.0023096 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5590-32_0_6_load_6 | 2 | 0.015775 | 0.0039535 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5590-32_0_6_load_25 | 5 | 0.021798 | 0.0054631 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5590-32_0_6_load_7 | 7 | 0.00099086 | 0.00024833 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5590-32_0_6_load_23 | 9 | 0.0042176 | 0.001057 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5590-32_0_6_load_27 | 10 | 0.0089403 | 0.0022407 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5590-32_0_6_load_57 | 12 | 0.0086389 | 0.0021651 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5590-32_0_6_load_58 | 13 | 0.0086868 | 0.0021771 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5590-32_0_6_load_56 | 14 | 0.008069 | 0.0020223 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5590-32_0_6_load_8 | 15 | 0.013688 | 0.0034306 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5590-32_0_6_load_9 | 16 | 0.013612 | 0.0034116 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5590-32_0_6_load_12 | 18 | 0.026008 | 0.0065182 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5590-32_0_6_load_13 | 19 | 0.021794 | 0.0054621 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5590-32_0_6_load_16 | 22 | 0.0022343 | 0.00055996 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5590-32_0_6_load_17 | 25 | 0.034691 | 0.0086943 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5590-32_0_6_load_29 | 26 | 0.0082071 | 0.0020569 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5590-32_0_6_load_18 | 28 | 0.013634 | 0.003417 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5590-32_0_6_load_31 | 29 | 0.0041582 | 0.0010422 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5590-32_0_6_load_39 | 30 | 0.0039834 | 0.00099834 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5590-32_0_6_load_22 | 31 | 0.005967 | 0.0014955 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5590-32_0_6_load_20 | 32 | 0.025451 | 0.0063787 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5590-32_0_6_load_38 | 33 | 0.012038 | 0.0030169 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5590-32_0_6_load_52 | 35 | 0.023985 | 0.0060112 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5590-32_0_6_load_53 | 36 | 0.0027621 | 0.00069224 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5590-32_0_6_load_59 | 37 | 0.013333 | 0.0033416 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5590-32_0_6_load_61 | 38 | 0.0063375 | 0.0015883 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5590-32_0_6_load_55 | 39 | 0.0051435 | 0.0012891 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5590-32_0_6_load_60 | 41 | 0.0040579 | 0.001017 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5590-32_0_6_load_44 | 42 | 0.0031568 | 0.00079118 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5590-32_0_6_load_32 | 43 | 0.0066036 | 0.001655 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5590-32_0_6_load_42 | 44 | 0.0079963 | 0.0020041 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5590-32_0_6_load_37 | 46 | 0.0055952 | 0.0014023 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5590-32_0_6_load_36 | 47 | 0.0059796 | 0.0014986 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5590-32_0_6_load_35 | 49 | 0.0042692 | 0.00107 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5590-32_0_6_load_34 | 50 | 0.010366 | 0.0025981 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5590-32_0_6_load_40 | 52 | 0.0077714 | 0.0019477 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5590-32_0_6_load_41 | 53 | 0.0050251 | 0.0012594 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5590-32_0_6_load_50 | 56 | 0.0039564 | 0.00099156 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5590-32_0_6_load_48 | 58 | 0.0074682 | 0.0018717 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5590-32_0_6_load_54 | 59 | 0.0090809 | 0.0022759 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5590-32_0_6_line_0 |  | 0 | 1 | 0.013019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5590-32_0_6_line_1 |  | 1 | 2 | 0.01601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5590-32_0_6_line_2 |  | 2 | 7 | 0.0005336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5590-32_0_6_line_3 |  | 3 | 4 | 0.044259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_5590-32_0_6_line_4 |  | 3 | 5 | 0.038729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_5590-32_0_6_line_5 |  | 4 | 9 | 0.037334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_5590-32_0_6_line_6 |  | 5 | 8 | 0.0037361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_5590-32_0_6_line_7 |  | 6 | 7 | 0.012888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5590-32_0_6_line_8 |  | 6 | 8 | 0.047608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5590-32_0_6_line_9 |  | 8 | 10 | 0.019805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_5590-32_0_6_line_10 |  | 9 | 21 | 0.010769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_5590-32_0_6_line_11 |  | 10 | 34 | 0.019274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_5590-32_0_6_line_12 |  | 11 | 12 | 0.021388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5590-32_0_6_line_13 |  | 11 | 13 | 0.038466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5590-32_0_6_line_14 |  | 11 | 14 | 0.011383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5590-32_0_6_line_15 |  | 12 | 37 | 0.014903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5590-32_0_6_line_16 |  | 13 | 38 | 0.021517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5590-32_0_6_line_17 |  | 14 | 39 | 0.021777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5590-32_0_6_line_18 |  | 15 | 16 | 0.028613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5590-32_0_6_line_19 |  | 15 | 17 | 0.014659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_5590-32_0_6_line_20 |  | 17 | 18 | 0.013236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_5590-32_0_6_line_21 |  | 17 | 19 | 0.005601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5590-32_0_6_line_22 |  | 18 | 20 | 0.010182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_5590-32_0_6_line_23 |  | 20 | 22 | 0.026276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_5590-32_0_6_line_24 |  | 21 | 31 | 0.017523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_5590-32_0_6_line_25 |  | 21 | 32 | 0.01721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5590-32_0_6_line_26 |  | 22 | 26 | 0.012609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_5590-32_0_6_line_27 |  | 23 | 24 | 0.053431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_5590-32_0_6_line_28 |  | 23 | 25 | 0.0079884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_5590-32_0_6_line_29 |  | 24 | 27 | 0.015479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_5590-32_0_6_line_30 |  | 25 | 28 | 0.036265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_5590-32_0_6_line_31 |  | 26 | 29 | 0.030842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_5590-32_0_6_line_32 |  | 27 | 30 | 0.0086178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_5590-32_0_6_line_33 |  | 27 | 31 | 0.0071111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_5590-32_0_6_line_34 |  | 29 | 43 | 0.0054559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_5590-32_0_6_line_35 |  | 30 | 33 | 0.018155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5590-32_0_6_line_36 |  | 33 | 52 | 0.044414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5590-32_0_6_line_37 |  | 34 | 35 | 0.028793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5590-32_0_6_line_38 |  | 34 | 36 | 0.035836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_5590-32_0_6_line_39 |  | 35 | 59 | 0.0047182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5590-32_0_6_line_40 |  | 36 | 41 | 0.027852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_5590-32_0_6_line_41 |  | 39 | 59 | 0.018353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5590-32_0_6_line_42 |  | 40 | 41 | 1.4441e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_5590-32_0_6_line_43 |  | 40 | 42 | 0.0045397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_5590-32_0_6_line_44 |  | 42 | 44 | 0.015623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_5590-32_0_6_line_45 |  | 43 | 45 | 0.027798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_5590-32_0_6_line_46 |  | 44 | 53 | 0.013539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_5590-32_0_6_line_47 |  | 45 | 46 | 0.037697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_5590-32_0_6_line_48 |  | 45 | 47 | 0.012634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5590-32_0_6_line_49 |  | 46 | 48 | 0.0073721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_5590-32_0_6_line_50 |  | 47 | 49 | 0.00048072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5590-32_0_6_line_51 |  | 48 | 51 | 0.004912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_5590-32_0_6_line_52 |  | 49 | 50 | 0.027834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5590-32_0_6_line_53 |  | 51 | 58 | 0.030122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_5590-32_0_6_line_54 |  | 53 | 54 | 0.052523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_5590-32_0_6_line_55 |  | 54 | 55 | 0.037635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_5590-32_0_6_line_56 |  | 55 | 56 | 0.0073259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_5590-32_0_6_line_57 |  | 56 | 57 | 0.014238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_5590-32_0_6_line_58 |  | 57 | 58 | 0.0075502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5590-32_0_6_trafo_8 | 0.63 MVA 20/0.4 kV | 60 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2540006.1657 | 1151878.278 | 2540013.557 | 1151879.1047 | 2540019.1183 | 1151879.5828
1 | 2540006.1657 | 1151878.278 | 2540005.2294 | 1151892.8841 | 2540005.4482 | 1151894.2404
2 | 2540005.5331 | 1151894.7671 | 2540005.4482 | 1151894.2404
3 | 2539930.5219 | 1151898.0884 | 2539960.8554 | 1151884.5559 | 2539971.759 | 1151882.8016
4 | 2539971.759 | 1151882.8016 | 2539969.9616 | 1151891.1018 | 2539967.4757 | 1151921.2356
5 | 2539930.5219 | 1151898.0884 | 2539902.8973 | 1151909.2704 | 2539896.4997 | 1151913.2465
6 | 2539967.1685 | 1151924.959 | 2539967.4757 | 1151921.2356
7 | 2540007.5855 | 1151907.4907 | 2540005.5331 | 1151894.7671
8 | 2539967.1685 | 1151924.959 | 2539990.7634 | 1151924.4788 | 2539997.1381 | 1151916.4998 | 2540007.5855 | 1151907.4907
9 | 2539967.1685 | 1151924.959 | 2539965.2595 | 1151944.6715
10 | 2539887.3529 | 1151918.931 | 2539896.4997 | 1151913.2465
11 | 2539963.167 | 1151963.831 | 2539964.5736 | 1151951.7549 | 2539965.2595 | 1151944.6715
12 | 2540047.8564 | 1151969.9782 | 2540046.8749 | 1151975.4465 | 2540044.0795 | 1151991.03
13 | 2540047.8564 | 1151969.9782 | 2540076.6669 | 1151966.8893 | 2540084.9817 | 1151962.3139
14 | 2540047.8564 | 1151969.9782 | 2540041.8003 | 1151970.6612 | 2540036.5317 | 1151970.2035
15 | 2540044.0795 | 1151991.03 | 2540041.4482 | 1152005.6984
16 | 2540084.9817 | 1151962.3139 | 2540103.8333 | 1151951.9404
17 | 2540014.8364 | 1151968.3191 | 2540036.5317 | 1151970.2035
18 | 2539924.7208 | 1151988.6168 | 2539926.5506 | 1151960.0626
19 | 2539923.7834 | 1152003.2457 | 2539924.7208 | 1151988.6168
20 | 2539923.7834 | 1152003.2457 | 2539912.0861 | 1152009.4386
21 | 2539925.8844 | 1152008.4386 | 2539923.7834 | 1152003.2457
22 | 2539903.0872 | 1152014.2029 | 2539912.0861 | 1152009.4386
23 | 2539903.0872 | 1152014.2029 | 2539909.2709 | 1152029.3492 | 2539908.0691 | 1152032.7297 | 2539911.0611 | 1152038.3054
24 | 2539887.3529 | 1151918.931 | 2539872.393 | 1151928.0563
25 | 2539887.3529 | 1151918.931 | 2539892.4615 | 1151933.9992 | 2539891.3676 | 1151934.6997
26 | 2539917.0233 | 1152049.4159 | 2539911.0611 | 1152038.3054
27 | 2539873.6651 | 1151945.3933 | 2539886.5166 | 1151969.5889 | 2539863.1722 | 1151981.2731
28 | 2539863.1722 | 1151981.2731 | 2539856.1455 | 1151985.073
29 | 2539873.6651 | 1151945.3933 | 2539866.3222 | 1151931.7594
30 | 2539836.754 | 1152004.8167 | 2539840.0301 | 1152003.1831 | 2539836.5431 | 1151999.0824 | 2539842.2822 | 1151996.6348 | 2539840.8449 | 1151993.3474 | 2539856.1455 | 1151985.073
31 | 2539917.0233 | 1152049.4159 | 2539889.0282 | 1152062.3578
32 | 2539866.3222 | 1151931.7594 | 2539859.479 | 1151936.9974
33 | 2539866.3222 | 1151931.7594 | 2539872.393 | 1151928.0563
34 | 2539889.0282 | 1152062.3578 | 2539884.0759 | 1152064.6472
35 | 2539845.0627 | 1151948.0322 | 2539859.479 | 1151936.9974
36 | 2539812.0149 | 1151937.7615 | 2539832.4601 | 1151957.6787 | 2539845.0627 | 1151948.0322
37 | 2539963.167 | 1151963.831 | 2539991.8521 | 1151966.3227
38 | 2539963.167 | 1151963.831 | 2539964.052 | 1151999.6557
39 | 2539996.5526 | 1151966.7309 | 2539991.8521 | 1151966.3227
40 | 2539967.327 | 1152027.1985 | 2539965.1479 | 1152018.4629 | 2539964.2751 | 1152008.6886 | 2539964.052 | 1151999.6557
41 | 2539996.5526 | 1151966.7309 | 2540014.8364 | 1151968.3191
42 | 2539967.327 | 1152027.1985 | 2539967.3305 | 1152027.2125
43 | 2539967.3305 | 1152027.2125 | 2539968.2224 | 1152031.6637
44 | 2539971.2918 | 1152046.9824 | 2539968.2224 | 1152031.6637
45 | 2539858.8433 | 1152076.3121 | 2539884.0759 | 1152064.6472
46 | 2539973.9517 | 1152060.2572 | 2539971.2918 | 1152046.9824
47 | 2539858.8433 | 1152076.3121 | 2539864.2358 | 1152092.1555 | 2539881.5449 | 1152103.9777
48 | 2539858.8433 | 1152076.3121 | 2539853.2557 | 1152064.9813
49 | 2539882.0559 | 1152111.3321 | 2539881.5449 | 1152103.9777
50 | 2539853.0431 | 1152064.5502 | 2539853.2557 | 1152064.9813
51 | 2539886.9823 | 1152111.2717 | 2539882.0559 | 1152111.3321
52 | 2539854.944 | 1152044.0106 | 2539845.5106 | 1152049.2753 | 2539853.0431 | 1152064.5502
53 | 2539886.9823 | 1152111.2717 | 2539917.1022 | 1152110.926
54 | 2539983.9236 | 1152111.8146 | 2539980.9961 | 1152098.3922 | 2539977.9035 | 1152079.9798 | 2539973.9517 | 1152060.2572
55 | 2539946.2145 | 1152110.5905 | 2539971.0392 | 1152111.91 | 2539983.9236 | 1152111.8146
56 | 2539946.2145 | 1152110.5905 | 2539938.8891 | 1152110.6751
57 | 2539924.6518 | 1152110.8394 | 2539938.8891 | 1152110.6751
58 | 2539924.6518 | 1152110.8394 | 2539917.1022 | 1152110.926

## bus_geodata
| x | y | coords
0 | 2540019.1183 | 1151879.5828
1 | 2540006.1657 | 1151878.278
2 | 2540005.4482 | 1151894.2404
3 | 2539971.759 | 1151882.8016
4 | 2539930.5219 | 1151898.0884
5 | 2539967.4757 | 1151921.2356
6 | 2540007.5855 | 1151907.4907
7 | 2540005.5331 | 1151894.7671
8 | 2539967.1685 | 1151924.959
9 | 2539896.4997 | 1151913.2465
10 | 2539965.2595 | 1151944.6715
11 | 2540047.8564 | 1151969.9782
12 | 2540044.0795 | 1151991.03
13 | 2540084.9817 | 1151962.3139
14 | 2540036.5317 | 1151970.2035
15 | 2539924.7208 | 1151988.6168
16 | 2539926.5506 | 1151960.0626
17 | 2539923.7834 | 1152003.2457
18 | 2539912.0861 | 1152009.4386
19 | 2539925.8844 | 1152008.4386
20 | 2539903.0872 | 1152014.2028
21 | 2539887.3529 | 1151918.931
22 | 2539911.0611 | 1152038.3054
23 | 2539863.1722 | 1151981.2731
24 | 2539873.6651 | 1151945.3933
25 | 2539856.1455 | 1151985.073
26 | 2539917.0233 | 1152049.4159
27 | 2539866.3222 | 1151931.7594
28 | 2539836.754 | 1152004.8167
29 | 2539889.0282 | 1152062.3578
30 | 2539859.479 | 1151936.9974
31 | 2539872.393 | 1151928.0563
32 | 2539891.3676 | 1151934.6997
33 | 2539845.0627 | 1151948.0322
34 | 2539963.167 | 1151963.831
35 | 2539991.8521 | 1151966.3227
36 | 2539964.052 | 1151999.6557
37 | 2540041.4482 | 1152005.6984
38 | 2540103.8333 | 1151951.9404
39 | 2540014.8364 | 1151968.3191
40 | 2539967.3305 | 1152027.2125
41 | 2539967.327 | 1152027.1985
42 | 2539968.2224 | 1152031.6637
43 | 2539884.0759 | 1152064.6472
44 | 2539971.2918 | 1152046.9824
45 | 2539858.8433 | 1152076.3121
46 | 2539881.5449 | 1152103.9777
47 | 2539853.2557 | 1152064.9813
48 | 2539882.0559 | 1152111.3321
49 | 2539853.0431 | 1152064.5502
50 | 2539854.944 | 1152044.0106
51 | 2539886.9823 | 1152111.2717
52 | 2539812.0149 | 1151937.7615
53 | 2539973.9517 | 1152060.2572
54 | 2539983.9236 | 1152111.8146
55 | 2539946.2145 | 1152110.5905
56 | 2539938.8891 | 1152110.6751
57 | 2539924.6518 | 1152110.8394
58 | 2539917.1022 | 1152110.926
59 | 2539996.5526 | 1151966.7309
60 | 2539923.7834 | 1152003.2457

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1