## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5624-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5624-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5624-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5624-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5624-2_0_4_node_74 | 0.4 | n |  | TRUE
5 | bus_LV_5624-2_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_5624-2_0_4_node_71 | 0.4 | n |  | TRUE
7 | bus_LV_5624-2_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_5624-2_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5624-2_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_5624-2_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_5624-2_0_4_node_44 | 0.4 | n |  | TRUE
12 | bus_LV_5624-2_0_4_node_54 | 0.4 | n |  | TRUE
13 | bus_LV_5624-2_0_4_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_5624-2_0_4_node_53 | 0.4 | n |  | TRUE
15 | bus_LV_5624-2_0_4_node_75 | 0.4 | n |  | TRUE
16 | bus_LV_5624-2_0_4_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_5624-2_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_5624-2_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_5624-2_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_5624-2_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_5624-2_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_5624-2_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_5624-2_0_4_node_77 | 0.4 | n |  | TRUE
24 | bus_LV_5624-2_0_4_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_5624-2_0_4_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_5624-2_0_4_node_42 | 0.4 | n |  | TRUE
27 | bus_LV_5624-2_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_5624-2_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_5624-2_0_4_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_5624-2_0_4_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_5624-2_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_5624-2_0_4_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_5624-2_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_5624-2_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_5624-2_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_5624-2_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_5624-2_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_5624-2_0_4_node_59 | 0.4 | n |  | TRUE
39 | bus_LV_5624-2_0_4_node_62 | 0.4 | n |  | TRUE
40 | bus_LV_5624-2_0_4_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_5624-2_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_5624-2_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_5624-2_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_5624-2_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_5624-2_0_4_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_5624-2_0_4_node_51 | 0.4 | n |  | TRUE
47 | bus_LV_5624-2_0_4_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_5624-2_0_4_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_5624-2_0_4_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_5624-2_0_4_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_5624-2_0_4_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_5624-2_0_4_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_5624-2_0_4_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_5624-2_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_5624-2_0_4_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_5624-2_0_4_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_5624-2_0_4_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_5624-2_0_4_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_5624-2_0_4_node_61 | 0.4 | n |  | TRUE
60 | bus_LV_5624-2_0_4_node_57 | 0.4 | n |  | TRUE
61 | bus_LV_5624-2_0_4_node_58 | 0.4 | n |  | TRUE
62 | bus_LV_5624-2_0_4_node_67 | 0.4 | n |  | TRUE
63 | bus_LV_5624-2_0_4_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_5624-2_0_4_node_66 | 0.4 | n |  | TRUE
65 | bus_LV_5624-2_0_4_node_63 | 0.4 | n |  | TRUE
66 | bus_LV_5624-2_0_4_node_68 | 0.4 | n |  | TRUE
67 | bus_LV_5624-2_0_4_node_69 | 0.4 | n |  | TRUE
68 | bus_LV_5624-2_0_4_node_73 | 0.4 | n |  | TRUE
69 | bus_LV_5624-2_0_4_node_72 | 0.4 | n |  | TRUE
70 | bus_LV_5624-2_0_4_node_78 | 0.4 | n |  | TRUE
71 | bus_LV_5624-2_0_4_node_79 | 0.4 | n |  | TRUE
72 | bus_LV_5624-2_0_4_node_70 | 0.4 | n |  | TRUE
73 | bus_MV_623_0_node_110 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5624-2_0_4_load_0 | 0 | 0.0070304 | 0.001762 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5624-2_0_4_load_3 | 3 | 0.016601 | 0.0041605 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5624-2_0_4_load_74 | 4 | 0.0075825 | 0.0019004 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5624-2_0_4_load_4 | 5 | 0.00076467 | 0.00019164 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5624-2_0_4_load_5 | 7 | 0.042825 | 0.010733 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5624-2_0_4_load_8 | 9 | 0.0017176 | 0.00043047 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5624-2_0_4_load_9 | 10 | 0.0037907 | 0.00095004 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5624-2_0_4_load_44 | 11 | 0.0018024 | 0.00045172 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5624-2_0_4_load_54 | 12 | 0.001778 | 0.00044561 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5624-2_0_4_load_43 | 13 | 0.0016228 | 0.00040671 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5624-2_0_4_load_53 | 14 | 0.0018941 | 0.0004747 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5624-2_0_4_load_75 | 15 | 0.01293 | 0.0032407 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5624-2_0_4_load_12 | 17 | 0.018505 | 0.0046379 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5624-2_0_4_load_13 | 18 | 0.033137 | 0.008305 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5624-2_0_4_load_77 | 23 | 0.061784 | 0.015484 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5624-2_0_4_load_38 | 24 | 0.0018169 | 0.00045537 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5624-2_0_4_load_37 | 25 | 0.012341 | 0.003093 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5624-2_0_4_load_42 | 26 | 0.0019194 | 0.00048106 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5624-2_0_4_load_19 | 27 | 0.0033039 | 0.00082803 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5624-2_0_4_load_20 | 28 | 0.0034361 | 0.00086117 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5624-2_0_4_load_22 | 30 | 0.0035048 | 0.00087838 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5624-2_0_4_load_23 | 31 | 0.0033558 | 0.00084104 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5624-2_0_4_load_30 | 32 | 0.0033287 | 0.00083425 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5624-2_0_4_load_31 | 33 | 0.0016119 | 0.00040399 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5624-2_0_4_load_25 | 34 | 0.0054215 | 0.0013588 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5624-2_0_4_load_26 | 35 | 0.0031833 | 0.0007978 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5624-2_0_4_load_27 | 36 | 0.0013864 | 0.00034747 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5624-2_0_4_load_59 | 38 | 0.0030688 | 0.00076912 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5624-2_0_4_load_32 | 40 | 0.0053937 | 0.0013518 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5624-2_0_4_load_33 | 41 | 0.0065446 | 0.0016402 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5624-2_0_4_load_34 | 42 | 0.0027379 | 0.00068618 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5624-2_0_4_load_35 | 43 | 0.010423 | 0.0026123 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5624-2_0_4_load_36 | 44 | 0.0047125 | 0.0011811 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5624-2_0_4_load_55 | 45 | 0.012228 | 0.0030646 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5624-2_0_4_load_52 | 48 | 0.0043855 | 0.0010991 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5624-2_0_4_load_48 | 49 | 0.0074138 | 0.0018581 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5624-2_0_4_load_40 | 51 | 0.0016723 | 0.00041912 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5624-2_0_4_load_41 | 52 | 0.0079143 | 0.0019835 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5624-2_0_4_load_50 | 53 | 0.0019481 | 0.00048823 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5624-2_0_4_load_46 | 54 | 0.0097253 | 0.0024374 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5624-2_0_4_load_45 | 55 | 0.0096316 | 0.0024139 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5624-2_0_4_load_49 | 57 | 0.0022274 | 0.00055823 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5624-2_0_4_load_60 | 58 | 0.0053638 | 0.0013443 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5624-2_0_4_load_61 | 59 | 0.0061595 | 0.0015437 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5624-2_0_4_load_58 | 61 | 0.015278 | 0.0038292 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5624-2_0_4_load_67 | 62 | 0.021065 | 0.0052793 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5624-2_0_4_load_65 | 63 | 0.0071656 | 0.0017959 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5624-2_0_4_load_63 | 65 | 0.0086554 | 0.0021693 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5624-2_0_4_load_73 | 68 | 0.020738 | 0.0051974 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5624-2_0_4_load_72 | 69 | 0.0086082 | 0.0021574 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5624-2_0_4_load_78 | 70 | 0.0066392 | 0.0016639 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5624-2_0_4_load_79 | 71 | 0.001339 | 0.00033558 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 62 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5624-2_0_4_line_0 |  | 0 | 1 | 0.15722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5624-2_0_4_line_1 |  | 1 | 2 | 0.059107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5624-2_0_4_line_2 |  | 1 | 3 | 0.048183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5624-2_0_4_line_3 |  | 2 | 4 | 0.01618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5624-2_0_4_line_4 |  | 3 | 5 | 0.11764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5624-2_0_4_line_5 |  | 4 | 6 | 0.077116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5624-2_0_4_line_6 |  | 6 | 72 | 0.085612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5624-2_0_4_line_7 |  | 7 | 8 | 0.023806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5624-2_0_4_line_8 |  | 8 | 9 | 0.040772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5624-2_0_4_line_9 |  | 8 | 10 | 0.015254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5624-2_0_4_line_10 |  | 9 | 11 | 0.016215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5624-2_0_4_line_11 |  | 10 | 12 | 0.013062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5624-2_0_4_line_12 |  | 11 | 13 | 0.012786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5624-2_0_4_line_13 |  | 12 | 14 | 0.002306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5624-2_0_4_line_14 |  | 13 | 26 | 0.013098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5624-2_0_4_line_15 |  | 14 | 57 | 0.030384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5624-2_0_4_line_16 |  | 15 | 16 | 0.005723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5624-2_0_4_line_17 |  | 16 | 29 | 0.014865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5624-2_0_4_line_18 |  | 17 | 18 | 0.084417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_5624-2_0_4_line_19 |  | 17 | 19 | 0.11508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_5624-2_0_4_line_20 |  | 18 | 20 | 0.066495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_5624-2_0_4_line_21 |  | 19 | 21 | 0.030624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5624-2_0_4_line_22 |  | 20 | 22 | 0.018626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_5624-2_0_4_line_23 |  | 21 | 23 | 0.10249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5624-2_0_4_line_24 |  | 22 | 24 | 0.0026415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_5624-2_0_4_line_25 |  | 24 | 25 | 0.01278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_5624-2_0_4_line_26 |  | 25 | 50 | 0.0055136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_5624-2_0_4_line_27 |  | 27 | 28 | 0.0018201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5624-2_0_4_line_28 |  | 27 | 29 | 0.020264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5624-2_0_4_line_29 |  | 28 | 30 | 0.0087292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5624-2_0_4_line_30 |  | 29 | 31 | 0.014686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5624-2_0_4_line_31 |  | 30 | 32 | 0.0090102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5624-2_0_4_line_32 |  | 32 | 33 | 0.0091453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5624-2_0_4_line_33 |  | 33 | 37 | 0.011996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5624-2_0_4_line_34 |  | 34 | 35 | 0.0085528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5624-2_0_4_line_35 |  | 34 | 36 | 0.0095629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5624-2_0_4_line_36 |  | 35 | 37 | 0.007981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5624-2_0_4_line_37 |  | 37 | 38 | 0.017939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5624-2_0_4_line_38 |  | 38 | 39 | 0.0011984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5624-2_0_4_line_39 |  | 39 | 65 | 0.014329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5624-2_0_4_line_40 |  | 39 | 59 | 0.010566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5624-2_0_4_line_41 |  | 40 | 41 | 0.0023565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_5624-2_0_4_line_42 |  | 40 | 42 | 0.0076763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_5624-2_0_4_line_43 |  | 41 | 43 | 0.0090463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_5624-2_0_4_line_44 |  | 42 | 44 | 0.0093439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_5624-2_0_4_line_45 |  | 43 | 45 | 0.016163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_5624-2_0_4_line_46 |  | 44 | 46 | 0.0090197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_5624-2_0_4_line_47 |  | 45 | 47 | 0.019074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_5624-2_0_4_line_48 |  | 46 | 48 | 0.0016893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5624-2_0_4_line_49 |  | 46 | 49 | 0.018884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_5624-2_0_4_line_50 |  | 47 | 60 | 0.011295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_5624-2_0_4_line_51 |  | 47 | 61 | 0.031985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5624-2_0_4_line_52 |  | 48 | 58 | 0.0073497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5624-2_0_4_line_53 |  | 49 | 56 | 0.019598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_5624-2_0_4_line_54 |  | 50 | 51 | 0.034913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5624-2_0_4_line_55 |  | 50 | 52 | 0.0080304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_5624-2_0_4_line_56 |  | 51 | 53 | 0.00821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5624-2_0_4_line_57 |  | 52 | 54 | 0.012115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_5624-2_0_4_line_58 |  | 54 | 55 | 0.013106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_5624-2_0_4_line_59 |  | 55 | 56 | 0.014004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_5624-2_0_4_line_60 |  | 56 | 57 | 0.046221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5624-2_0_4_line_61 |  | 58 | 59 | 0.01194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5624-2_0_4_line_62 |  | 60 | 62 | 0.029488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_5624-2_0_4_line_63 |  | 60 | 63 | 0.021072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5624-2_0_4_line_64 |  | 63 | 64 | 0.04485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5624-2_0_4_line_65 |  | 64 | 66 | 0.004085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5624-2_0_4_line_66 |  | 64 | 67 | 0.041012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5624-2_0_4_line_67 |  | 66 | 68 | 0.031373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5624-2_0_4_line_68 |  | 66 | 69 | 0.028026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5624-2_0_4_line_69 |  | 67 | 70 | 0.004524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5624-2_0_4_line_70 |  | 67 | 71 | 0.041973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5624-2_0_4_line_71 |  | 69 | 72 | 0.013455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5624-2_0_4_trafo_67 | 0.63 MVA 20/0.4 kV | 73 | 62 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2531303.9411 | 1155871.7809 | 2531367.3858 | 1155745.5414 | 2531374.6904 | 1155731.3774
1 | 2531356.5978 | 1155898.8831 | 2531325.7434 | 1155882.2375 | 2531303.9411 | 1155871.7809
2 | 2531303.9411 | 1155871.7809 | 2531262.7113 | 1155846.8465
3 | 2531356.5978 | 1155898.8831 | 2531370.8364 | 1155906.5668
4 | 2531262.7113 | 1155846.8465 | 2531227.9509 | 1155825.8245 | 2531265.4899 | 1155758.5728
5 | 2531439.5697 | 1155941.1706 | 2531428.4536 | 1155937.5843 | 2531408.2041 | 1155926.7316 | 2531370.8364 | 1155906.5668
6 | 2531439.5697 | 1155941.1706 | 2531459.6174 | 1155942.4204 | 2531471.8707 | 1155940.1349 | 2531480.7392 | 1155937.6435 | 2531502.2298 | 1155930.9059 | 2531514.0269 | 1155926.947 | 2531518.061 | 1155925.5892 | 2531519.5682 | 1155929.9633
7 | 2531801.4174 | 1155807.657 | 2531825.0168 | 1155804.5275
8 | 2531801.4174 | 1155807.657 | 2531794.7182 | 1155767.4389
9 | 2531801.4174 | 1155807.657 | 2531786.4416 | 1155810.5547
10 | 2531792.0531 | 1155751.4441 | 2531793.4991 | 1155760.1205 | 2531794.7182 | 1155767.4389
11 | 2531773.6194 | 1155813.0455 | 2531773.8279 | 1155812.9953 | 2531786.4416 | 1155810.5547
12 | 2531792.0531 | 1155751.4441 | 2531789.9511 | 1155738.8318
13 | 2531771.3773 | 1155813.5848 | 2531773.6194 | 1155813.0455
14 | 2531787.7977 | 1155725.9116 | 2531789.9511 | 1155738.8318
15 | 2531771.3773 | 1155813.5848 | 2531741.8355 | 1155820.6903
16 | 2531831.0462 | 1155851.5563 | 2531825.4217 | 1155852.6985
17 | 2531825.4217 | 1155852.6985 | 2531810.8136 | 1155855.6659
18 | 2531632.4789 | 1155690.341 | 2531653.8523 | 1155715.7268 | 2531654.9019 | 1155716.9711 | 2531656.449 | 1155718.799 | 2531658.4789 | 1155721.2551 | 2531655.8992 | 1155723.7302 | 2531637.7417 | 1155740.3571 | 2531626.1264 | 1155749.5388 | 2531625.2347 | 1155750.0381
19 | 2531557.6952 | 1155602.8696 | 2531608.4139 | 1155661.7582 | 2531632.4789 | 1155690.341
20 | 2531669.0461 | 1155768.9391 | 2531652.033 | 1155784.3523 | 2531625.2347 | 1155750.0381 | 2531625.2347 | 1155750.0381
21 | 2531538.7029 | 1155626.3545 | 2531540.8277 | 1155621.6499 | 2531548.9295 | 1155614.4314 | 2531556.4613 | 1155605.6519 | 2531557.6952 | 1155602.8696
22 | 2531687.0504 | 1155773.9039 | 2531669.0461 | 1155768.9391
23 | 2531482.6006 | 1155709.5067 | 2531491.8819 | 1155706.1879 | 2531506.2652 | 1155685.5014 | 2531536.856 | 1155628.5101 | 2531538.7029 | 1155626.3545
24 | 2531687.0504 | 1155773.9039 | 2531687.6024 | 1155776.487
25 | 2531690.2729 | 1155788.9848 | 2531687.6024 | 1155776.487
26 | 2531691.425 | 1155794.3766 | 2531690.2729 | 1155788.9848
27 | 2531789.1701 | 1155860.0557 | 2531790.9539 | 1155859.6939
28 | 2531810.8136 | 1155855.6659 | 2531790.9539 | 1155859.6939
29 | 2531780.6151 | 1155861.7908 | 2531789.1701 | 1155860.0557
30 | 2531810.8136 | 1155855.6659 | 2531806.8144 | 1155841.5346
31 | 2531780.6151 | 1155861.7908 | 2531771.7846 | 1155863.5818
32 | 2531762.8218 | 1155865.3996 | 2531771.7846 | 1155863.5818
33 | 2531751.0648 | 1155867.7842 | 2531762.8218 | 1155865.3996
34 | 2531753.947 | 1155875.2266 | 2531757.0357 | 1155883.2023
35 | 2531760.4891 | 1155892.1198 | 2531757.0357 | 1155883.2023
36 | 2531751.0648 | 1155867.7842 | 2531753.947 | 1155875.2266
37 | 2531751.0648 | 1155867.7842 | 2531744.7823 | 1155869.0563 | 2531733.4837 | 1155871.3498
38 | 2531732.3092 | 1155871.5882 | 2531733.4837 | 1155871.3498
39 | 2531732.3092 | 1155871.5882 | 2531729.5263 | 1155857.5343
40 | 2531732.3092 | 1155871.5882 | 2531721.9542 | 1155873.6907
41 | 2531676.075 | 1155883.949 | 2531673.7837 | 1155884.4995
42 | 2531676.075 | 1155883.949 | 2531683.5389 | 1155882.1555
43 | 2531664.9878 | 1155886.613 | 2531673.7837 | 1155884.4995
44 | 2531692.6242 | 1155879.9725 | 2531683.5389 | 1155882.1555
45 | 2531664.9878 | 1155886.613 | 2531654.2844 | 1155889.1849 | 2531649.2722 | 1155890.389
46 | 2531701.3943 | 1155877.8652 | 2531692.6242 | 1155879.9725
47 | 2531630.7257 | 1155894.8449 | 2531649.2722 | 1155890.389
48 | 2531701.3943 | 1155877.8652 | 2531703.0498 | 1155877.5291
49 | 2531701.3943 | 1155877.8652 | 2531699.5387 | 1155868.47 | 2531698.6746 | 1155865.3225 | 2531697.5581 | 1155859.3829
50 | 2531630.7257 | 1155894.8449 | 2531619.7353 | 1155897.5825
51 | 2531630.7257 | 1155894.8449 | 2531644.9627 | 1155923.4866
52 | 2531703.0498 | 1155877.5291 | 2531710.2525 | 1155876.0666
53 | 2531701.2926 | 1155840.5901 | 2531698.7759 | 1155845.2324 | 2531697.4767 | 1155851.0393 | 2531697.3275 | 1155858.1561 | 2531697.5581 | 1155859.3829
54 | 2531691.425 | 1155794.3766 | 2531712.4902 | 1155789.957 | 2531723.9704 | 1155783.0658
55 | 2531691.425 | 1155794.3766 | 2531693.1022 | 1155802.2299
56 | 2531731.0096 | 1155778.8404 | 2531723.9704 | 1155783.0658
57 | 2531695.6324 | 1155814.0775 | 2531693.1022 | 1155802.2299
58 | 2531698.3697 | 1155826.8949 | 2531695.6324 | 1155814.0775
59 | 2531701.2926 | 1155840.5901 | 2531699.421 | 1155831.8176 | 2531698.3697 | 1155826.8949
60 | 2531701.2926 | 1155840.5901 | 2531704.9242 | 1155835.5238 | 2531709.7822 | 1155832.4113 | 2531714.9426 | 1155829.5845 | 2531739.675 | 1155821.21 | 2531741.8355 | 1155820.6903
61 | 2531721.9542 | 1155873.6907 | 2531710.2525 | 1155876.0666
62 | 2531619.7353 | 1155897.5825 | 2531614.9708 | 1155868.4873
63 | 2531619.7353 | 1155897.5825 | 2531599.2861 | 1155902.6693
64 | 2531555.8861 | 1155913.9296 | 2531560.6921 | 1155912.3295 | 2531594.3969 | 1155903.8855 | 2531599.2861 | 1155902.6693
65 | 2531555.8861 | 1155913.9296 | 2531558.8784 | 1155916.7193
66 | 2531518.4176 | 1155908.4312 | 2531527.1064 | 1155908.3321 | 2531542.6745 | 1155908.855 | 2531546.0844 | 1155911.2731 | 2531548.2034 | 1155915.4957 | 2531555.8861 | 1155913.9296
67 | 2531586.5865 | 1155923.8633 | 2531581.7704 | 1155919.8715 | 2531564.7004 | 1155922.156 | 2531558.8784 | 1155916.7193
68 | 2531558.8784 | 1155916.7193 | 2531532.3192 | 1155925.6674
69 | 2531518.4176 | 1155908.4312 | 2531517.6688 | 1155903.9706
70 | 2531518.4176 | 1155908.4312 | 2531503.2401 | 1155905.1579 | 2531478.3457 | 1155895.9143
71 | 2531519.5682 | 1155929.9633 | 2531532.3192 | 1155925.6674

## bus_geodata
| x | y | coords
0 | 2531374.6904 | 1155731.3774
1 | 2531303.9411 | 1155871.7809
2 | 2531356.5978 | 1155898.8831
3 | 2531262.7113 | 1155846.8465
4 | 2531370.8364 | 1155906.5668
5 | 2531265.4899 | 1155758.5728
6 | 2531439.5697 | 1155941.1706
7 | 2531825.0168 | 1155804.5275
8 | 2531801.4174 | 1155807.657
9 | 2531794.7182 | 1155767.4389
10 | 2531786.4416 | 1155810.5547
11 | 2531792.0531 | 1155751.4441
12 | 2531773.6194 | 1155813.0455
13 | 2531789.9511 | 1155738.8318
14 | 2531771.3773 | 1155813.5848
15 | 2531831.0462 | 1155851.5563
16 | 2531825.4217 | 1155852.6985
17 | 2531632.4789 | 1155690.341
18 | 2531625.2347 | 1155750.0381
19 | 2531557.6952 | 1155602.8696
20 | 2531669.0461 | 1155768.9391
21 | 2531538.7029 | 1155626.3545
22 | 2531687.0504 | 1155773.9039
23 | 2531482.6006 | 1155709.5067
24 | 2531687.6024 | 1155776.487
25 | 2531690.2729 | 1155788.9848
26 | 2531787.7977 | 1155725.9116
27 | 2531790.9539 | 1155859.6939
28 | 2531789.1701 | 1155860.0557
29 | 2531810.8136 | 1155855.6659
30 | 2531780.6151 | 1155861.7908
31 | 2531806.8144 | 1155841.5346
32 | 2531771.7846 | 1155863.5818
33 | 2531762.8218 | 1155865.3996
34 | 2531757.0357 | 1155883.2023
35 | 2531753.947 | 1155875.2266
36 | 2531760.4891 | 1155892.1198
37 | 2531751.0648 | 1155867.7842
38 | 2531733.4837 | 1155871.3498
39 | 2531732.3092 | 1155871.5882
40 | 2531676.075 | 1155883.949
41 | 2531673.7837 | 1155884.4995
42 | 2531683.5389 | 1155882.1555
43 | 2531664.9878 | 1155886.613
44 | 2531692.6242 | 1155879.9725
45 | 2531649.2722 | 1155890.389
46 | 2531701.3943 | 1155877.8652
47 | 2531630.7257 | 1155894.8449
48 | 2531703.0498 | 1155877.5291
49 | 2531697.5581 | 1155859.3829
50 | 2531691.425 | 1155794.3766
51 | 2531723.9704 | 1155783.0658
52 | 2531693.1022 | 1155802.2299
53 | 2531731.0096 | 1155778.8404
54 | 2531695.6324 | 1155814.0775
55 | 2531698.3697 | 1155826.8949
56 | 2531701.2926 | 1155840.5901
57 | 2531741.8355 | 1155820.6903
58 | 2531710.2525 | 1155876.0666
59 | 2531721.9542 | 1155873.6907
60 | 2531619.7353 | 1155897.5825
61 | 2531644.9627 | 1155923.4866
62 | 2531614.9708 | 1155868.4873
63 | 2531599.2861 | 1155902.6693
64 | 2531555.8861 | 1155913.9296
65 | 2531729.5263 | 1155857.5343
66 | 2531558.8784 | 1155916.7193
67 | 2531518.4176 | 1155908.4312
68 | 2531586.5865 | 1155923.8633
69 | 2531532.3192 | 1155925.6674
70 | 2531517.6688 | 1155903.9706
71 | 2531478.3457 | 1155895.9143
72 | 2531519.5682 | 1155929.9633
73 | 2531619.7353 | 1155897.5825

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1