## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5642-37_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5642-37_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5642-37_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5642-37_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5642-37_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_5642-37_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_5642-37_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_5642-37_0_4_node_94 | 0.4 | n |  | TRUE
8 | bus_LV_5642-37_0_4_node_95 | 0.4 | n |  | TRUE
9 | bus_LV_5642-37_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_5642-37_0_4_node_54 | 0.4 | n |  | TRUE
11 | bus_LV_5642-37_0_4_node_61 | 0.4 | n |  | TRUE
12 | bus_LV_5642-37_0_4_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_5642-37_0_4_node_93 | 0.4 | n |  | TRUE
14 | bus_LV_5642-37_0_4_node_72 | 0.4 | n |  | TRUE
15 | bus_LV_5642-37_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_5642-37_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_5642-37_0_4_node_98 | 0.4 | n |  | TRUE
18 | bus_LV_5642-37_0_4_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_5642-37_0_4_node_78 | 0.4 | n |  | TRUE
20 | bus_LV_5642-37_0_4_node_87 | 0.4 | n |  | TRUE
21 | bus_LV_5642-37_0_4_node_86 | 0.4 | n |  | TRUE
22 | bus_LV_5642-37_0_4_node_58 | 0.4 | n |  | TRUE
23 | bus_LV_5642-37_0_4_node_55 | 0.4 | n |  | TRUE
24 | bus_LV_5642-37_0_4_node_85 | 0.4 | n |  | TRUE
25 | bus_LV_5642-37_0_4_node_70 | 0.4 | n |  | TRUE
26 | bus_LV_5642-37_0_4_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_5642-37_0_4_node_10 | 0.4 | n |  | TRUE
28 | bus_LV_5642-37_0_4_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_5642-37_0_4_node_12 | 0.4 | n |  | TRUE
30 | bus_LV_5642-37_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_5642-37_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_5642-37_0_4_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_5642-37_0_4_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_5642-37_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_5642-37_0_4_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_5642-37_0_4_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_5642-37_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_5642-37_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_5642-37_0_4_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_5642-37_0_4_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_5642-37_0_4_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_5642-37_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_5642-37_0_4_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_5642-37_0_4_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_5642-37_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_5642-37_0_4_node_92 | 0.4 | n |  | TRUE
47 | bus_LV_5642-37_0_4_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_5642-37_0_4_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_5642-37_0_4_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_5642-37_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_5642-37_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_5642-37_0_4_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_5642-37_0_4_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_5642-37_0_4_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_5642-37_0_4_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_5642-37_0_4_node_89 | 0.4 | n |  | TRUE
57 | bus_LV_5642-37_0_4_node_90 | 0.4 | n |  | TRUE
58 | bus_LV_5642-37_0_4_node_99 | 0.4 | n |  | TRUE
59 | bus_LV_5642-37_0_4_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_5642-37_0_4_node_40 | 0.4 | n |  | TRUE
61 | bus_LV_5642-37_0_4_node_41 | 0.4 | n |  | TRUE
62 | bus_LV_5642-37_0_4_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_5642-37_0_4_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_5642-37_0_4_node_44 | 0.4 | n |  | TRUE
65 | bus_LV_5642-37_0_4_node_45 | 0.4 | n |  | TRUE
66 | bus_LV_5642-37_0_4_node_91 | 0.4 | n |  | TRUE
67 | bus_LV_5642-37_0_4_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_5642-37_0_4_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_5642-37_0_4_node_49 | 0.4 | n |  | TRUE
70 | bus_LV_5642-37_0_4_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_5642-37_0_4_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_5642-37_0_4_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_5642-37_0_4_node_81 | 0.4 | n |  | TRUE
74 | bus_LV_5642-37_0_4_node_82 | 0.4 | n |  | TRUE
75 | bus_LV_5642-37_0_4_node_80 | 0.4 | n |  | TRUE
76 | bus_LV_5642-37_0_4_node_97 | 0.4 | n |  | TRUE
77 | bus_LV_5642-37_0_4_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_5642-37_0_4_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_5642-37_0_4_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_5642-37_0_4_node_62 | 0.4 | n |  | TRUE
81 | bus_LV_5642-37_0_4_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_5642-37_0_4_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_5642-37_0_4_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_5642-37_0_4_node_88 | 0.4 | n |  | TRUE
85 | bus_LV_5642-37_0_4_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_5642-37_0_4_node_96 | 0.4 | n |  | TRUE
87 | bus_LV_5642-37_0_4_node_67 | 0.4 | n |  | TRUE
88 | bus_LV_5642-37_0_4_node_68 | 0.4 | n |  | TRUE
89 | bus_LV_5642-37_0_4_node_65 | 0.4 | n |  | TRUE
90 | bus_LV_5642-37_0_4_node_71 | 0.4 | n |  | TRUE
91 | bus_LV_5642-37_0_4_node_73 | 0.4 | n |  | TRUE
92 | bus_LV_5642-37_0_4_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_5642-37_0_4_node_84 | 0.4 | n |  | TRUE
94 | bus_LV_5642-37_0_4_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_5642-37_0_4_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_5642-37_0_4_node_77 | 0.4 | n |  | TRUE
97 | bus_LV_5642-37_0_4_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_5642-37_0_4_node_83 | 0.4 | n |  | TRUE
99 | bus_MV_636_0_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5642-37_0_4_load_0 | 0 | 0.011423 | 0.0028628 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5642-37_0_4_load_6 | 5 | 0.01809 | 0.0045337 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5642-37_0_4_load_7 | 6 | 0.011504 | 0.0028832 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5642-37_0_4_load_94 | 7 | 0.0060074 | 0.0015056 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5642-37_0_4_load_54 | 10 | 0.0062945 | 0.0015776 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5642-37_0_4_load_56 | 12 | 0.0071567 | 0.0017936 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5642-37_0_4_load_93 | 13 | 0.0057856 | 0.00145 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5642-37_0_4_load_98 | 17 | 0.0058773 | 0.001473 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5642-37_0_4_load_51 | 18 | 0.0020801 | 0.00052132 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5642-37_0_4_load_86 | 21 | 0.0052337 | 0.0013117 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5642-37_0_4_load_58 | 22 | 0.001933 | 0.00048447 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5642-37_0_4_load_55 | 23 | 0.0021306 | 0.00053398 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5642-37_0_4_load_85 | 24 | 0.0013497 | 0.00033828 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5642-37_0_4_load_11 | 26 | 0.014368 | 0.0036008 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5642-37_0_4_load_13 | 28 | 0.00656 | 0.0016441 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5642-37_0_4_load_12 | 29 | 0.0067508 | 0.0016919 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5642-37_0_4_load_18 | 30 | 0.0061129 | 0.001532 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5642-37_0_4_load_17 | 31 | 0.035839 | 0.0089822 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5642-37_0_4_load_14 | 32 | 0.0062917 | 0.0015769 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5642-37_0_4_load_22 | 34 | 0.03584 | 0.0089824 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5642-37_0_4_load_29 | 36 | 0.0098912 | 0.002479 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5642-37_0_4_load_25 | 38 | 0.0059969 | 0.001503 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5642-37_0_4_load_20 | 40 | 0.025407 | 0.0063676 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5642-37_0_4_load_24 | 42 | 0.0044967 | 0.001127 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5642-37_0_4_load_26 | 43 | 0.0048965 | 0.0012272 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5642-37_0_4_load_27 | 44 | 0.0046487 | 0.0011651 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5642-37_0_4_load_92 | 46 | 0.0055411 | 0.0013887 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5642-37_0_4_load_39 | 48 | 0.0056613 | 0.0014189 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5642-37_0_4_load_31 | 50 | 0.00363 | 0.00090978 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5642-37_0_4_load_32 | 51 | 0.0038217 | 0.00095781 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5642-37_0_4_load_35 | 53 | 0.0068775 | 0.0017237 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5642-37_0_4_load_38 | 55 | 0.0066417 | 0.0016646 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5642-37_0_4_load_89 | 56 | 0.0069967 | 0.0017535 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5642-37_0_4_load_99 | 58 | 0.0032774 | 0.0008214 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5642-37_0_4_load_40 | 60 | 0.0044546 | 0.0011164 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5642-37_0_4_load_43 | 63 | 0.0030362 | 0.00076094 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5642-37_0_4_load_44 | 64 | 0.0057544 | 0.0014422 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5642-37_0_4_load_45 | 65 | 0.0035981 | 0.00090177 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5642-37_0_4_load_91 | 66 | 0.010368 | 0.0025984 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5642-37_0_4_load_47 | 67 | 0.0067491 | 0.0016915 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5642-37_0_4_load_49 | 69 | 0.0048144 | 0.0012066 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5642-37_0_4_load_53 | 72 | 0.0032248 | 0.00080822 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5642-37_0_4_load_81 | 73 | 0.0036759 | 0.00092126 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5642-37_0_4_load_82 | 74 | 0.00085524 | 0.00021434 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5642-37_0_4_load_80 | 75 | 0.0048673 | 0.0012199 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5642-37_0_4_load_97 | 76 | 0.0030235 | 0.00075775 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5642-37_0_4_load_59 | 78 | 0.0020555 | 0.00051516 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5642-37_0_4_load_62 | 80 | 0.0023477 | 0.00058839 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5642-37_0_4_load_64 | 83 | 0.0013058 | 0.00032727 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5642-37_0_4_load_88 | 84 | 0.0019721 | 0.00049425 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5642-37_0_4_load_96 | 86 | 0.0027489 | 0.00068893 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5642-37_0_4_load_67 | 87 | 0.0048162 | 0.0012071 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5642-37_0_4_load_65 | 89 | 0.0018201 | 0.00045616 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5642-37_0_4_load_73 | 91 | 0.0016241 | 0.00040703 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5642-37_0_4_load_69 | 92 | 0.00095011 | 0.00023812 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5642-37_0_4_load_84 | 93 | 0.0019707 | 0.0004939 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5642-37_0_4_load_74 | 94 | 0.0020767 | 0.00052048 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5642-37_0_4_load_77 | 96 | 0.0024519 | 0.0006145 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5642-37_0_4_load_83 | 98 | 0.0021917 | 0.00054929 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5642-37_0_4_line_0 |  | 0 | 1 | 0.026861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_5642-37_0_4_line_1 |  | 0 | 2 | 0.01345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_5642-37_0_4_line_2 |  | 1 | 3 | 0.030472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5642-37_0_4_line_3 |  | 1 | 4 | 0.042289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_5642-37_0_4_line_4 |  | 2 | 5 | 0.031462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_5642-37_0_4_line_5 |  | 2 | 6 | 0.0022801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5642-37_0_4_line_6 |  | 3 | 7 | 0.018544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5642-37_0_4_line_7 |  | 3 | 8 | 0.019671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5642-37_0_4_line_8 |  | 4 | 13 | 0.025269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5642-37_0_4_line_9 |  | 4 | 14 | 0.035855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_5642-37_0_4_line_10 |  | 5 | 15 | 0.024429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_5642-37_0_4_line_11 |  | 6 | 16 | 0.037108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5642-37_0_4_line_12 |  | 8 | 17 | 0.025823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5642-37_0_4_line_13 |  | 9 | 10 | 0.019523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5642-37_0_4_line_14 |  | 9 | 11 | 0.090866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5642-37_0_4_line_15 |  | 9 | 12 | 0.023509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5642-37_0_4_line_16 |  | 10 | 18 | 0.018562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5642-37_0_4_line_17 |  | 11 | 19 | 0.065396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5642-37_0_4_line_18 |  | 11 | 20 | 0.075759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5642-37_0_4_line_19 |  | 11 | 21 | 0.010565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5642-37_0_4_line_20 |  | 12 | 22 | 0.019524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5642-37_0_4_line_21 |  | 12 | 23 | 0.031985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5642-37_0_4_line_22 |  | 14 | 24 | 0.023474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5642-37_0_4_line_23 |  | 14 | 25 | 0.079547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_5642-37_0_4_line_24 |  | 15 | 26 | 0.062869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_5642-37_0_4_line_25 |  | 16 | 27 | 0.022085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5642-37_0_4_line_26 |  | 18 | 68 | 0.039607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5642-37_0_4_line_27 |  | 19 | 84 | 0.014221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5642-37_0_4_line_28 |  | 19 | 85 | 0.037658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5642-37_0_4_line_29 |  | 20 | 86 | 0.018782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5642-37_0_4_line_30 |  | 23 | 77 | 0.00092453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5642-37_0_4_line_31 |  | 24 | 93 | 0.0045383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5642-37_0_4_line_32 |  | 25 | 92 | 0.026931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_5642-37_0_4_line_33 |  | 26 | 29 | 0.010521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_5642-37_0_4_line_34 |  | 27 | 28 | 0.024332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5642-37_0_4_line_35 |  | 28 | 32 | 0.015998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5642-37_0_4_line_36 |  | 29 | 30 | 0.016007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_5642-37_0_4_line_37 |  | 30 | 31 | 0.039723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_5642-37_0_4_line_38 |  | 31 | 36 | 0.088536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5642-37_0_4_line_39 |  | 31 | 35 | 0.046016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5642-37_0_4_line_40 |  | 33 | 34 | 0.033867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5642-37_0_4_line_41 |  | 33 | 35 | 0.043357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5642-37_0_4_line_42 |  | 36 | 37 | 0.019496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5642-37_0_4_line_43 |  | 37 | 45 | 0.009494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5642-37_0_4_line_44 |  | 37 | 44 | 0.0090571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5642-37_0_4_line_45 |  | 38 | 39 | 0.019053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5642-37_0_4_line_46 |  | 39 | 43 | 0.012122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5642-37_0_4_line_47 |  | 39 | 41 | 0.015047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5642-37_0_4_line_48 |  | 40 | 41 | 0.0061318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5642-37_0_4_line_49 |  | 41 | 42 | 0.018839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5642-37_0_4_line_50 |  | 43 | 44 | 0.0084626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5642-37_0_4_line_51 |  | 45 | 46 | 0.009359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5642-37_0_4_line_52 |  | 45 | 47 | 0.015829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5642-37_0_4_line_53 |  | 47 | 48 | 0.01109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5642-37_0_4_line_54 |  | 47 | 49 | 0.007449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5642-37_0_4_line_55 |  | 49 | 53 | 0.019495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5642-37_0_4_line_56 |  | 49 | 50 | 0.010693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5642-37_0_4_line_57 |  | 50 | 51 | 0.010342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5642-37_0_4_line_58 |  | 51 | 52 | 0.0080117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5642-37_0_4_line_59 |  | 52 | 54 | 0.002927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5642-37_0_4_line_60 |  | 52 | 55 | 0.019487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5642-37_0_4_line_61 |  | 54 | 56 | 0.020504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5642-37_0_4_line_62 |  | 54 | 57 | 0.030702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5642-37_0_4_line_63 |  | 57 | 58 | 0.016948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5642-37_0_4_line_64 |  | 57 | 59 | 0.001294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5642-37_0_4_line_65 |  | 59 | 66 | 0.020125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5642-37_0_4_line_66 |  | 59 | 62 | 0.027414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5642-37_0_4_line_67 |  | 60 | 61 | 0.062537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5642-37_0_4_line_68 |  | 60 | 62 | 0.010778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5642-37_0_4_line_69 |  | 61 | 63 | 0.010428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5642-37_0_4_line_70 |  | 61 | 64 | 0.023161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5642-37_0_4_line_71 |  | 62 | 65 | 0.016587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5642-37_0_4_line_72 |  | 67 | 68 | 0.017591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5642-37_0_4_line_73 |  | 67 | 69 | 0.0035528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5642-37_0_4_line_74 |  | 68 | 70 | 0.019398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5642-37_0_4_line_75 |  | 70 | 71 | 0.016349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5642-37_0_4_line_76 |  | 70 | 72 | 0.023427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5642-37_0_4_line_77 |  | 71 | 73 | 0.02278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5642-37_0_4_line_78 |  | 71 | 74 | 0.013506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5642-37_0_4_line_79 |  | 72 | 75 | 0.013875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5642-37_0_4_line_80 |  | 73 | 76 | 0.034585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5642-37_0_4_line_81 |  | 77 | 78 | 0.023764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5642-37_0_4_line_82 |  | 77 | 79 | 0.034057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5642-37_0_4_line_83 |  | 79 | 80 | 0.027358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5642-37_0_4_line_84 |  | 79 | 81 | 0.007609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_5642-37_0_4_line_85 |  | 81 | 82 | 0.019954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5642-37_0_4_line_86 |  | 81 | 83 | 0.011384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_5642-37_0_4_line_87 |  | 82 | 87 | 0.02174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5642-37_0_4_line_88 |  | 82 | 88 | 0.018203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_5642-37_0_4_line_89 |  | 83 | 89 | 0.0031067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5642-37_0_4_line_90 |  | 85 | 96 | 0.015628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5642-37_0_4_line_91 |  | 85 | 94 | 0.023962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5642-37_0_4_line_92 |  | 88 | 90 | 0.051126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_5642-37_0_4_line_93 |  | 88 | 91 | 0.012524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5642-37_0_4_line_94 |  | 90 | 92 | 0.017947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_5642-37_0_4_line_95 |  | 94 | 95 | 0.00813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5642-37_0_4_line_96 |  | 95 | 97 | 0.028129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5642-37_0_4_line_97 |  | 97 | 98 | 0.016305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5642-37_0_4_trafo_11 | 0.63 MVA 20/0.4 kV | 99 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2526401.0779 | 1151632.9864 | 2526407.5096 | 1151627.9493 | 2526415.7639 | 1151621.3113 | 2526422.0389 | 1151616.1912
1 | 2526432.4601 | 1151607.6882 | 2526422.0389 | 1151616.1912
2 | 2526379.0799 | 1151617.3024 | 2526388.5517 | 1151627.9813 | 2526392.3098 | 1151632.1377 | 2526392.7322 | 1151631.5322 | 2526394.545 | 1151630.3871 | 2526396.6593 | 1151630.0499 | 2526398.738 | 1151630.5692 | 2526400.4425 | 1151631.8713 | 2526401.0779 | 1151632.9864
3 | 2526401.0779 | 1151632.9864 | 2526401.4939 | 1151633.7373 | 2526401.7381 | 1151635.502 | 2526401.3909 | 1151637.2405 | 2526400.4733 | 1151638.7749 | 2526399.6303 | 1151639.5078 | 2526403.1677 | 1151643.1888 | 2526423.1575 | 1151665.379
4 | 2526432.4601 | 1151607.6882 | 2526431.5611 | 1151576.2393
5 | 2526432.4601 | 1151607.6882 | 2526434.228 | 1151606.2482
6 | 2526379.0799 | 1151617.3024 | 2526365.0758 | 1151629.5029
7 | 2526365.944 | 1151602.6327 | 2526369.0787 | 1151606.0184 | 2526379.0799 | 1151617.3024
8 | 2526423.1575 | 1151665.379 | 2526403.1691 | 1151680.9101
9 | 2526423.1575 | 1151665.379 | 2526445.6325 | 1151689.9623 | 2526447.2689 | 1151691.9657
10 | 2526430.863 | 1151551.8207 | 2526431.5611 | 1151576.2393
11 | 2526463.2454 | 1151583.1312 | 2526454.1399 | 1151590.4689 | 2526449.78 | 1151593.5907 | 2526444.5437 | 1151597.846 | 2526440.303 | 1151601.2998 | 2526434.228 | 1151606.2482
12 | 2526365.944 | 1151602.6327 | 2526349.0459 | 1151616.6809 | 2526346.4468 | 1151613.7888
13 | 2526338.0805 | 1151682.6746 | 2526324.4229 | 1151668.7234
14 | 2526270.0097 | 1151709.1347 | 2526276.2484 | 1151715.9065 | 2526285.4044 | 1151725.8665 | 2526312.2908 | 1151704.5584 | 2526338.0805 | 1151682.6746
15 | 2526338.0805 | 1151682.6746 | 2526344.8205 | 1151690.2741 | 2526353.7462 | 1151700.237
16 | 2526324.4229 | 1151668.7234 | 2526311.4376 | 1151655.4589
17 | 2526270.0097 | 1151709.1347 | 2526276.2484 | 1151715.9065 | 2526285.4044 | 1151725.8665 | 2526314.394 | 1151757.1622
18 | 2526270.0097 | 1151709.1347 | 2526246.8279 | 1151683.9269 | 2526238.9088 | 1151675.3192 | 2526218.7218 | 1151653.3767
19 | 2526270.0097 | 1151709.1347 | 2526280.4471 | 1151707.4943
20 | 2526353.7462 | 1151700.237 | 2526339.068 | 1151713.1574
21 | 2526353.7462 | 1151700.237 | 2526375.0893 | 1151724.0601
22 | 2526447.2689 | 1151691.9657 | 2526429.304 | 1151707.0751
23 | 2526447.2689 | 1151691.9657 | 2526451.4451 | 1151697.0508 | 2526456.1043 | 1151702.7192 | 2526482.0092 | 1151731.0074 | 2526485.2375 | 1151734.5254 | 2526491.7037 | 1151741.7282 | 2526500.2708 | 1151751.2622
24 | 2526430.863 | 1151551.8207 | 2526406.9539 | 1151493.6754
25 | 2526475.1025 | 1151573.592 | 2526476.2077 | 1151576.7247 | 2526476.056 | 1151579.3836 | 2526475.6266 | 1151580.6785 | 2526473.8233 | 1151583.2242 | 2526471.279 | 1151584.8006 | 2526468.6523 | 1151585.2886 | 2526466.8923 | 1151585.0989 | 2526464.4312 | 1151584.0728 | 2526463.2454 | 1151583.1312
26 | 2526284.0446 | 1151626.8718 | 2526287.5887 | 1151631.0974 | 2526311.4376 | 1151655.4589
27 | 2526314.394 | 1151757.1622 | 2526324.3838 | 1151747.0403
28 | 2526314.394 | 1151757.1622 | 2526335.2926 | 1151780.864 | 2526339.301 | 1151785.4064
29 | 2526225.96 | 1151640.2694 | 2526229.0842 | 1151643.4217 | 2526218.7218 | 1151653.3767
30 | 2526375.0893 | 1151724.0601 | 2526375.7062 | 1151724.7487
31 | 2526425.8308 | 1151709.9963 | 2526429.304 | 1151707.0751
32 | 2526500.2708 | 1151751.2622 | 2526479.5712 | 1151768.4909
33 | 2526415.3481 | 1151487.3323 | 2526406.9539 | 1151493.6754
34 | 2526475.1025 | 1151573.592 | 2526483.4504 | 1151566.4415 | 2526493.891 | 1151558.137
35 | 2526493.891 | 1151558.137 | 2526506.4113 | 1151548.1783
36 | 2526415.3481 | 1151487.3323 | 2526428.1192 | 1151477.6817
37 | 2526459.8114 | 1151453.7332 | 2526428.1192 | 1151477.6817
38 | 2526393.4526 | 1151395.1235 | 2526459.8114 | 1151453.7332
39 | 2526496.4067 | 1151425.8373 | 2526483.6477 | 1151435.721 | 2526459.8114 | 1151453.7332
40 | 2526509.0629 | 1151467.8174 | 2526512.0828 | 1151462.4441 | 2526526.4249 | 1151451.4627 | 2526529.8941 | 1151453.9662 | 2526532.8708 | 1151449.4495
41 | 2526532.8708 | 1151449.4495 | 2526496.4067 | 1151425.8373
42 | 2526378.7118 | 1151382.3189 | 2526393.4526 | 1151395.1235
43 | 2526378.7118 | 1151382.3189 | 2526372.6532 | 1151389.6417
44 | 2526378.7118 | 1151382.3189 | 2526384.4874 | 1151375.3423
45 | 2526397.614 | 1151359.4858 | 2526412.6564 | 1151371.2306
46 | 2526397.614 | 1151359.4858 | 2526389.8839 | 1151368.8235
47 | 2526407.2202 | 1151347.884 | 2526397.614 | 1151359.4858
48 | 2526407.2202 | 1151347.884 | 2526412.2826 | 1151351.3439
49 | 2526407.2202 | 1151347.884 | 2526400.3591 | 1151342.9541 | 2526392.1238 | 1151337.385 | 2526391.7648 | 1151337.1155
50 | 2526384.4874 | 1151375.3423 | 2526389.8839 | 1151368.8235
51 | 2526372.6532 | 1151389.6417 | 2526365.2902 | 1151383.8397
52 | 2526362.5247 | 1151401.8281 | 2526372.6532 | 1151389.6417
53 | 2526362.5247 | 1151401.8281 | 2526353.7901 | 1151394.9645
54 | 2526357.7903 | 1151407.5893 | 2526362.5247 | 1151401.8281
55 | 2526357.7903 | 1151407.5893 | 2526373.2344 | 1151419.5403
56 | 2526357.7903 | 1151407.5893 | 2526350.9711 | 1151415.8254
57 | 2526350.9711 | 1151415.8254 | 2526344.3759 | 1151423.7911
58 | 2526339.2666 | 1151429.9621 | 2526344.3759 | 1151423.7911
59 | 2526337.3983 | 1151432.2196 | 2526339.2666 | 1151429.9621
60 | 2526320.601 | 1151433.237 | 2526322.3646 | 1151434.3382 | 2526339.2666 | 1151429.9621
61 | 2526337.3983 | 1151432.2196 | 2526353.2777 | 1151445.2435
62 | 2526337.3983 | 1151432.2196 | 2526317.8008 | 1151455.8952
63 | 2526301.2778 | 1151456.7425 | 2526302.6647 | 1151457.7928 | 2526317.8008 | 1151455.8952
64 | 2526316.9764 | 1151456.8947 | 2526317.8008 | 1151455.8952
65 | 2526316.9764 | 1151456.8947 | 2526332.7805 | 1151469.4082
66 | 2526316.9764 | 1151456.8947 | 2526299.4741 | 1151478.0322
67 | 2526260.7846 | 1151531.4921 | 2526268.9655 | 1151527.0115 | 2526287.372 | 1151517.0358 | 2526291.2206 | 1151511.6523 | 2526293.7238 | 1151501.0934 | 2526292.5987 | 1151486.3322
68 | 2526299.4741 | 1151478.0322 | 2526292.5987 | 1151486.3322
69 | 2526260.7846 | 1151531.4921 | 2526253.387 | 1151524.1231
70 | 2526239.0497 | 1151538.5626 | 2526251.1781 | 1151536.7684 | 2526260.7846 | 1151531.4921
71 | 2526296.7189 | 1151462.4127 | 2526298.2331 | 1151463.2057 | 2526299.4741 | 1151478.0322
72 | 2526284.0446 | 1151626.8718 | 2526297.8885 | 1151616.0183
73 | 2526301.3805 | 1151615.364 | 2526297.8885 | 1151616.0183
74 | 2526284.0446 | 1151626.8718 | 2526271.9992 | 1151611.6442
75 | 2526261.5443 | 1151599.0542 | 2526271.9992 | 1151611.6442
76 | 2526271.9992 | 1151611.6442 | 2526255.1845 | 1151627.9571
77 | 2526261.5443 | 1151599.0542 | 2526270.0151 | 1151591.3015 | 2526272.5508 | 1151589.0247 | 2526273.5346 | 1151587.8898 | 2526273.7711 | 1151586.5195 | 2526273.0575 | 1151584.6605 | 2526271.3992 | 1151582.1238
78 | 2526261.5443 | 1151599.0542 | 2526252.4734 | 1151589.0473
79 | 2526247.8678 | 1151639.189 | 2526249.4485 | 1151633.5219 | 2526255.1845 | 1151627.9571
80 | 2526271.3992 | 1151582.1238 | 2526294.1369 | 1151556.0638
81 | 2526375.7062 | 1151724.7487 | 2526357.6209 | 1151740.2232
82 | 2526398.4598 | 1151750.14 | 2526375.7062 | 1151724.7487
83 | 2526398.4598 | 1151750.14 | 2526380.7922 | 1151766.5099 | 2526377.8943 | 1151764.9001
84 | 2526403.5412 | 1151755.8144 | 2526398.4598 | 1151750.14
85 | 2526403.5412 | 1151755.8144 | 2526416.8711 | 1151770.693
86 | 2526403.5412 | 1151755.8144 | 2526411.5541 | 1151748.2787 | 2526411.7087 | 1151747.9265
87 | 2526416.8711 | 1151770.693 | 2526400.5846 | 1151785.1448
88 | 2526416.8711 | 1151770.693 | 2526429.0336 | 1151784.2629
89 | 2526412.9579 | 1151745.082 | 2526411.7087 | 1151747.9265
90 | 2526339.301 | 1151785.4064 | 2526351.1826 | 1151775.2538
91 | 2526339.301 | 1151785.4064 | 2526355.3702 | 1151803.181
92 | 2526429.0336 | 1151784.2629 | 2526442.9704 | 1151799.8235 | 2526465.7918 | 1151779.9888
93 | 2526429.0336 | 1151784.2629 | 2526435.1923 | 1151778.8735 | 2526438.1372 | 1151782.0614
94 | 2526465.7918 | 1151779.9888 | 2526466.5968 | 1151779.2896 | 2526479.5712 | 1151768.4909
95 | 2526360.8224 | 1151809.2118 | 2526355.3702 | 1151803.181
96 | 2526360.8224 | 1151809.2118 | 2526368.8645 | 1151818.4852 | 2526379.2499 | 1151830.4648
97 | 2526379.2499 | 1151830.4648 | 2526386.3666 | 1151827.476 | 2526391.17 | 1151824.2377 | 2526392.9955 | 1151822.2586 | 2526393.0727 | 1151822.1931

## bus_geodata
| x | y | coords
0 | 2526422.0389 | 1151616.1912
1 | 2526401.0779 | 1151632.9864
2 | 2526432.4601 | 1151607.6882
3 | 2526379.0799 | 1151617.3024
4 | 2526423.1575 | 1151665.379
5 | 2526431.5611 | 1151576.2393
6 | 2526434.228 | 1151606.2482
7 | 2526365.0758 | 1151629.5029
8 | 2526365.944 | 1151602.6327
9 | 2526338.0805 | 1151682.6746
10 | 2526324.4229 | 1151668.7234
11 | 2526270.0097 | 1151709.1347
12 | 2526353.7462 | 1151700.237
13 | 2526403.169 | 1151680.9101
14 | 2526447.2689 | 1151691.9657
15 | 2526430.863 | 1151551.8207
16 | 2526463.2454 | 1151583.1312
17 | 2526346.4468 | 1151613.7888
18 | 2526311.4376 | 1151655.4589
19 | 2526314.394 | 1151757.1622
20 | 2526218.7218 | 1151653.3767
21 | 2526280.4471 | 1151707.4943
22 | 2526339.068 | 1151713.1574
23 | 2526375.0893 | 1151724.0601
24 | 2526429.304 | 1151707.0751
25 | 2526500.2708 | 1151751.2622
26 | 2526406.9539 | 1151493.6754
27 | 2526475.1025 | 1151573.592
28 | 2526493.891 | 1151558.137
29 | 2526415.3481 | 1151487.3323
30 | 2526428.1192 | 1151477.6817
31 | 2526459.8114 | 1151453.7332
32 | 2526506.4113 | 1151548.1783
33 | 2526532.8708 | 1151449.4495
34 | 2526509.0629 | 1151467.8174
35 | 2526496.4067 | 1151425.8373
36 | 2526393.4526 | 1151395.1235
37 | 2526378.7118 | 1151382.3189
38 | 2526412.6564 | 1151371.2306
39 | 2526397.614 | 1151359.4858
40 | 2526412.2827 | 1151351.3439
41 | 2526407.2202 | 1151347.884
42 | 2526391.7648 | 1151337.1155
43 | 2526389.8839 | 1151368.8235
44 | 2526384.4874 | 1151375.3423
45 | 2526372.6532 | 1151389.6417
46 | 2526365.2902 | 1151383.8397
47 | 2526362.5247 | 1151401.8281
48 | 2526353.7901 | 1151394.9645
49 | 2526357.7903 | 1151407.5893
50 | 2526350.9711 | 1151415.8254
51 | 2526344.3759 | 1151423.7911
52 | 2526339.2666 | 1151429.9621
53 | 2526373.2344 | 1151419.5403
54 | 2526337.3983 | 1151432.2196
55 | 2526320.601 | 1151433.237
56 | 2526353.2777 | 1151445.2435
57 | 2526317.8008 | 1151455.8952
58 | 2526301.2778 | 1151456.7425
59 | 2526316.9764 | 1151456.8947
60 | 2526292.5987 | 1151486.3322
61 | 2526260.7846 | 1151531.4921
62 | 2526299.4741 | 1151478.0322
63 | 2526253.387 | 1151524.1231
64 | 2526239.0497 | 1151538.5626
65 | 2526296.7189 | 1151462.4127
66 | 2526332.7805 | 1151469.4082
67 | 2526297.8885 | 1151616.0183
68 | 2526284.0446 | 1151626.8718
69 | 2526301.3805 | 1151615.364
70 | 2526271.9992 | 1151611.6442
71 | 2526261.5443 | 1151599.0542
72 | 2526255.1845 | 1151627.9571
73 | 2526271.3992 | 1151582.1238
74 | 2526252.4734 | 1151589.0473
75 | 2526247.8678 | 1151639.189
76 | 2526294.1369 | 1151556.0638
77 | 2526375.7062 | 1151724.7487
78 | 2526357.6209 | 1151740.2232
79 | 2526398.4598 | 1151750.14
80 | 2526377.8943 | 1151764.9001
81 | 2526403.5412 | 1151755.8144
82 | 2526416.8711 | 1151770.693
83 | 2526411.7087 | 1151747.9265
84 | 2526324.3838 | 1151747.0403
85 | 2526339.301 | 1151785.4064
86 | 2526225.96 | 1151640.2694
87 | 2526400.5846 | 1151785.1448
88 | 2526429.0336 | 1151784.2629
89 | 2526412.9579 | 1151745.082
90 | 2526465.7918 | 1151779.9888
91 | 2526438.1372 | 1151782.0614
92 | 2526479.5712 | 1151768.4909
93 | 2526425.8308 | 1151709.9963
94 | 2526355.3702 | 1151803.181
95 | 2526360.8224 | 1151809.2118
96 | 2526351.1826 | 1151775.2538
97 | 2526379.2499 | 1151830.4648
98 | 2526393.0727 | 1151822.1931
99 | 2526430.863 | 1151551.8207

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1