## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5643-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5643-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5643-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5643-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5643-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5643-3_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_5643-3_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_5643-3_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_5643-3_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5643-3_0_4_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_5643-3_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_5643-3_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_5643-3_0_4_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_5643-3_0_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_5643-3_0_4_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_5643-3_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_5643-3_0_4_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_5643-3_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_5643-3_0_4_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_5643-3_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_5643-3_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_5643-3_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_5643-3_0_4_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_5643-3_0_4_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_5643-3_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_5643-3_0_4_node_40 | 0.4 | n |  | TRUE
26 | bus_LV_5643-3_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_5643-3_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_5643-3_0_4_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_5643-3_0_4_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_5643-3_0_4_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_5643-3_0_4_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_5643-3_0_4_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_5643-3_0_4_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_5643-3_0_4_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_5643-3_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_5643-3_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_5643-3_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_5643-3_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_5643-3_0_4_node_32 | 0.4 | n |  | TRUE
40 | bus_MV_451_1_node_106 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5643-3_0_4_load_0 | 0 | 0.028762 | 0.0072084 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5643-3_0_4_load_2 | 2 | 0.023739 | 0.0059496 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5643-3_0_4_load_4 | 4 | 0.023739 | 0.0059494 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5643-3_0_4_load_10 | 6 | 0.024163 | 0.0060557 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5643-3_0_4_load_9 | 7 | 0.023822 | 0.0059703 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5643-3_0_4_load_15 | 9 | 0.012952 | 0.003246 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5643-3_0_4_load_34 | 12 | 0.033571 | 0.0084138 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5643-3_0_4_load_17 | 17 | 0.025239 | 0.0063254 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5643-3_0_4_load_35 | 18 | 0.017551 | 0.0043987 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5643-3_0_4_load_11 | 20 | 0.013488 | 0.0033805 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5643-3_0_4_load_13 | 21 | 0.013602 | 0.003409 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5643-3_0_4_load_25 | 22 | 0.010028 | 0.0025134 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5643-3_0_4_load_24 | 23 | 0.048596 | 0.012179 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5643-3_0_4_load_40 | 25 | 0.019815 | 0.0049661 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5643-3_0_4_load_37 | 28 | 0.020278 | 0.0050822 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5643-3_0_4_load_38 | 29 | 0.020954 | 0.0052516 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5643-3_0_4_load_39 | 30 | 0.022896 | 0.0057382 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5643-3_0_4_load_36 | 31 | 0.019592 | 0.0049102 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5643-3_0_4_load_33 | 32 | 0.0021236 | 0.00053223 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5643-3_0_4_load_26 | 33 | 0.0010856 | 0.00027208 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5643-3_0_4_load_27 | 34 | 0.0010277 | 0.00025756 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5643-3_0_4_load_29 | 37 | 0.0012086 | 0.00030291 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5643-3_0_4_load_32 | 39 | 0.00070244 | 0.00017605 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5643-3_0_4_line_0 |  | 0 | 1 | 0.041344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5643-3_0_4_line_1 |  | 0 | 2 | 0.038214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5643-3_0_4_line_2 |  | 1 | 3 | 0.028373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5643-3_0_4_line_3 |  | 1 | 4 | 0.026221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_5643-3_0_4_line_4 |  | 1 | 5 | 0.086947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_5643-3_0_4_line_5 |  | 3 | 6 | 0.068629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5643-3_0_4_line_6 |  | 3 | 7 | 0.018969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5643-3_0_4_line_7 |  | 4 | 8 | 0.0622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_5643-3_0_4_line_8 |  | 5 | 9 | 0.093932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_5643-3_0_4_line_9 |  | 8 | 10 | 0.16122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_5643-3_0_4_line_10 |  | 9 | 11 | 0.070881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_5643-3_0_4_line_11 |  | 10 | 12 | 0.009064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5643-3_0_4_line_12 |  | 10 | 13 | 0.004173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_5643-3_0_4_line_13 |  | 11 | 14 | 0.071395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_5643-3_0_4_line_14 |  | 13 | 15 | 0.13874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_5643-3_0_4_line_15 |  | 13 | 16 | 0.071487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5643-3_0_4_line_16 |  | 13 | 17 | 0.054735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5643-3_0_4_line_17 |  | 14 | 18 | 0.008185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5643-3_0_4_line_18 |  | 14 | 19 | 0.005544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5643-3_0_4_line_19 |  | 15 | 22 | 0.0024207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_5643-3_0_4_line_20 |  | 15 | 23 | 0.022774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5643-3_0_4_line_21 |  | 16 | 28 | 0.009359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5643-3_0_4_line_22 |  | 16 | 29 | 0.005834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5643-3_0_4_line_23 |  | 16 | 26 | 0.051055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5643-3_0_4_line_24 |  | 19 | 20 | 0.024397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5643-3_0_4_line_25 |  | 20 | 21 | 0.039194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5643-3_0_4_line_26 |  | 24 | 25 | 0.005089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5643-3_0_4_line_27 |  | 24 | 26 | 0.048401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5643-3_0_4_line_28 |  | 24 | 27 | 0.006505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5643-3_0_4_line_29 |  | 26 | 30 | 0.025055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5643-3_0_4_line_30 |  | 27 | 31 | 0.006884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5643-3_0_4_line_31 |  | 30 | 32 | 0.35211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5643-3_0_4_line_32 |  | 32 | 39 | 0.016443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5643-3_0_4_line_33 |  | 33 | 34 | 0.029418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5643-3_0_4_line_34 |  | 34 | 35 | 0.031283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5643-3_0_4_line_35 |  | 35 | 36 | 0.16447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5643-3_0_4_line_36 |  | 36 | 37 | 0.034852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5643-3_0_4_line_37 |  | 37 | 38 | 0.0054037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5643-3_0_4_line_38 |  | 38 | 39 | 0.0017993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5643-3_0_4_trafo_25 | 0.63 MVA 20/0.4 kV | 40 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2530863.8673 | 1151885.2457 | 2530890.4888 | 1151873.6332 | 2530886.9887 | 1151861.842
1 | 2530882.7815 | 1151826.1065 | 2530878.4484 | 1151833.0713 | 2530886.9887 | 1151861.842
2 | 2530863.8673 | 1151885.2457 | 2530858.3427 | 1151882.6966 | 2530848.4041 | 1151862.7221
3 | 2530863.8673 | 1151885.2457 | 2530864.6658 | 1151879.9335 | 2530857.8447 | 1151863.425 | 2530856.5705 | 1151860.7236
4 | 2530812.4806 | 1151910.3395 | 2530816.4396 | 1151915.5635 | 2530821.8483 | 1151922.7163 | 2530870.6223 | 1151902.6777 | 2530863.8673 | 1151885.2457
5 | 2530809.3358 | 1151831.8432 | 2530811.2625 | 1151825.8622 | 2530815.8068 | 1151822.5858 | 2530823.8669 | 1151822.0261 | 2530831.2553 | 1151826.4658 | 2530848.4041 | 1151862.7221
6 | 2530848.4041 | 1151862.7221 | 2530829.8285 | 1151866.5656
7 | 2530830.0351 | 1151804.4677 | 2530856.5705 | 1151860.7236
8 | 2530812.4806 | 1151910.3395 | 2530780.179 | 1151854.558 | 2530772.5849 | 1151844.929 | 2530764.4125 | 1151838.3972 | 2530757.6694 | 1151838.6507
9 | 2530830.0351 | 1151804.4677 | 2530834.2712 | 1151803.0848 | 2530972.0436 | 1151743.3465 | 2530977.4365 | 1151747.7871
10 | 2530686.8354 | 1151839.258 | 2530715.3826 | 1151840.2407 | 2530757.6694 | 1151838.6507
11 | 2530975.0106 | 1151739.0545 | 2530977.4365 | 1151747.7871
12 | 2530976.6085 | 1151751.8766 | 2530977.4365 | 1151747.7871
13 | 2530686.8354 | 1151839.258 | 2530687.7486 | 1151846.5626 | 2530687.8764 | 1151857.6451 | 2530689.2838 | 1151871.2031 | 2530691.554 | 1151881.7161 | 2530697.3745 | 1151888.6195 | 2530702.9825 | 1151893.7355 | 2530703.7006 | 1151894.1163 | 2530706.5888 | 1151895.6505 | 2530708.9242 | 1151898.503 | 2530710.9769 | 1151902.1369
14 | 2530976.6085 | 1151751.8766 | 2530982.5628 | 1151771.119 | 2530990.1432 | 1151795.6233 | 2530994.0893 | 1151808.4185 | 2530959.3873 | 1151821.524 | 2530952.4228 | 1151803.2049 | 2530931.033 | 1151811.2773
15 | 2530976.6085 | 1151751.8766 | 2530982.5628 | 1151771.119 | 2531015.0835 | 1151770.5566 | 2531021.0142 | 1151768.3651 | 2531021.0243 | 1151755.8692
16 | 2530976.6085 | 1151751.8766 | 2530945.5399 | 1151764.607 | 2530953.606 | 1151784.1688
17 | 2530710.9769 | 1151902.1369 | 2530713.5299 | 1151907.8885 | 2530713.7894 | 1151909.7643
18 | 2530714.3182 | 1151897.7071 | 2530710.9769 | 1151902.1369
19 | 2530931.033 | 1151811.2773 | 2530930.1731 | 1151809.0145
20 | 2530931.033 | 1151811.2773 | 2530939.1242 | 1151832.5659
21 | 2531021.0243 | 1151755.8692 | 2531011.648 | 1151755.4321
22 | 2531021.0243 | 1151755.8692 | 2531020.9917 | 1151753.0236 | 2531023.9861 | 1151753.1226
23 | 2531021.0243 | 1151755.8692 | 2531021.0142 | 1151768.3651 | 2531026.4407 | 1151766.3685 | 2531032.1346 | 1151764.9468 | 2531037.697 | 1151764.7607 | 2531050.5939 | 1151764.3237 | 2531057.5152 | 1151759.4972
24 | 2530714.3182 | 1151897.7071 | 2530721.3071 | 1151897.4486 | 2530727.552 | 1151895.231 | 2530735.7424 | 1151890.6786 | 2530736.988 | 1151890.0261
25 | 2530774.3984 | 1151885.7641 | 2530772.2311 | 1151884.177 | 2530764.332 | 1151883.3786 | 2530751.6245 | 1151884.2366 | 2530744.119 | 1151886.2908 | 2530736.988 | 1151890.0261
26 | 2531038.1993 | 1151791.8144 | 2531043.3025 | 1151791.7558
27 | 2531038.1993 | 1151791.8144 | 2531037.697 | 1151764.7607 | 2531050.5939 | 1151764.3237 | 2531057.5152 | 1151759.4972
28 | 2531038.3199 | 1151798.3166 | 2531038.1993 | 1151791.8144
29 | 2531057.5152 | 1151759.4972 | 2531056.5409 | 1151738.1299 | 2531060.2077 | 1151737.9544
30 | 2531038.3199 | 1151798.3166 | 2531031.4239 | 1151797.9844
31 | 2531060.2077 | 1151737.9544 | 2531038.3539 | 1151386.5213
32 | 2531038.3539 | 1151386.5213 | 2531038.2068 | 1151370.0789
33 | 2531109.9161 | 1151315.3733 | 2531103.4505 | 1151312.8344 | 2531083.8285 | 1151301.8824
34 | 2531056.7307 | 1151286.255 | 2531073.1988 | 1151295.9494 | 2531083.8285 | 1151301.8824
35 | 2531011.8972 | 1151337.7977 | 2530989.772 | 1151311.3813 | 2530977.6775 | 1151297.5569 | 2530973.9 | 1151291.4524 | 2530972.2064 | 1151285.6687 | 2530975.0332 | 1151277.8319 | 2530979.0102 | 1151273.2393 | 2530985.1413 | 1151271.7459 | 2530995.0698 | 1151271.3984 | 2531024.6546 | 1151272.9488 | 2531035.5297 | 1151272.824 | 2531046.4264 | 1151274.5778 | 2531053.8126 | 1151279.4514 | 2531056.7307 | 1151286.255
36 | 2531011.8972 | 1151337.7977 | 2531034.6612 | 1151364.1879
37 | 2531038.1907 | 1151368.2797 | 2531034.6612 | 1151364.1879
38 | 2531038.1907 | 1151368.2797 | 2531038.2068 | 1151370.0789

## bus_geodata
| x | y | coords
0 | 2530886.9887 | 1151861.842
1 | 2530863.8673 | 1151885.2457
2 | 2530882.7815 | 1151826.1065
3 | 2530848.4041 | 1151862.7221
4 | 2530856.5705 | 1151860.7236
5 | 2530812.4806 | 1151910.3395
6 | 2530809.3358 | 1151831.8432
7 | 2530829.8285 | 1151866.5656
8 | 2530830.0351 | 1151804.4677
9 | 2530757.6694 | 1151838.6507
10 | 2530977.4365 | 1151747.7871
11 | 2530686.8354 | 1151839.258
12 | 2530975.0106 | 1151739.0545
13 | 2530976.6085 | 1151751.8766
14 | 2530710.9769 | 1151902.1369
15 | 2530931.033 | 1151811.2773
16 | 2531021.0243 | 1151755.8692
17 | 2530953.606 | 1151784.1688
18 | 2530713.7894 | 1151909.7643
19 | 2530714.3182 | 1151897.7071
20 | 2530736.988 | 1151890.0261
21 | 2530774.3984 | 1151885.7641
22 | 2530930.1731 | 1151809.0145
23 | 2530939.1242 | 1151832.5659
24 | 2531038.1993 | 1151791.8144
25 | 2531043.3025 | 1151791.7558
26 | 2531057.5152 | 1151759.4972
27 | 2531038.3199 | 1151798.3166
28 | 2531011.648 | 1151755.4321
29 | 2531023.9861 | 1151753.1226
30 | 2531060.2077 | 1151737.9544
31 | 2531031.4239 | 1151797.9844
32 | 2531038.3539 | 1151386.5213
33 | 2531109.9161 | 1151315.3733
34 | 2531083.8285 | 1151301.8824
35 | 2531056.7307 | 1151286.255
36 | 2531011.8972 | 1151337.7977
37 | 2531034.6612 | 1151364.1879
38 | 2531038.1907 | 1151368.2797
39 | 2531038.2068 | 1151370.0789
40 | 2530931.033 | 1151811.2773

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1