## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5712-9_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5712-9_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5712-9_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5712-9_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5712-9_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5712-9_0_6_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_5712-9_0_6_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_5712-9_0_6_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_5712-9_0_6_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_5712-9_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_5712-9_0_6_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_5712-9_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_5712-9_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_5712-9_0_6_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_5712-9_0_6_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_5712-9_0_6_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_5712-9_0_6_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_5712-9_0_6_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_5712-9_0_6_node_39 | 0.4 | n |  | TRUE
19 | bus_LV_5712-9_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_5712-9_0_6_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_5712-9_0_6_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_5712-9_0_6_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_5712-9_0_6_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_5712-9_0_6_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_5712-9_0_6_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_5712-9_0_6_node_38 | 0.4 | n |  | TRUE
27 | bus_LV_5712-9_0_6_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_5712-9_0_6_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_5712-9_0_6_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_5712-9_0_6_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_5712-9_0_6_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_5712-9_0_6_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_5712-9_0_6_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_5712-9_0_6_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_5712-9_0_6_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_5712-9_0_6_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_5712-9_0_6_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_5712-9_0_6_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_5712-9_0_6_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_5712-9_0_6_node_53 | 0.4 | n |  | TRUE
41 | bus_LV_5712-9_0_6_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_5712-9_0_6_node_55 | 0.4 | n |  | TRUE
43 | bus_LV_5712-9_0_6_node_49 | 0.4 | n |  | TRUE
44 | bus_LV_5712-9_0_6_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_5712-9_0_6_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_5712-9_0_6_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_5712-9_0_6_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_5712-9_0_6_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_5712-9_0_6_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_5712-9_0_6_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_5712-9_0_6_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_5712-9_0_6_node_67 | 0.4 | n |  | TRUE
53 | bus_LV_5712-9_0_6_node_68 | 0.4 | n |  | TRUE
54 | bus_LV_5712-9_0_6_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_5712-9_0_6_node_96 | 0.4 | n |  | TRUE
56 | bus_LV_5712-9_0_6_node_95 | 0.4 | n |  | TRUE
57 | bus_LV_5712-9_0_6_node_75 | 0.4 | n |  | TRUE
58 | bus_LV_5712-9_0_6_node_72 | 0.4 | n |  | TRUE
59 | bus_LV_5712-9_0_6_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_5712-9_0_6_node_94 | 0.4 | n |  | TRUE
61 | bus_LV_5712-9_0_6_node_93 | 0.4 | n |  | TRUE
62 | bus_LV_5712-9_0_6_node_155 | 0.4 | n |  | TRUE
63 | bus_LV_5712-9_0_6_node_154 | 0.4 | n |  | TRUE
64 | bus_LV_5712-9_0_6_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_5712-9_0_6_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_5712-9_0_6_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_5712-9_0_6_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_5712-9_0_6_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_5712-9_0_6_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_5712-9_0_6_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_5712-9_0_6_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_5712-9_0_6_node_64 | 0.4 | n |  | TRUE
73 | bus_LV_5712-9_0_6_node_63 | 0.4 | n |  | TRUE
74 | bus_LV_5712-9_0_6_node_70 | 0.4 | n |  | TRUE
75 | bus_LV_5712-9_0_6_node_71 | 0.4 | n |  | TRUE
76 | bus_LV_5712-9_0_6_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_5712-9_0_6_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_5712-9_0_6_node_79 | 0.4 | n |  | TRUE
79 | bus_LV_5712-9_0_6_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_5712-9_0_6_node_66 | 0.4 | n |  | TRUE
81 | bus_LV_5712-9_0_6_node_111 | 0.4 | n |  | TRUE
82 | bus_LV_5712-9_0_6_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_5712-9_0_6_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_5712-9_0_6_node_91 | 0.4 | n |  | TRUE
85 | bus_LV_5712-9_0_6_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_5712-9_0_6_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_5712-9_0_6_node_114 | 0.4 | n |  | TRUE
88 | bus_LV_5712-9_0_6_node_76 | 0.4 | n |  | TRUE
89 | bus_LV_5712-9_0_6_node_110 | 0.4 | n |  | TRUE
90 | bus_LV_5712-9_0_6_node_133 | 0.4 | n |  | TRUE
91 | bus_LV_5712-9_0_6_node_108 | 0.4 | n |  | TRUE
92 | bus_LV_5712-9_0_6_node_112 | 0.4 | n |  | TRUE
93 | bus_LV_5712-9_0_6_node_113 | 0.4 | n |  | TRUE
94 | bus_LV_5712-9_0_6_node_115 | 0.4 | n |  | TRUE
95 | bus_LV_5712-9_0_6_node_116 | 0.4 | n |  | TRUE
96 | bus_LV_5712-9_0_6_node_117 | 0.4 | n |  | TRUE
97 | bus_LV_5712-9_0_6_node_134 | 0.4 | n |  | TRUE
98 | bus_LV_5712-9_0_6_node_135 | 0.4 | n |  | TRUE
99 | bus_LV_5712-9_0_6_node_118 | 0.4 | n |  | TRUE
100 | bus_LV_5712-9_0_6_node_119 | 0.4 | n |  | TRUE
101 | bus_LV_5712-9_0_6_node_120 | 0.4 | n |  | TRUE
102 | bus_LV_5712-9_0_6_node_90 | 0.4 | n |  | TRUE
103 | bus_LV_5712-9_0_6_node_80 | 0.4 | n |  | TRUE
104 | bus_LV_5712-9_0_6_node_92 | 0.4 | n |  | TRUE
105 | bus_LV_5712-9_0_6_node_121 | 0.4 | n |  | TRUE
106 | bus_LV_5712-9_0_6_node_88 | 0.4 | n |  | TRUE
107 | bus_LV_5712-9_0_6_node_82 | 0.4 | n |  | TRUE
108 | bus_LV_5712-9_0_6_node_83 | 0.4 | n |  | TRUE
109 | bus_LV_5712-9_0_6_node_84 | 0.4 | n |  | TRUE
110 | bus_LV_5712-9_0_6_node_85 | 0.4 | n |  | TRUE
111 | bus_LV_5712-9_0_6_node_86 | 0.4 | n |  | TRUE
112 | bus_LV_5712-9_0_6_node_126 | 0.4 | n |  | TRUE
113 | bus_LV_5712-9_0_6_node_125 | 0.4 | n |  | TRUE
114 | bus_LV_5712-9_0_6_node_87 | 0.4 | n |  | TRUE
115 | bus_LV_5712-9_0_6_node_128 | 0.4 | n |  | TRUE
116 | bus_LV_5712-9_0_6_node_89 | 0.4 | n |  | TRUE
117 | bus_LV_5712-9_0_6_node_122 | 0.4 | n |  | TRUE
118 | bus_LV_5712-9_0_6_node_103 | 0.4 | n |  | TRUE
119 | bus_LV_5712-9_0_6_node_104 | 0.4 | n |  | TRUE
120 | bus_LV_5712-9_0_6_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_5712-9_0_6_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_5712-9_0_6_node_107 | 0.4 | n |  | TRUE
123 | bus_LV_5712-9_0_6_node_136 | 0.4 | n |  | TRUE
124 | bus_LV_5712-9_0_6_node_109 | 0.4 | n |  | TRUE
125 | bus_LV_5712-9_0_6_node_137 | 0.4 | n |  | TRUE
126 | bus_LV_5712-9_0_6_node_138 | 0.4 | n |  | TRUE
127 | bus_LV_5712-9_0_6_node_97 | 0.4 | n |  | TRUE
128 | bus_LV_5712-9_0_6_node_98 | 0.4 | n |  | TRUE
129 | bus_LV_5712-9_0_6_node_99 | 0.4 | n |  | TRUE
130 | bus_LV_5712-9_0_6_node_100 | 0.4 | n |  | TRUE
131 | bus_LV_5712-9_0_6_node_102 | 0.4 | n |  | TRUE
132 | bus_LV_5712-9_0_6_node_105 | 0.4 | n |  | TRUE
133 | bus_LV_5712-9_0_6_node_141 | 0.4 | n |  | TRUE
134 | bus_LV_5712-9_0_6_node_139 | 0.4 | n |  | TRUE
135 | bus_LV_5712-9_0_6_node_142 | 0.4 | n |  | TRUE
136 | bus_LV_5712-9_0_6_node_140 | 0.4 | n |  | TRUE
137 | bus_LV_5712-9_0_6_node_130 | 0.4 | n |  | TRUE
138 | bus_LV_5712-9_0_6_node_131 | 0.4 | n |  | TRUE
139 | bus_LV_5712-9_0_6_node_129 | 0.4 | n |  | TRUE
140 | bus_LV_5712-9_0_6_node_132 | 0.4 | n |  | TRUE
141 | bus_LV_5712-9_0_6_node_123 | 0.4 | n |  | TRUE
142 | bus_LV_5712-9_0_6_node_124 | 0.4 | n |  | TRUE
143 | bus_LV_5712-9_0_6_node_127 | 0.4 | n |  | TRUE
144 | bus_LV_5712-9_0_6_node_152 | 0.4 | n |  | TRUE
145 | bus_LV_5712-9_0_6_node_149 | 0.4 | n |  | TRUE
146 | bus_LV_5712-9_0_6_node_143 | 0.4 | n |  | TRUE
147 | bus_LV_5712-9_0_6_node_144 | 0.4 | n |  | TRUE
148 | bus_LV_5712-9_0_6_node_145 | 0.4 | n |  | TRUE
149 | bus_LV_5712-9_0_6_node_146 | 0.4 | n |  | TRUE
150 | bus_LV_5712-9_0_6_node_147 | 0.4 | n |  | TRUE
151 | bus_LV_5712-9_0_6_node_150 | 0.4 | n |  | TRUE
152 | bus_LV_5712-9_0_6_node_148 | 0.4 | n |  | TRUE
153 | bus_LV_5712-9_0_6_node_153 | 0.4 | n |  | TRUE
154 | bus_LV_5712-9_0_6_node_151 | 0.4 | n |  | TRUE
155 | bus_MV_453_0_node_125 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5712-9_0_6_load_0 | 0 | 0.0031985 | 0.00080163 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5712-9_0_6_load_2 | 2 | 0.0034502 | 0.00086469 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5712-9_0_6_load_3 | 3 | 0.005836 | 0.0014626 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5712-9_0_6_load_4 | 4 | 0.006028 | 0.0015108 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5712-9_0_6_load_28 | 5 | 0.0070768 | 0.0017736 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5712-9_0_6_load_7 | 6 | 0.006761 | 0.0016945 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5712-9_0_6_load_34 | 7 | 0.0067592 | 0.001694 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5712-9_0_6_load_32 | 8 | 0.0059985 | 0.0015034 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5712-9_0_6_load_5 | 9 | 0.0053931 | 0.0013516 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5712-9_0_6_load_6 | 10 | 0.0053729 | 0.0013466 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5712-9_0_6_load_10 | 13 | 0.0067618 | 0.0016947 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5712-9_0_6_load_30 | 14 | 0.0056759 | 0.0014225 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5712-9_0_6_load_11 | 16 | 0.010237 | 0.0025655 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5712-9_0_6_load_14 | 17 | 0.0054206 | 0.0013585 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5712-9_0_6_load_39 | 18 | 0.0057957 | 0.0014525 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5712-9_0_6_load_12 | 19 | 0.002169 | 0.0005436 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5712-9_0_6_load_35 | 20 | 0.0054149 | 0.0013571 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5712-9_0_6_load_36 | 21 | 0.0034656 | 0.00086857 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5712-9_0_6_load_33 | 22 | 0.0021131 | 0.0005296 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5712-9_0_6_load_13 | 23 | 0.0061187 | 0.0015335 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5712-9_0_6_load_15 | 24 | 0.0072255 | 0.0018109 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5712-9_0_6_load_38 | 26 | 0.0031346 | 0.00078561 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5712-9_0_6_load_37 | 27 | 0.003806 | 0.00095388 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5712-9_0_6_load_17 | 28 | 0.0065218 | 0.0016345 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5712-9_0_6_load_18 | 29 | 0.0045424 | 0.0011384 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5712-9_0_6_load_21 | 32 | 0.0056368 | 0.0014127 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5712-9_0_6_load_26 | 33 | 0.0025262 | 0.00063313 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5712-9_0_6_load_22 | 34 | 0.0054306 | 0.001361 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5712-9_0_6_load_48 | 35 | 0.005637 | 0.0014128 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5712-9_0_6_load_24 | 37 | 0.0031548 | 0.00079066 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5712-9_0_6_load_25 | 38 | 0.0030872 | 0.00077373 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5712-9_0_6_load_27 | 39 | 0.0048287 | 0.0012102 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5712-9_0_6_load_54 | 41 | 0.0030662 | 0.00076847 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5712-9_0_6_load_55 | 42 | 0.0040866 | 0.0010242 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5712-9_0_6_load_49 | 43 | 0.0034016 | 0.00085251 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5712-9_0_6_load_40 | 44 | 0.0026769 | 0.0006709 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5712-9_0_6_load_41 | 45 | 0.0031492 | 0.00078926 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5712-9_0_6_load_45 | 48 | 0.0040427 | 0.0010132 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5712-9_0_6_load_42 | 49 | 0.0031785 | 0.0007966 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5712-9_0_6_load_52 | 54 | 0.0015747 | 0.00039465 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5712-9_0_6_load_96 | 55 | 0.0080157 | 0.0020089 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5712-9_0_6_load_95 | 56 | 0.0041401 | 0.0010376 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5712-9_0_6_load_75 | 57 | 0.0029958 | 0.00075082 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5712-9_0_6_load_72 | 58 | 0.0027559 | 0.00069069 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5712-9_0_6_load_50 | 59 | 0.0049669 | 0.0012448 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5712-9_0_6_load_93 | 61 | 0.0019295 | 0.00048357 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5712-9_0_6_load_155 | 62 | 0.003169 | 0.00079422 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5712-9_0_6_load_154 | 63 | 0.0029131 | 0.00073009 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5712-9_0_6_load_51 | 64 | 0.0055105 | 0.0013811 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5712-9_0_6_load_57 | 66 | 0.0032194 | 0.00080686 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5712-9_0_6_load_58 | 67 | 0.0030618 | 0.00076736 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5712-9_0_6_load_62 | 68 | 0.0039311 | 0.00098523 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5712-9_0_6_load_59 | 69 | 0.0033198 | 0.00083202 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5712-9_0_6_load_60 | 70 | 0.0027715 | 0.00069461 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5712-9_0_6_load_64 | 72 | 0.0045858 | 0.0011493 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5712-9_0_6_load_70 | 74 | 0.0050767 | 0.0012723 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5712-9_0_6_load_69 | 76 | 0.0035593 | 0.00089204 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5712-9_0_6_load_79 | 78 | 0.0015314 | 0.0003838 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5712-9_0_6_load_77 | 79 | 0.003547 | 0.00088896 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5712-9_0_6_load_66 | 80 | 0.0035962 | 0.00090128 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5712-9_0_6_load_111 | 81 | 0.0028567 | 0.00071596 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5712-9_0_6_load_73 | 82 | 0.0021351 | 0.0005351 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5712-9_0_6_load_91 | 84 | 0.0027321 | 0.00068474 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5712-9_0_6_load_74 | 86 | 0.0015894 | 0.00039833 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5712-9_0_6_load_114 | 87 | 0.0026632 | 0.00066745 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5712-9_0_6_load_133 | 90 | 0.0025699 | 0.00064409 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5712-9_0_6_load_112 | 92 | 0.0034626 | 0.0008678 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5712-9_0_6_load_113 | 93 | 0.0018887 | 0.00047336 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5712-9_0_6_load_116 | 95 | 0.0025673 | 0.00064343 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5712-9_0_6_load_117 | 96 | 0.00060915 | 0.00015267 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5712-9_0_6_load_134 | 97 | 0.0024196 | 0.00060642 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5712-9_0_6_load_135 | 98 | 0.0033598 | 0.00084204 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5712-9_0_6_load_118 | 99 | 0.0019136 | 0.0004796 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5712-9_0_6_load_80 | 103 | 0.0022484 | 0.00056351 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5712-9_0_6_load_92 | 104 | 0.0029926 | 0.00075001 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5712-9_0_6_load_121 | 105 | 0.0017148 | 0.00042978 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5712-9_0_6_load_82 | 107 | 0.0039048 | 0.00097864 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5712-9_0_6_load_83 | 108 | 0.0033457 | 0.00083852 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5712-9_0_6_load_85 | 110 | 0.0040249 | 0.0010087 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5712-9_0_6_load_125 | 113 | 0.0034475 | 0.00086402 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5712-9_0_6_load_87 | 114 | 0.0030423 | 0.00076248 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5712-9_0_6_load_128 | 115 | 0.0035773 | 0.00089656 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5712-9_0_6_load_89 | 116 | 0.0016762 | 0.00042009 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5712-9_0_6_load_122 | 117 | 0.0030382 | 0.00076145 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5712-9_0_6_load_103 | 118 | 0.0037718 | 0.00094529 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5712-9_0_6_load_106 | 121 | 0.0029454 | 0.00073818 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5712-9_0_6_load_107 | 122 | 0.0022669 | 0.00056814 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5712-9_0_6_load_136 | 123 | 0.0020151 | 0.00050503 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5712-9_0_6_load_109 | 124 | 0.0027709 | 0.00069446 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5712-9_0_6_load_137 | 125 | 0.0039898 | 0.00099993 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5712-9_0_6_load_138 | 126 | 0.00095801 | 0.0002401 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5712-9_0_6_load_97 | 127 | 0.0024236 | 0.0006074 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5712-9_0_6_load_98 | 128 | 0.0024932 | 0.00062485 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5712-9_0_6_load_100 | 130 | 0.0042827 | 0.0010733 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5712-9_0_6_load_102 | 131 | 0.0020723 | 0.00051938 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5712-9_0_6_load_105 | 132 | 0.002943 | 0.00073759 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5712-9_0_6_load_141 | 133 | 0.0026558 | 0.00066561 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5712-9_0_6_load_139 | 134 | 0.0030034 | 0.00075273 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5712-9_0_6_load_140 | 136 | 0.0029457 | 0.00073826 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5712-9_0_6_load_131 | 138 | 0.0028557 | 0.0007157 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5712-9_0_6_load_129 | 139 | 0.0029757 | 0.00074577 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5712-9_0_6_load_132 | 140 | 0.0025105 | 0.00062919 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5712-9_0_6_load_123 | 141 | 0.0028828 | 0.0007225 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5712-9_0_6_load_124 | 142 | 0.0027364 | 0.0006858 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5712-9_0_6_load_127 | 143 | 0.0034121 | 0.00085516 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5712-9_0_6_load_152 | 144 | 0.0026942 | 0.00067522 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5712-9_0_6_load_143 | 146 | 0.0023803 | 0.00059656 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_5712-9_0_6_load_146 | 149 | 0.0029735 | 0.00074523 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_5712-9_0_6_load_148 | 152 | 0.0024623 | 0.00061712 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_5712-9_0_6_load_153 | 153 | 0.0028176 | 0.00070615 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_5712-9_0_6_load_151 | 154 | 0.0027986 | 0.0007014 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5712-9_0_6_line_0 |  | 0 | 1 | 0.022769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5712-9_0_6_line_1 |  | 1 | 2 | 0.008668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_5712-9_0_6_line_2 |  | 1 | 3 | 0.027929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_5712-9_0_6_line_3 |  | 2 | 4 | 0.026968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_5712-9_0_6_line_4 |  | 3 | 5 | 0.042601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_5712-9_0_6_line_5 |  | 4 | 9 | 0.0275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_5712-9_0_6_line_6 |  | 5 | 8 | 0.034618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_5712-9_0_6_line_7 |  | 6 | 7 | 0.029853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5712-9_0_6_line_8 |  | 6 | 8 | 0.031495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5712-9_0_6_line_9 |  | 7 | 13 | 0.033841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5712-9_0_6_line_10 |  | 8 | 14 | 0.0044631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_5712-9_0_6_line_11 |  | 9 | 10 | 0.027876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_5712-9_0_6_line_12 |  | 10 | 11 | 0.015747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_5712-9_0_6_line_13 |  | 11 | 12 | 0.003439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_5712-9_0_6_line_14 |  | 12 | 16 | 0.016586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_5712-9_0_6_line_15 |  | 14 | 15 | 0.018641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_5712-9_0_6_line_16 |  | 15 | 22 | 0.027524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_5712-9_0_6_line_17 |  | 16 | 19 | 0.010515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_5712-9_0_6_line_18 |  | 17 | 18 | 0.030262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5712-9_0_6_line_19 |  | 18 | 26 | 0.0377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5712-9_0_6_line_20 |  | 19 | 23 | 0.018835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_5712-9_0_6_line_21 |  | 20 | 21 | 0.028557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_5712-9_0_6_line_22 |  | 20 | 22 | 0.0071885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_5712-9_0_6_line_23 |  | 21 | 27 | 0.032194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_5712-9_0_6_line_24 |  | 23 | 24 | 0.030637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_5712-9_0_6_line_25 |  | 24 | 25 | 0.0066919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_5712-9_0_6_line_26 |  | 25 | 28 | 0.022006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_5712-9_0_6_line_27 |  | 25 | 29 | 0.025363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5712-9_0_6_line_28 |  | 26 | 44 | 0.029489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_5712-9_0_6_line_29 |  | 26 | 27 | 0.0052966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_5712-9_0_6_line_30 |  | 28 | 30 | 0.01893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_5712-9_0_6_line_31 |  | 30 | 31 | 0.00388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_5712-9_0_6_line_32 |  | 30 | 32 | 0.051649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5712-9_0_6_line_33 |  | 31 | 33 | 0.050317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5712-9_0_6_line_34 |  | 31 | 34 | 0.0020291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_5712-9_0_6_line_35 |  | 33 | 35 | 0.0082364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5712-9_0_6_line_36 |  | 34 | 36 | 0.037106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_5712-9_0_6_line_37 |  | 35 | 43 | 0.013927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5712-9_0_6_line_38 |  | 36 | 37 | 0.019199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5712-9_0_6_line_39 |  | 36 | 38 | 0.037148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_5712-9_0_6_line_40 |  | 37 | 39 | 9.7735e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5712-9_0_6_line_41 |  | 38 | 40 | 0.014516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5712-9_0_6_line_42 |  | 40 | 41 | 0.0085208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5712-9_0_6_line_43 |  | 40 | 42 | 0.034992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5712-9_0_6_line_44 |  | 41 | 65 | 0.018954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5712-9_0_6_line_45 |  | 44 | 45 | 0.0068965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_5712-9_0_6_line_46 |  | 45 | 46 | 0.031999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_5712-9_0_6_line_47 |  | 46 | 47 | 0.016202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5712-9_0_6_line_48 |  | 46 | 48 | 0.0092643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_5712-9_0_6_line_49 |  | 47 | 60 | 0.006693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5712-9_0_6_line_50 |  | 47 | 61 | 0.013604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5712-9_0_6_line_51 |  | 48 | 50 | 0.025034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_5712-9_0_6_line_52 |  | 49 | 50 | 0.04217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5712-9_0_6_line_53 |  | 50 | 51 | 0.031321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_5712-9_0_6_line_54 |  | 51 | 52 | 0.032022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5712-9_0_6_line_55 |  | 51 | 53 | 0.042415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5712-9_0_6_line_56 |  | 51 | 54 | 0.015814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5712-9_0_6_line_57 |  | 52 | 55 | 0.017611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5712-9_0_6_line_58 |  | 52 | 56 | 0.017769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5712-9_0_6_line_59 |  | 53 | 57 | 0.050942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5712-9_0_6_line_60 |  | 53 | 58 | 0.01701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5712-9_0_6_line_61 |  | 54 | 59 | 0.0093668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5712-9_0_6_line_62 |  | 55 | 81 | 0.049305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5712-9_0_6_line_63 |  | 58 | 82 | 0.038746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5712-9_0_6_line_64 |  | 59 | 64 | 0.030837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5712-9_0_6_line_65 |  | 60 | 62 | 0.025776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5712-9_0_6_line_66 |  | 60 | 63 | 0.02348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5712-9_0_6_line_67 |  | 65 | 66 | 0.006508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5712-9_0_6_line_68 |  | 65 | 67 | 0.031991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5712-9_0_6_line_69 |  | 66 | 68 | 0.035163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5712-9_0_6_line_70 |  | 66 | 69 | 0.025898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5712-9_0_6_line_71 |  | 69 | 70 | 0.027973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5712-9_0_6_line_72 |  | 70 | 71 | 0.0015645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5712-9_0_6_line_73 |  | 71 | 72 | 0.033301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5712-9_0_6_line_74 |  | 72 | 77 | 0.013284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5712-9_0_6_line_75 |  | 73 | 74 | 0.02976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5712-9_0_6_line_76 |  | 73 | 75 | 0.031193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5712-9_0_6_line_77 |  | 73 | 76 | 0.016597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5712-9_0_6_line_78 |  | 75 | 78 | 0.015705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5712-9_0_6_line_79 |  | 75 | 79 | 0.027398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5712-9_0_6_line_80 |  | 77 | 80 | 0.037588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5712-9_0_6_line_81 |  | 78 | 83 | 0.041069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5712-9_0_6_line_82 |  | 78 | 84 | 0.020583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5712-9_0_6_line_83 |  | 79 | 85 | 0.016643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5712-9_0_6_line_84 |  | 81 | 124 | 0.0018655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_5712-9_0_6_line_85 |  | 82 | 86 | 0.04214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5712-9_0_6_line_86 |  | 82 | 87 | 0.029468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_5712-9_0_6_line_87 |  | 83 | 102 | 0.043905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5712-9_0_6_line_88 |  | 83 | 88 | 0.003357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_5712-9_0_6_line_89 |  | 84 | 104 | 0.027662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5712-9_0_6_line_90 |  | 85 | 103 | 0.004897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5712-9_0_6_line_91 |  | 86 | 88 | 0.013978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5712-9_0_6_line_92 |  | 87 | 92 | 0.0098782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5712-9_0_6_line_93 |  | 89 | 90 | 0.019598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5712-9_0_6_line_94 |  | 89 | 91 | 0.053622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5712-9_0_6_line_95 |  | 90 | 97 | 0.00034398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5712-9_0_6_line_96 |  | 91 | 124 | 0.031526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5712-9_0_6_line_97 |  | 91 | 121 | 0.020151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5712-9_0_6_line_98 |  | 92 | 93 | 0.016818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5712-9_0_6_line_99 |  | 93 | 94 | 0.0088321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5712-9_0_6_line_100 |  | 94 | 95 | 0.014675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5712-9_0_6_line_101 |  | 94 | 96 | 0.0052136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5712-9_0_6_line_102 |  | 96 | 99 | 0.012964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5712-9_0_6_line_103 |  | 97 | 98 | 0.012551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_5712-9_0_6_line_104 |  | 99 | 100 | 0.009797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_5712-9_0_6_line_105 |  | 100 | 101 | 0.010031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_5712-9_0_6_line_106 |  | 101 | 137 | 0.021196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_5712-9_0_6_line_107 |  | 101 | 138 | 0.018672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_5712-9_0_6_line_108 |  | 102 | 105 | 0.020592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_5712-9_0_6_line_109 |  | 102 | 106 | 0.005767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_5712-9_0_6_line_110 |  | 105 | 117 | 0.0088243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_5712-9_0_6_line_111 |  | 106 | 114 | 0.017922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_5712-9_0_6_line_112 |  | 106 | 110 | 0.03399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_5712-9_0_6_line_113 |  | 107 | 108 | 0.022238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_5712-9_0_6_line_114 |  | 108 | 109 | 0.036529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_5712-9_0_6_line_115 |  | 109 | 110 | 0.02238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_5712-9_0_6_line_116 |  | 109 | 111 | 0.018086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_5712-9_0_6_line_117 |  | 111 | 112 | 0.046435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_5712-9_0_6_line_118 |  | 111 | 113 | 0.019374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_5712-9_0_6_line_119 |  | 112 | 115 | 0.019759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_5712-9_0_6_line_120 |  | 114 | 116 | 0.0030301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_5712-9_0_6_line_121 |  | 115 | 143 | 0.027546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_5712-9_0_6_line_122 |  | 117 | 141 | 0.026349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_5712-9_0_6_line_123 |  | 118 | 119 | 0.020834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_5712-9_0_6_line_124 |  | 118 | 120 | 0.032771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_5712-9_0_6_line_125 |  | 119 | 121 | 0.0063082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_5712-9_0_6_line_126 |  | 119 | 122 | 0.018891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_5712-9_0_6_line_127 |  | 120 | 132 | 0.023953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_5712-9_0_6_line_128 |  | 120 | 129 | 0.013953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_5712-9_0_6_line_129 |  | 122 | 123 | 0.020582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_5712-9_0_6_line_130 |  | 123 | 125 | 0.010967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_5712-9_0_6_line_131 |  | 125 | 126 | 0.0014586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_5712-9_0_6_line_132 |  | 127 | 128 | 0.0083309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_5712-9_0_6_line_133 |  | 127 | 129 | 0.016626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_5712-9_0_6_line_134 |  | 128 | 130 | 0.025501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_5712-9_0_6_line_135 |  | 129 | 131 | 0.029702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_5712-9_0_6_line_136 |  | 131 | 133 | 0.050577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_5712-9_0_6_line_137 |  | 132 | 134 | 0.0081033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_5712-9_0_6_line_138 |  | 133 | 135 | 0.05279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_5712-9_0_6_line_139 |  | 134 | 136 | 0.011529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_5712-9_0_6_line_140 |  | 135 | 144 | 0.046987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_5712-9_0_6_line_141 |  | 137 | 139 | 0.029207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_5712-9_0_6_line_142 |  | 138 | 140 | 0.015153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_5712-9_0_6_line_143 |  | 141 | 142 | 0.0061553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_5712-9_0_6_line_144 |  | 144 | 145 | 0.012674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_5712-9_0_6_line_145 |  | 145 | 154 | 0.02363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_5712-9_0_6_line_146 |  | 145 | 152 | 0.0021331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_5712-9_0_6_line_147 |  | 146 | 147 | 0.014821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_5712-9_0_6_line_148 |  | 146 | 148 | 0.021392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_5712-9_0_6_line_149 |  | 147 | 149 | 0.01347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_5712-9_0_6_line_150 |  | 148 | 150 | 0.020981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_5712-9_0_6_line_151 |  | 150 | 151 | 0.026681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_5712-9_0_6_line_152 |  | 150 | 152 | 0.01407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_5712-9_0_6_line_153 |  | 151 | 153 | 0.008648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5712-9_0_6_trafo_43 | 0.63 MVA 20/0.4 kV | 155 | 50 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2503407.7435 | 1131188.7801 | 2503426.7142 | 1131176.1894
1 | 2503407.7435 | 1131188.7801 | 2503400.5031 | 1131193.5767
2 | 2503407.7435 | 1131188.7801 | 2503413.0266 | 1131196.4336 | 2503416.3286 | 1131205.9088 | 2503420.7821 | 1131213.26
3 | 2503400.5031 | 1131193.5767 | 2503388.0119 | 1131201.8706 | 2503378.037 | 1131208.4947
4 | 2503420.7821 | 1131213.26 | 2503454.8457 | 1131238.8433
5 | 2503378.037 | 1131208.4947 | 2503355.1279 | 1131223.7082
6 | 2503427.3755 | 1131259.9096 | 2503454.8457 | 1131238.8433
7 | 2503407.3966 | 1131235.5629 | 2503393.8132 | 1131244.7707 | 2503382.6826 | 1131252.3087
8 | 2503407.3966 | 1131235.5629 | 2503427.3755 | 1131259.9096
9 | 2503382.6826 | 1131252.3087 | 2503354.6623 | 1131271.2849
10 | 2503427.3755 | 1131259.9096 | 2503423.8043 | 1131262.5865
11 | 2503355.1279 | 1131223.7082 | 2503331.9062 | 1131239.1292
12 | 2503318.7884 | 1131247.8404 | 2503331.9062 | 1131239.1292
13 | 2503318.7884 | 1131247.8404 | 2503315.9152 | 1131249.7432
14 | 2503315.9152 | 1131249.7432 | 2503302.0883 | 1131258.903
15 | 2503411.5061 | 1131275.1284 | 2503411.6133 | 1131271.7246 | 2503423.8043 | 1131262.5865
16 | 2503411.5061 | 1131275.1284 | 2503409.1338 | 1131275.6111 | 2503388.5904 | 1131290.038
17 | 2503302.0883 | 1131258.903 | 2503293.3226 | 1131264.71
18 | 2503327.3003 | 1131288.6745 | 2503301.8598 | 1131305.0622
19 | 2503301.8598 | 1131305.0622 | 2503328.4342 | 1131331.8037
20 | 2503293.3226 | 1131264.71 | 2503277.6205 | 1131275.1121
21 | 2503382.7076 | 1131294.1692 | 2503359.3376 | 1131310.5811
22 | 2503382.7076 | 1131294.1692 | 2503388.5904 | 1131290.038
23 | 2503359.3376 | 1131310.5811 | 2503344.5077 | 1131320.9956 | 2503332.8295 | 1131328.8482
24 | 2503277.6205 | 1131275.1121 | 2503252.0793 | 1131292.0323
25 | 2503246.5005 | 1131295.728 | 2503252.0793 | 1131292.0323
26 | 2503246.5005 | 1131295.728 | 2503228.1545 | 1131307.88
27 | 2503246.5005 | 1131295.728 | 2503248.937 | 1131299.2467 | 2503260.608 | 1131316.8048
28 | 2503328.4342 | 1131331.8037 | 2503303.9627 | 1131348.2586
29 | 2503328.4342 | 1131331.8037 | 2503332.8295 | 1131328.8482
30 | 2503212.3728 | 1131318.3335 | 2503228.1545 | 1131307.88
31 | 2503212.3728 | 1131318.3335 | 2503209.1733 | 1131320.5417
32 | 2503212.3728 | 1131318.3335 | 2503214.4772 | 1131321.3238 | 2503231.8841 | 1131347.2495 | 2503233.5519 | 1131347.9899 | 2503247.0388 | 1131341.5613
33 | 2503209.1733 | 1131320.5417 | 2503210.8383 | 1131323.0276 | 2503227.3542 | 1131348.1449 | 2503229.0659 | 1131351.6196 | 2503228.8453 | 1131354.1914 | 2503227.1219 | 1131356.2314 | 2503223.3406 | 1131358.6602 | 2503219.9873 | 1131360.0878
34 | 2503209.1733 | 1131320.5417 | 2503207.5026 | 1131321.6931
35 | 2503212.4091 | 1131363.3141 | 2503219.9873 | 1131360.0878
36 | 2503176.9495 | 1131342.7499 | 2503207.5026 | 1131321.6931
37 | 2503199.5954 | 1131368.7693 | 2503212.4091 | 1131363.3141
38 | 2503176.9495 | 1131342.7499 | 2503173.8404 | 1131338.5861 | 2503165.4412 | 1131327.3827
39 | 2503176.9495 | 1131342.7499 | 2503146.624 | 1131364.2055
40 | 2503165.3825 | 1131327.3045 | 2503165.4412 | 1131327.3827
41 | 2503134.7742 | 1131372.5893 | 2503146.624 | 1131364.2055
42 | 2503134.7742 | 1131372.5893 | 2503127.8945 | 1131377.6166
43 | 2503134.7742 | 1131372.5893 | 2503138.7229 | 1131379.6303 | 2503154.4401 | 1131401.4843
44 | 2503112.5906 | 1131388.7997 | 2503127.8945 | 1131377.6166
45 | 2503303.9627 | 1131348.2586 | 2503298.2397 | 1131352.1068
46 | 2503303.5123 | 1131383.6684 | 2503298.2397 | 1131352.1068
47 | 2503312.5316 | 1131397.1322 | 2503306.8671 | 1131388.262 | 2503303.5123 | 1131383.6684
48 | 2503303.5123 | 1131383.6684 | 2503295.8627 | 1131388.8944
49 | 2503312.5316 | 1131397.1322 | 2503316.1342 | 1131402.778
50 | 2503312.5316 | 1131397.1322 | 2503307.7269 | 1131409.86
51 | 2503275.7611 | 1131403.8032 | 2503289.9969 | 1131392.9017 | 2503295.8627 | 1131388.8944
52 | 2503275.7611 | 1131403.8032 | 2503272.3511 | 1131400.0889 | 2503250.1733 | 1131370.3134
53 | 2503253.9319 | 1131426.2779 | 2503266.6 | 1131412.2441 | 2503275.7611 | 1131403.8032
54 | 2503253.9319 | 1131426.2779 | 2503244.9548 | 1131437.0618 | 2503249.7553 | 1131440.5536 | 2503256.5236 | 1131450.5291
55 | 2503253.9319 | 1131426.2779 | 2503244.9548 | 1131437.0618 | 2503226.7968 | 1131458.8774
56 | 2503253.9319 | 1131426.2779 | 2503250.9287 | 1131423.4354 | 2503243.4712 | 1131414.4474
57 | 2503256.5236 | 1131450.5291 | 2503254.9486 | 1131468.0651
58 | 2503256.5236 | 1131450.5291 | 2503273.5428 | 1131455.6348
59 | 2503226.7968 | 1131458.8774 | 2503222.5121 | 1131454.8881 | 2503192.9056 | 1131420.8086
60 | 2503226.7968 | 1131458.8774 | 2503215.4161 | 1131471.5195
61 | 2503237.4902 | 1131407.2388 | 2503243.4712 | 1131414.4474
62 | 2503254.9486 | 1131468.0651 | 2503275.72 | 1131512.7817
63 | 2503215.4161 | 1131471.5195 | 2503206.1613 | 1131481.8001 | 2503190.4761 | 1131495.9492 | 2503187.4315 | 1131498.2053
64 | 2503237.4902 | 1131407.2388 | 2503233.6502 | 1131402.6107 | 2503213.1644 | 1131416.629
65 | 2503316.1342 | 1131402.778 | 2503310.0648 | 1131420.5417 | 2503310.7494 | 1131424.333 | 2503313.2602 | 1131426.2495
66 | 2503336.6666 | 1131404.6169 | 2503333.9419 | 1131408.5741 | 2503316.1342 | 1131402.778
67 | 2503107.2673 | 1131392.5653 | 2503112.5906 | 1131388.7997
68 | 2503112.5906 | 1131388.7997 | 2503116.652 | 1131394.7048 | 2503130.9476 | 1131414.999
69 | 2503107.2673 | 1131392.5653 | 2503109.2751 | 1131395.2903 | 2503116.1845 | 1131404.4405 | 2503122.2909 | 1131417.7841 | 2503125.5947 | 1131422.3523
70 | 2503107.2673 | 1131392.5653 | 2503086.2928 | 1131407.7571
71 | 2503086.2928 | 1131407.7571 | 2503063.6378 | 1131424.1661
72 | 2503062.3707 | 1131425.0839 | 2503063.6378 | 1131424.1661
73 | 2503062.3707 | 1131425.0839 | 2503035.3417 | 1131444.5369
74 | 2503024.5598 | 1131452.2968 | 2503035.3417 | 1131444.5369
75 | 2503088.1272 | 1131461.0924 | 2503063.7647 | 1131478.283
76 | 2503088.1272 | 1131461.0924 | 2503106.2881 | 1131486.4831
77 | 2503088.1272 | 1131461.0924 | 2503101.7636 | 1131451.6319
78 | 2503115.2525 | 1131499.3916 | 2503106.2881 | 1131486.4831
79 | 2503106.2881 | 1131486.4831 | 2503128.5169 | 1131470.4673
80 | 2503041.0646 | 1131482.9283 | 2503043.7022 | 1131479.7951 | 2503029.5136 | 1131458.61 | 2503024.5598 | 1131452.2968
81 | 2503139.1038 | 1131532.8627 | 2503134.4356 | 1131526.1001 | 2503115.2525 | 1131499.3916
82 | 2503115.2525 | 1131499.3916 | 2503098.244 | 1131510.9827
83 | 2503142.02 | 1131460.7383 | 2503128.5169 | 1131470.4673
84 | 2503275.72 | 1131512.7817 | 2503277.4698 | 1131513.4284
85 | 2503187.4315 | 1131498.2053 | 2503172.9166 | 1131508.9611 | 2503153.3386 | 1131522.9705
86 | 2503187.4315 | 1131498.2053 | 2503203.7681 | 1131522.7303
87 | 2503139.1038 | 1131532.8627 | 2503102.0299 | 1131556.55
88 | 2503139.1038 | 1131532.8627 | 2503141.9715 | 1131531.1045
89 | 2503073.6873 | 1131516.3026 | 2503080.5147 | 1131519.3949 | 2503086.7821 | 1131518.7939 | 2503098.244 | 1131510.9827
90 | 2503142.02 | 1131460.7383 | 2503146.0022 | 1131457.8726
91 | 2503141.9715 | 1131531.1045 | 2503153.3386 | 1131522.9705
92 | 2503203.7681 | 1131522.7303 | 2503208.622 | 1131531.3337
93 | 2503245.6993 | 1131559.3471 | 2503253.2177 | 1131577.446
94 | 2503245.6993 | 1131559.3471 | 2503294.7784 | 1131537.4249
95 | 2503253.3496 | 1131577.7637 | 2503253.2177 | 1131577.446
96 | 2503294.7784 | 1131537.4249 | 2503285.4374 | 1131516.3728 | 2503277.4698 | 1131513.4284
97 | 2503294.7784 | 1131537.4249 | 2503313.225 | 1131529.3139
98 | 2503208.622 | 1131531.3337 | 2503210.2765 | 1131534.2663 | 2503205.8871 | 1131546.9805
99 | 2503203.005 | 1131555.3292 | 2503205.8871 | 1131546.9805
100 | 2503203.005 | 1131555.3292 | 2503216.9796 | 1131559.8077
101 | 2503203.005 | 1131555.3292 | 2503201.3042 | 1131560.2575
102 | 2503201.3042 | 1131560.2575 | 2503197.0748 | 1131572.5126
103 | 2503258.1646 | 1131589.3546 | 2503253.3496 | 1131577.7637
104 | 2503196.4616 | 1131581.9282 | 2503195.4466 | 1131577.2305 | 2503197.0748 | 1131572.5126
105 | 2503196.4616 | 1131581.9282 | 2503187.3173 | 1131586.1108
106 | 2503167.1581 | 1131591.1706 | 2503170.2144 | 1131591.5662 | 2503174.4026 | 1131591.4657 | 2503187.3173 | 1131586.1108
107 | 2503187.3173 | 1131586.1108 | 2503194.3928 | 1131603.3902
108 | 2503102.0299 | 1131556.55 | 2503105.4591 | 1131562.4208 | 2503110.4985 | 1131575.2601
109 | 2503097.1267 | 1131559.6084 | 2503102.0299 | 1131556.55
110 | 2503110.4985 | 1131575.2601 | 2503113.7226 | 1131583.4743
111 | 2503097.1267 | 1131559.6084 | 2503087.1439 | 1131544.7238
112 | 2503097.1267 | 1131559.6084 | 2503068.2735 | 1131577.5761
113 | 2503006.1599 | 1131549.7581 | 2503022.948 | 1131564.3426
114 | 2503049.2764 | 1131589.4062 | 2503045.6711 | 1131584.0831 | 2503022.948 | 1131564.3426
115 | 2503049.2764 | 1131589.4062 | 2503068.2735 | 1131577.5761
116 | 2503033.8959 | 1131598.9925 | 2503049.2764 | 1131589.4062
117 | 2502994.6677 | 1131623.7269 | 2503002.3128 | 1131617.8004 | 2503010.2129 | 1131612.8926 | 2503022.2315 | 1131605.9397 | 2503033.8959 | 1131598.9925
118 | 2503033.8959 | 1131598.9925 | 2503037.2198 | 1131605.0206 | 2503042.7901 | 1131616.1997
119 | 2502994.6677 | 1131623.7269 | 2502998.6233 | 1131629.2778 | 2503003.2469 | 1131638.0534 | 2503004.5902 | 1131640.762
120 | 2503085.4561 | 1131542.2073 | 2503087.1439 | 1131544.7238
121 | 2503016.7396 | 1131665.4836 | 2503012.9897 | 1131657.6978 | 2503004.5902 | 1131640.762
122 | 2503123.3493 | 1131608.0013 | 2503113.7226 | 1131583.4743
123 | 2503318.9996 | 1131526.7748 | 2503338.0276 | 1131518.2901
124 | 2503367.9575 | 1131504.9441 | 2503338.0276 | 1131518.2901
125 | 2503318.9996 | 1131526.7748 | 2503313.225 | 1131529.3139
126 | 2503318.9996 | 1131526.7748 | 2503320.333 | 1131532.6015 | 2503316.3912 | 1131544.8986
127 | 2503367.9575 | 1131504.9441 | 2503377.3276 | 1131526.988
128 | 2503367.9575 | 1131504.9441 | 2503380.6565 | 1131499.0817
129 | 2503316.3912 | 1131544.8986 | 2503310.1086 | 1131564.4979
130 | 2503306.7608 | 1131574.9417 | 2503310.1086 | 1131564.4979
131 | 2503306.3156 | 1131576.3306 | 2503306.7608 | 1131574.9417
132 | 2503373.9314 | 1131483.8767 | 2503370.5616 | 1131476.2577
133 | 2503380.6565 | 1131499.0817 | 2503373.9314 | 1131483.8767
134 | 2503360.2465 | 1131452.9357 | 2503370.5616 | 1131476.2577
135 | 2503380.6565 | 1131499.0817 | 2503407.8001 | 1131487.023
136 | 2503407.8001 | 1131487.023 | 2503452.3471 | 1131510.973
137 | 2503377.8448 | 1131534.7527 | 2503378.6502 | 1131530.0995 | 2503377.3276 | 1131526.988
138 | 2503489.8635 | 1131547.7867 | 2503485.5295 | 1131545.5102 | 2503452.3471 | 1131510.973
139 | 2503377.8448 | 1131534.7527 | 2503375.8788 | 1131546.113
140 | 2503530.6634 | 1131571.0932 | 2503489.8635 | 1131547.7867
141 | 2503167.1581 | 1131591.1706 | 2503164.9836 | 1131596.7645 | 2503171.6286 | 1131618.9976
142 | 2503200.1349 | 1131617.4133 | 2503194.3928 | 1131603.3902
143 | 2503123.3493 | 1131608.0013 | 2503125.5983 | 1131613.731
144 | 2503542.2003 | 1131565.7722 | 2503530.6634 | 1131571.0932
145 | 2503542.2003 | 1131565.7722 | 2503544.1574 | 1131571.122 | 2503551.8191 | 1131587.3363
146 | 2503542.2003 | 1131565.7722 | 2503544.1368 | 1131564.8778
147 | 2503574.5703 | 1131519.46 | 2503562.7346 | 1131528.3812
148 | 2503545.6516 | 1131541.2576 | 2503562.7346 | 1131528.3812
149 | 2503564.6388 | 1131514.8936 | 2503570.195 | 1131513.1594 | 2503574.5703 | 1131519.46
150 | 2503545.6516 | 1131541.2576 | 2503556.9101 | 1131558.9775
151 | 2503582.3645 | 1131563.7849 | 2503570.888 | 1131558.9208 | 2503562.9631 | 1131557.491 | 2503556.9101 | 1131558.9775
152 | 2503556.9101 | 1131558.9775 | 2503544.1368 | 1131564.8778
153 | 2503577.9243 | 1131570.282 | 2503581.4057 | 1131568.3697 | 2503582.3645 | 1131563.7849

## bus_geodata
| x | y | coords
0 | 2503426.7142 | 1131176.1894
1 | 2503407.7435 | 1131188.7801
2 | 2503400.5031 | 1131193.5767
3 | 2503420.7821 | 1131213.26
4 | 2503378.037 | 1131208.4947
5 | 2503454.8457 | 1131238.8433
6 | 2503407.3966 | 1131235.5629
7 | 2503382.6826 | 1131252.3087
8 | 2503427.3755 | 1131259.9096
9 | 2503355.1279 | 1131223.7082
10 | 2503331.9062 | 1131239.1292
11 | 2503318.7884 | 1131247.8404
12 | 2503315.9152 | 1131249.7432
13 | 2503354.6623 | 1131271.2849
14 | 2503423.8043 | 1131262.5865
15 | 2503411.5061 | 1131275.1284
16 | 2503302.0883 | 1131258.903
17 | 2503327.3003 | 1131288.6745
18 | 2503301.8598 | 1131305.0622
19 | 2503293.3226 | 1131264.71
20 | 2503382.7076 | 1131294.1692
21 | 2503359.3376 | 1131310.5811
22 | 2503388.5904 | 1131290.038
23 | 2503277.6205 | 1131275.1121
24 | 2503252.0793 | 1131292.0323
25 | 2503246.5005 | 1131295.728
26 | 2503328.4342 | 1131331.8037
27 | 2503332.8295 | 1131328.8482
28 | 2503228.1545 | 1131307.88
29 | 2503260.608 | 1131316.8048
30 | 2503212.3728 | 1131318.3335
31 | 2503209.1733 | 1131320.5417
32 | 2503247.0388 | 1131341.5613
33 | 2503219.9873 | 1131360.0878
34 | 2503207.5026 | 1131321.6931
35 | 2503212.4091 | 1131363.3141
36 | 2503176.9495 | 1131342.7499
37 | 2503165.4412 | 1131327.3827
38 | 2503146.624 | 1131364.2055
39 | 2503165.3825 | 1131327.3045
40 | 2503134.7742 | 1131372.5893
41 | 2503127.8945 | 1131377.6166
42 | 2503154.4401 | 1131401.4843
43 | 2503199.5954 | 1131368.7693
44 | 2503303.9627 | 1131348.2586
45 | 2503298.2397 | 1131352.1068
46 | 2503303.5123 | 1131383.6684
47 | 2503312.5316 | 1131397.1322
48 | 2503295.8627 | 1131388.8944
49 | 2503250.1733 | 1131370.3134
50 | 2503275.7611 | 1131403.8032
51 | 2503253.9319 | 1131426.2779
52 | 2503256.5236 | 1131450.5291
53 | 2503226.7968 | 1131458.8774
54 | 2503243.4712 | 1131414.4474
55 | 2503254.9486 | 1131468.0651
56 | 2503273.5428 | 1131455.6348
57 | 2503192.9056 | 1131420.8086
58 | 2503215.4161 | 1131471.5195
59 | 2503237.4902 | 1131407.2388
60 | 2503316.1342 | 1131402.778
61 | 2503307.7269 | 1131409.86
62 | 2503313.2602 | 1131426.2495
63 | 2503336.6666 | 1131404.6169
64 | 2503213.1644 | 1131416.629
65 | 2503112.5906 | 1131388.7997
66 | 2503107.2673 | 1131392.5653
67 | 2503130.9476 | 1131414.999
68 | 2503125.5947 | 1131422.3523
69 | 2503086.2928 | 1131407.7571
70 | 2503063.6378 | 1131424.1661
71 | 2503062.3707 | 1131425.0839
72 | 2503035.3417 | 1131444.5369
73 | 2503088.1271 | 1131461.0924
74 | 2503063.7647 | 1131478.283
75 | 2503106.2881 | 1131486.4831
76 | 2503101.7636 | 1131451.6319
77 | 2503024.5598 | 1131452.2968
78 | 2503115.2525 | 1131499.3916
79 | 2503128.5169 | 1131470.4673
80 | 2503041.0646 | 1131482.9283
81 | 2503275.72 | 1131512.7817
82 | 2503187.4315 | 1131498.2053
83 | 2503139.1038 | 1131532.8627
84 | 2503098.244 | 1131510.9827
85 | 2503142.02 | 1131460.7383
86 | 2503153.3386 | 1131522.9705
87 | 2503203.7681 | 1131522.7303
88 | 2503141.9715 | 1131531.1045
89 | 2503245.6993 | 1131559.3471
90 | 2503253.2177 | 1131577.446
91 | 2503294.7784 | 1131537.4249
92 | 2503208.622 | 1131531.3337
93 | 2503205.8871 | 1131546.9805
94 | 2503203.005 | 1131555.3292
95 | 2503216.9796 | 1131559.8077
96 | 2503201.3041 | 1131560.2575
97 | 2503253.3496 | 1131577.7637
98 | 2503258.1646 | 1131589.3546
99 | 2503197.0748 | 1131572.5126
100 | 2503196.4616 | 1131581.9282
101 | 2503187.3173 | 1131586.1108
102 | 2503102.0299 | 1131556.55
103 | 2503146.0022 | 1131457.8726
104 | 2503073.6873 | 1131516.3026
105 | 2503110.4985 | 1131575.2601
106 | 2503097.1267 | 1131559.6084
107 | 2503006.1599 | 1131549.7581
108 | 2503022.948 | 1131564.3426
109 | 2503049.2764 | 1131589.4062
110 | 2503068.2735 | 1131577.5761
111 | 2503033.8959 | 1131598.9925
112 | 2502994.6677 | 1131623.7269
113 | 2503042.7901 | 1131616.1997
114 | 2503087.1439 | 1131544.7238
115 | 2503004.5902 | 1131640.762
116 | 2503085.4561 | 1131542.2073
117 | 2503113.7226 | 1131583.4743
118 | 2503338.0276 | 1131518.2901
119 | 2503318.9996 | 1131526.7748
120 | 2503367.9575 | 1131504.9441
121 | 2503313.225 | 1131529.3139
122 | 2503316.3912 | 1131544.8986
123 | 2503310.1086 | 1131564.4979
124 | 2503277.4698 | 1131513.4284
125 | 2503306.7608 | 1131574.9417
126 | 2503306.3156 | 1131576.3306
127 | 2503373.9314 | 1131483.8767
128 | 2503370.5616 | 1131476.2577
129 | 2503380.6565 | 1131499.0817
130 | 2503360.2465 | 1131452.9357
131 | 2503407.8001 | 1131487.023
132 | 2503377.3276 | 1131526.988
133 | 2503452.3471 | 1131510.973
134 | 2503377.8448 | 1131534.7527
135 | 2503489.8635 | 1131547.7867
136 | 2503375.8788 | 1131546.113
137 | 2503167.1581 | 1131591.1706
138 | 2503194.3928 | 1131603.3902
139 | 2503171.6286 | 1131618.9976
140 | 2503200.1349 | 1131617.4133
141 | 2503123.3493 | 1131608.0013
142 | 2503125.5983 | 1131613.731
143 | 2503016.7396 | 1131665.4836
144 | 2503530.6634 | 1131571.0932
145 | 2503542.2003 | 1131565.7722
146 | 2503562.7346 | 1131528.3812
147 | 2503574.5703 | 1131519.46
148 | 2503545.6516 | 1131541.2576
149 | 2503564.6388 | 1131514.8936
150 | 2503556.9101 | 1131558.9775
151 | 2503582.3645 | 1131563.7849
152 | 2503544.1368 | 1131564.8778
153 | 2503577.9243 | 1131570.282
154 | 2503551.8191 | 1131587.3363
155 | 2503253.9319 | 1131426.2779

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1