## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5890-20_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5890-20_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5890-20_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_5890-20_0_6_node_19 | 0.4 | n |  | TRUE
4 | bus_LV_5890-20_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5890-20_0_6_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_5890-20_0_6_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_5890-20_0_6_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_5890-20_0_6_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_5890-20_0_6_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_5890-20_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_5890-20_0_6_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_5890-20_0_6_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_5890-20_0_6_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_5890-20_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_5890-20_0_6_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_5890-20_0_6_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_5890-20_0_6_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_5890-20_0_6_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_5890-20_0_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_5890-20_0_6_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_5890-20_0_6_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_5890-20_0_6_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_5890-20_0_6_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_5890-20_0_6_node_16 | 0.4 | n |  | TRUE
25 | bus_MV_263_0_node_81 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5890-20_0_6_load_0 | 0 | 0.081902 | 0.020526 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5890-20_0_6_load_1 | 1 | 0.024456 | 0.0061293 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5890-20_0_6_load_3 | 2 | 0.018562 | 0.0046521 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5890-20_0_6_load_19 | 3 | 0.0077193 | 0.0019346 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5890-20_0_6_load_4 | 4 | 0.0052772 | 0.0013226 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5890-20_0_6_load_8 | 5 | 0.063494 | 0.015913 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5890-20_0_6_load_24 | 8 | 0.016931 | 0.0042432 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5890-20_0_6_load_20 | 9 | 0.021559 | 0.0054033 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5890-20_0_6_load_14 | 11 | 0.025087 | 0.0062874 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5890-20_0_6_load_11 | 12 | 0.018793 | 0.0047099 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5890-20_0_6_load_9 | 14 | 0.0083589 | 0.0020949 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5890-20_0_6_load_23 | 15 | 0.019796 | 0.0049614 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5890-20_0_6_load_10 | 16 | 0.041049 | 0.010288 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5890-20_0_6_load_25 | 17 | 0.022858 | 0.0057287 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5890-20_0_6_load_12 | 18 | 0.013098 | 0.0032827 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5890-20_0_6_load_13 | 19 | 0.013281 | 0.0033286 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5890-20_0_6_load_21 | 20 | 0.014606 | 0.0036607 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5890-20_0_6_load_22 | 21 | 0.075554 | 0.018936 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5890-20_0_6_load_18 | 22 | 0.023983 | 0.0060107 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5890-20_0_6_load_15 | 23 | 0.031628 | 0.0079267 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5890-20_0_6_load_16 | 24 | 0.035001 | 0.008772 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5890-20_0_6_line_0 |  | 0 | 1 | 0.028108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5890-20_0_6_line_1 |  | 1 | 2 | 0.01622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5890-20_0_6_line_2 |  | 2 | 3 | 0.021527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5890-20_0_6_line_3 |  | 3 | 13 | 0.021016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5890-20_0_6_line_4 |  | 4 | 5 | 0.012825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5890-20_0_6_line_5 |  | 5 | 14 | 0.032078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5890-20_0_6_line_6 |  | 6 | 7 | 0.008967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5890-20_0_6_line_7 |  | 6 | 8 | 0.017398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5890-20_0_6_line_8 |  | 7 | 9 | 0.0014307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5890-20_0_6_line_9 |  | 8 | 15 | 0.013415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_5890-20_0_6_line_10 |  | 9 | 16 | 0.016651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5890-20_0_6_line_11 |  | 10 | 11 | 0.016622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_5890-20_0_6_line_12 |  | 10 | 12 | 0.019694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_5890-20_0_6_line_13 |  | 11 | 17 | 0.014579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_5890-20_0_6_line_14 |  | 12 | 18 | 0.011187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_5890-20_0_6_line_15 |  | 13 | 23 | 0.035094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5890-20_0_6_line_16 |  | 14 | 16 | 0.05375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5890-20_0_6_line_17 |  | 15 | 21 | 0.003894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_5890-20_0_6_line_18 |  | 17 | 22 | 0.014913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_5890-20_0_6_line_19 |  | 18 | 19 | 0.012959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_5890-20_0_6_line_20 |  | 19 | 20 | 0.013883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_5890-20_0_6_line_21 |  | 20 | 21 | 0.010614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_5890-20_0_6_line_22 |  | 22 | 24 | 0.016515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_5890-20_0_6_line_23 |  | 23 | 24 | 0.022502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5890-20_0_6_trafo_22 | 0.63 MVA 20/0.4 kV | 25 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2553770.7036 | 1145618.2137 | 2553794.2654 | 1145602.8879
1 | 2553807.9017 | 1145594.1053 | 2553797.6585 | 1145600.6808 | 2553794.2654 | 1145602.8879
2 | 2553826.0175 | 1145582.4761 | 2553807.9017 | 1145594.1053
3 | 2553843.7029 | 1145571.1232 | 2553826.0175 | 1145582.4761
4 | 2553719.1264 | 1145698.4261 | 2553706.8366 | 1145694.7615
5 | 2553719.1264 | 1145698.4261 | 2553749.867 | 1145707.5925
6 | 2553818.7037 | 1145728.1184 | 2553827.3199 | 1145730.6869
7 | 2553827.3199 | 1145730.6869 | 2553838.0164 | 1145723.0453 | 2553841.4715 | 1145720.5662
8 | 2553818.7037 | 1145728.1184 | 2553817.3326 | 1145727.7095
9 | 2553852.3714 | 1145712.7452 | 2553841.4715 | 1145720.5662
10 | 2553801.3756 | 1145722.9514 | 2553817.3326 | 1145727.7095
11 | 2553911.0573 | 1145670.6361 | 2553901.8604 | 1145656.7901
12 | 2553911.0573 | 1145670.6361 | 2553895.056 | 1145682.1176
13 | 2553901.8604 | 1145656.7901 | 2553893.7941 | 1145644.6462
14 | 2553885.9671 | 1145688.6391 | 2553895.056 | 1145682.1176
15 | 2553843.7029 | 1145571.1232 | 2553849.1833 | 1145577.4845 | 2553863.9548 | 1145599.7231
16 | 2553801.3756 | 1145722.9514 | 2553749.867 | 1145707.5925
17 | 2553855.5352 | 1145710.475 | 2553852.3714 | 1145712.7452
18 | 2553885.5427 | 1145632.2237 | 2553893.7941 | 1145644.6462
19 | 2553885.9671 | 1145688.6391 | 2553875.4385 | 1145696.1938
20 | 2553875.4385 | 1145696.1938 | 2553864.1586 | 1145704.2875
21 | 2553855.5352 | 1145710.475 | 2553864.1586 | 1145704.2875
22 | 2553876.4048 | 1145618.4667 | 2553885.5427 | 1145632.2237
23 | 2553876.4048 | 1145618.4667 | 2553863.9548 | 1145599.7231

## bus_geodata
| x | y | coords
0 | 2553770.7036 | 1145618.2137
1 | 2553794.2654 | 1145602.8879
2 | 2553807.9017 | 1145594.1053
3 | 2553826.0175 | 1145582.4761
4 | 2553706.8366 | 1145694.7615
5 | 2553719.1264 | 1145698.4261
6 | 2553827.3199 | 1145730.6869
7 | 2553818.7037 | 1145728.1184
8 | 2553841.4715 | 1145720.5662
9 | 2553817.3326 | 1145727.7095
10 | 2553911.0573 | 1145670.6361
11 | 2553901.8604 | 1145656.7901
12 | 2553895.056 | 1145682.1176
13 | 2553843.7029 | 1145571.1232
14 | 2553749.867 | 1145707.5925
15 | 2553852.3714 | 1145712.7452
16 | 2553801.3756 | 1145722.9514
17 | 2553893.7941 | 1145644.6462
18 | 2553885.9671 | 1145688.6391
19 | 2553875.4385 | 1145696.1938
20 | 2553864.1586 | 1145704.2875
21 | 2553855.5352 | 1145710.475
22 | 2553885.5427 | 1145632.2237
23 | 2553863.9548 | 1145599.7231
24 | 2553876.4048 | 1145618.4667
25 | 2553827.3199 | 1145730.6869

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9743 | -0.49584 | 0.081902 | 0.020526
1 | 0.97644 | -0.45367 | 0.024456 | 0.0061293
2 | 0.97805 | -0.42218 | 0.018562 | 0.0046521
3 | 0.98055 | -0.37331 | 0.0077193 | 0.0019346
4 | 0.98758 | -0.23917 | 0.0052772 | 0.0013226
5 | 0.98764 | -0.23796 | 0.063494 | 0.015913
6 | 0.9966 | -0.064905 | 0 | 0
7 | 0.99545 | -0.08692 | 0 | 0
8 | 0.99883 | -0.022336 | 0.016931 | 0.0042432
9 | 0.99527 | -0.090437 | 0.021559 | 0.0054033
10 | 0.99372 | -0.11938 | 0 | 0
11 | 0.99233 | -0.14594 | 0.025087 | 0.0062874
12 | 0.99537 | -0.088004 | 0.018793 | 0.0047099
13 | 0.98314 | -0.32291 | 0 | 0
14 | 0.98966 | -0.19862 | 0.0083589 | 0.0020949
15 | 0.99979 | -0.0039932 | 0.019796 | 0.0049614
16 | 0.99347 | -0.12513 | 0.041049 | 0.010288
17 | 0.99123 | -0.16713 | 0.022858 | 0.0057287
18 | 0.99636 | -0.068999 | 0.013098 | 0.0032827
19 | 0.99757 | -0.046041 | 0.013281 | 0.0033286
20 | 0.99892 | -0.020432 | 0.014606 | 0.0036607
21 | 1 | 0 | -0.51482 | -0.13084
22 | 0.9902 | -0.18684 | 0.023983 | 0.0060107
23 | 0.98747 | -0.23934 | 0.031628 | 0.0079267
24 | 0.98919 | -0.20636 | 0.035001 | 0.008772
25 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.081902 | -0.020526 | 0.082066 | 0.020632 | 0.00016492 | 0.0001052 | 0.12509 | 0.12509 | 0.12509 | 0.9743 | -0.49584 | 0.97644 | -0.45367 | 34.3642
1 | -0.10652 | -0.026761 | 0.10668 | 0.026863 | 0.00016033 | 0.00010241 | 0.16235 | 0.16235 | 0.16235 | 0.97644 | -0.45367 | 0.97805 | -0.42218 | 44.603
2 | -0.12525 | -0.031515 | 0.12554 | 0.031703 | 0.00029325 | 0.00018741 | 0.1906 | 0.1906 | 0.1906 | 0.97805 | -0.42218 | 0.98055 | -0.37331 | 52.3614
3 | -0.13326 | -0.033638 | 0.13358 | 0.033844 | 0.00032256 | 0.00020617 | 0.20231 | 0.20231 | 0.20231 | 0.98055 | -0.37331 | 0.98314 | -0.32291 | 55.5796
4 | -0.0052772 | -0.0013226 | 0.0052775 | 0.0013226 | 3.0405e-07 | 3.049e-08 | 0.0079513 | 0.0079513 | 0.0079513 | 0.98758 | -0.23917 | 0.98764 | -0.23796 | 2.1844
5 | -0.068771 | -0.017236 | 0.0689 | 0.017318 | 0.00012914 | 8.224e-05 | 0.10361 | 0.10361 | 0.10361 | 0.98764 | -0.23796 | 0.98966 | -0.19862 | 28.4652
6 | 0.14051 | 0.035513 | -0.14036 | -0.035418 | 0.00014815 | 9.4696e-05 | 0.2099 | 0.2099 | 0.2099 | 0.9966 | -0.064905 | 0.99545 | -0.08692 | 57.6639
7 | -0.14051 | -0.035513 | 0.1408 | 0.035697 | 0.00028744 | 0.00018373 | 0.2099 | 0.2099 | 0.2099 | 0.9966 | -0.064905 | 0.99883 | -0.022336 | 57.6639
8 | 0.14036 | 0.035418 | -0.14034 | -0.035403 | 2.3638e-05 | 1.511e-05 | 0.2099 | 0.2099 | 0.2099 | 0.99545 | -0.08692 | 0.99527 | -0.090437 | 57.6639
9 | -0.15773 | -0.03994 | 0.15787 | 0.040029 | 0.00013905 | 8.8643e-05 | 0.23512 | 0.23512 | 0.23512 | 0.99883 | -0.022336 | 0.99979 | -0.0039932 | 32.2966
10 | 0.11878 | 0.03 | -0.11858 | -0.029874 | 0.0001971 | 0.00012593 | 0.17766 | 0.17766 | 0.17766 | 0.99527 | -0.090437 | 0.99347 | -0.12513 | 48.8086
11 | 0.27395 | 0.069723 | -0.27359 | -0.0695 | 0.00035028 | 0.00022353 | 0.41059 | 0.41059 | 0.41059 | 0.99372 | -0.11938 | 0.99233 | -0.14594 | 37.5998
12 | -0.27395 | -0.069723 | 0.27436 | 0.069988 | 0.00041502 | 0.00026485 | 0.41059 | 0.41059 | 0.41059 | 0.99372 | -0.11938 | 0.99537 | -0.088004 | 37.5998
13 | 0.24851 | 0.063212 | -0.24825 | -0.063051 | 0.0002535 | 0.00016168 | 0.37297 | 0.37297 | 0.37297 | 0.99233 | -0.14594 | 0.99123 | -0.16713 | 34.155
14 | -0.29315 | -0.074698 | 0.29342 | 0.07487 | 0.0002691 | 0.00017178 | 0.43868 | 0.43868 | 0.43868 | 0.99537 | -0.088004 | 0.99636 | -0.068999 | 40.1724
15 | -0.13358 | -0.033844 | 0.13412 | 0.034188 | 0.00053864 | 0.00034428 | 0.20231 | 0.20231 | 0.20231 | 0.98314 | -0.32291 | 0.98747 | -0.23934 | 55.5795
16 | -0.077259 | -0.019413 | 0.077531 | 0.019586 | 0.00027207 | 0.00017343 | 0.11618 | 0.11618 | 0.11618 | 0.98966 | -0.19862 | 0.99347 | -0.12513 | 31.9179
17 | -0.17766 | -0.04499 | 0.1777 | 0.045012 | 3.4075e-05 | 2.1655e-05 | 0.26458 | 0.26458 | 0.26458 | 0.99979 | -0.0039932 | 1 | 0 | 24.2291
18 | 0.2254 | 0.057322 | -0.22518 | -0.057186 | 0.0002138 | 0.00013626 | 0.33866 | 0.33866 | 0.33866 | 0.99123 | -0.16713 | 0.9902 | -0.18684 | 31.0127
19 | -0.30652 | -0.078153 | 0.30686 | 0.07837 | 0.00034014 | 0.00021719 | 0.45824 | 0.45824 | 0.45824 | 0.99636 | -0.068999 | 0.99757 | -0.046041 | 41.9638
20 | -0.32014 | -0.081698 | 0.32054 | 0.081952 | 0.0003966 | 0.00025328 | 0.47805 | 0.47805 | 0.47805 | 0.99757 | -0.046041 | 0.99892 | -0.020432 | 43.7779
21 | -0.33514 | -0.085612 | 0.33548 | 0.085824 | 0.00033142 | 0.00021169 | 0.49981 | 0.49981 | 0.49981 | 0.99892 | -0.020432 | 1 | 0 | 45.7703
22 | 0.2012 | 0.051175 | -0.20101 | -0.051055 | 0.00018906 | 0.00012036 | 0.30262 | 0.30262 | 0.30262 | 0.9902 | -0.18684 | 0.98919 | -0.20636 | 27.7124
23 | -0.16575 | -0.042115 | 0.16601 | 0.042283 | 0.00026363 | 0.00016814 | 0.24997 | 0.24997 | 0.24997 | 0.98747 | -0.23934 | 0.98919 | -0.20636 | 34.3364

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59037 | 0.14977

## res_load
| p_mw | q_mvar
0 | 0.081902 | 0.020526
1 | 0.024456 | 0.0061293
2 | 0.018562 | 0.0046521
3 | 0.0077193 | 0.0019346
4 | 0.0052772 | 0.0013226
5 | 0.063494 | 0.015913
6 | 0.016931 | 0.0042432
7 | 0.021559 | 0.0054033
8 | 0.025087 | 0.0062874
9 | 0.018793 | 0.0047099
10 | 0.0083589 | 0.0020949
11 | 0.019796 | 0.0049614
12 | 0.041049 | 0.010288
13 | 0.022858 | 0.0057287
14 | 0.013098 | 0.0032827
15 | 0.013281 | 0.0033286
16 | 0.014606 | 0.0036607
17 | 0.075554 | 0.018936
18 | 0.023983 | 0.0060107
19 | 0.031628 | 0.0079267
20 | 0.035001 | 0.008772

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1