## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5909-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5909-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5909-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5909-1_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5909-1_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_5909-1_0_3_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_5909-1_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_5909-1_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_5909-1_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5909-1_0_3_node_65 | 0.4 | n |  | TRUE
10 | bus_LV_5909-1_0_3_node_87 | 0.4 | n |  | TRUE
11 | bus_LV_5909-1_0_3_node_100 | 0.4 | n |  | TRUE
12 | bus_LV_5909-1_0_3_node_98 | 0.4 | n |  | TRUE
13 | bus_LV_5909-1_0_3_node_96 | 0.4 | n |  | TRUE
14 | bus_LV_5909-1_0_3_node_73 | 0.4 | n |  | TRUE
15 | bus_LV_5909-1_0_3_node_68 | 0.4 | n |  | TRUE
16 | bus_LV_5909-1_0_3_node_99 | 0.4 | n |  | TRUE
17 | bus_LV_5909-1_0_3_node_114 | 0.4 | n |  | TRUE
18 | bus_LV_5909-1_0_3_node_69 | 0.4 | n |  | TRUE
19 | bus_LV_5909-1_0_3_node_112 | 0.4 | n |  | TRUE
20 | bus_LV_5909-1_0_3_node_141 | 0.4 | n |  | TRUE
21 | bus_LV_5909-1_0_3_node_144 | 0.4 | n |  | TRUE
22 | bus_LV_5909-1_0_3_node_67 | 0.4 | n |  | TRUE
23 | bus_LV_5909-1_0_3_node_63 | 0.4 | n |  | TRUE
24 | bus_LV_5909-1_0_3_node_88 | 0.4 | n |  | TRUE
25 | bus_LV_5909-1_0_3_node_146 | 0.4 | n |  | TRUE
26 | bus_LV_5909-1_0_3_node_97 | 0.4 | n |  | TRUE
27 | bus_LV_5909-1_0_3_node_158 | 0.4 | n |  | TRUE
28 | bus_LV_5909-1_0_3_node_110 | 0.4 | n |  | TRUE
29 | bus_LV_5909-1_0_3_node_113 | 0.4 | n |  | TRUE
30 | bus_LV_5909-1_0_3_node_108 | 0.4 | n |  | TRUE
31 | bus_LV_5909-1_0_3_node_118 | 0.4 | n |  | TRUE
32 | bus_LV_5909-1_0_3_node_115 | 0.4 | n |  | TRUE
33 | bus_LV_5909-1_0_3_node_119 | 0.4 | n |  | TRUE
34 | bus_LV_5909-1_0_3_node_111 | 0.4 | n |  | TRUE
35 | bus_LV_5909-1_0_3_node_117 | 0.4 | n |  | TRUE
36 | bus_LV_5909-1_0_3_node_116 | 0.4 | n |  | TRUE
37 | bus_LV_5909-1_0_3_node_64 | 0.4 | n |  | TRUE
38 | bus_LV_5909-1_0_3_node_70 | 0.4 | n |  | TRUE
39 | bus_LV_5909-1_0_3_node_71 | 0.4 | n |  | TRUE
40 | bus_LV_5909-1_0_3_node_145 | 0.4 | n |  | TRUE
41 | bus_LV_5909-1_0_3_node_130 | 0.4 | n |  | TRUE
42 | bus_LV_5909-1_0_3_node_109 | 0.4 | n |  | TRUE
43 | bus_LV_5909-1_0_3_node_142 | 0.4 | n |  | TRUE
44 | bus_LV_5909-1_0_3_node_72 | 0.4 | n |  | TRUE
45 | bus_LV_5909-1_0_3_node_74 | 0.4 | n |  | TRUE
46 | bus_LV_5909-1_0_3_node_75 | 0.4 | n |  | TRUE
47 | bus_LV_5909-1_0_3_node_94 | 0.4 | n |  | TRUE
48 | bus_LV_5909-1_0_3_node_76 | 0.4 | n |  | TRUE
49 | bus_LV_5909-1_0_3_node_92 | 0.4 | n |  | TRUE
50 | bus_LV_5909-1_0_3_node_77 | 0.4 | n |  | TRUE
51 | bus_LV_5909-1_0_3_node_78 | 0.4 | n |  | TRUE
52 | bus_LV_5909-1_0_3_node_80 | 0.4 | n |  | TRUE
53 | bus_LV_5909-1_0_3_node_95 | 0.4 | n |  | TRUE
54 | bus_LV_5909-1_0_3_node_81 | 0.4 | n |  | TRUE
55 | bus_LV_5909-1_0_3_node_85 | 0.4 | n |  | TRUE
56 | bus_LV_5909-1_0_3_node_149 | 0.4 | n |  | TRUE
57 | bus_LV_5909-1_0_3_node_151 | 0.4 | n |  | TRUE
58 | bus_LV_5909-1_0_3_node_154 | 0.4 | n |  | TRUE
59 | bus_LV_5909-1_0_3_node_155 | 0.4 | n |  | TRUE
60 | bus_LV_5909-1_0_3_node_152 | 0.4 | n |  | TRUE
61 | bus_LV_5909-1_0_3_node_156 | 0.4 | n |  | TRUE
62 | bus_LV_5909-1_0_3_node_153 | 0.4 | n |  | TRUE
63 | bus_LV_5909-1_0_3_node_161 | 0.4 | n |  | TRUE
64 | bus_LV_5909-1_0_3_node_162 | 0.4 | n |  | TRUE
65 | bus_LV_5909-1_0_3_node_83 | 0.4 | n |  | TRUE
66 | bus_LV_5909-1_0_3_node_82 | 0.4 | n |  | TRUE
67 | bus_LV_5909-1_0_3_node_84 | 0.4 | n |  | TRUE
68 | bus_LV_5909-1_0_3_node_86 | 0.4 | n |  | TRUE
69 | bus_LV_5909-1_0_3_node_93 | 0.4 | n |  | TRUE
70 | bus_LV_5909-1_0_3_node_147 | 0.4 | n |  | TRUE
71 | bus_LV_5909-1_0_3_node_91 | 0.4 | n |  | TRUE
72 | bus_LV_5909-1_0_3_node_89 | 0.4 | n |  | TRUE
73 | bus_LV_5909-1_0_3_node_90 | 0.4 | n |  | TRUE
74 | bus_LV_5909-1_0_3_node_102 | 0.4 | n |  | TRUE
75 | bus_LV_5909-1_0_3_node_103 | 0.4 | n |  | TRUE
76 | bus_LV_5909-1_0_3_node_104 | 0.4 | n |  | TRUE
77 | bus_LV_5909-1_0_3_node_105 | 0.4 | n |  | TRUE
78 | bus_LV_5909-1_0_3_node_106 | 0.4 | n |  | TRUE
79 | bus_LV_5909-1_0_3_node_107 | 0.4 | n |  | TRUE
80 | bus_LV_5909-1_0_3_node_131 | 0.4 | n |  | TRUE
81 | bus_LV_5909-1_0_3_node_143 | 0.4 | n |  | TRUE
82 | bus_MV_455_0_node_177 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5909-1_0_3_load_0 | 0 | 0.0051283 | 0.0012853 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5909-1_0_3_load_1 | 1 | 0.00042309 | 0.00010604 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5909-1_0_3_load_3 | 3 | 0.0012234 | 0.00030662 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5909-1_0_3_load_87 | 10 | 0.0022088 | 0.00055357 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5909-1_0_3_load_100 | 11 | 0.0054896 | 0.0013758 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5909-1_0_3_load_98 | 12 | 0.0011131 | 0.00027897 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5909-1_0_3_load_96 | 13 | 0.0023054 | 0.0005778 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5909-1_0_3_load_73 | 14 | 0.0025306 | 0.00063424 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5909-1_0_3_load_99 | 16 | 0.0030957 | 0.00077586 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5909-1_0_3_load_141 | 20 | 0.0033231 | 0.00083284 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5909-1_0_3_load_144 | 21 | 0.0033823 | 0.00084769 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5909-1_0_3_load_67 | 22 | 0.0033781 | 0.00084662 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5909-1_0_3_load_63 | 23 | 0.0039875 | 0.00099936 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5909-1_0_3_load_88 | 24 | 0.0029985 | 0.0007515 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5909-1_0_3_load_146 | 25 | 0.0051663 | 0.0012948 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5909-1_0_3_load_97 | 26 | 0.0016018 | 0.00040146 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5909-1_0_3_load_158 | 27 | 0.012925 | 0.0032394 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5909-1_0_3_load_108 | 30 | 0.0033366 | 0.00083622 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5909-1_0_3_load_118 | 31 | 0.0034789 | 0.00087188 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5909-1_0_3_load_115 | 32 | 0.0028374 | 0.00071112 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5909-1_0_3_load_119 | 33 | 0.012154 | 0.003046 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5909-1_0_3_load_111 | 34 | 0.0070008 | 0.0017546 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5909-1_0_3_load_117 | 35 | 0.0032306 | 0.00080967 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5909-1_0_3_load_116 | 36 | 0.0034375 | 0.00086152 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5909-1_0_3_load_64 | 37 | 0.005496 | 0.0013774 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5909-1_0_3_load_70 | 38 | 0.0024954 | 0.00062541 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5909-1_0_3_load_145 | 40 | 0.0032912 | 0.00082485 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5909-1_0_3_load_130 | 41 | 0.0015521 | 0.00038899 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5909-1_0_3_load_142 | 43 | 0.0036665 | 0.00091892 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5909-1_0_3_load_72 | 44 | 0.0025946 | 0.00065027 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5909-1_0_3_load_74 | 45 | 0.0043235 | 0.0010836 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5909-1_0_3_load_75 | 46 | 0.0027642 | 0.00069277 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5909-1_0_3_load_94 | 47 | 0.0057797 | 0.0014485 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5909-1_0_3_load_76 | 48 | 0.0036453 | 0.00091359 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5909-1_0_3_load_92 | 49 | 0.0036097 | 0.00090467 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5909-1_0_3_load_77 | 50 | 0.002864 | 0.00071778 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5909-1_0_3_load_78 | 51 | 0.0018525 | 0.00046429 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5909-1_0_3_load_80 | 52 | 0.001635 | 0.00040977 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5909-1_0_3_load_95 | 53 | 0.0043389 | 0.0010874 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5909-1_0_3_load_85 | 55 | 0.0030434 | 0.00076274 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5909-1_0_3_load_155 | 59 | 0.00184 | 0.00046114 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5909-1_0_3_load_161 | 63 | 0.0070296 | 0.0017618 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5909-1_0_3_load_162 | 64 | 0.0038365 | 0.00096151 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5909-1_0_3_load_83 | 65 | 0.0013354 | 0.00033469 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5909-1_0_3_load_82 | 66 | 0.0019784 | 0.00049584 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5909-1_0_3_load_84 | 67 | 0.0032061 | 0.00080353 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5909-1_0_3_load_86 | 68 | 0.0038194 | 0.00095722 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5909-1_0_3_load_93 | 69 | 0.0013881 | 0.00034789 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5909-1_0_3_load_147 | 70 | 0.0011819 | 0.00029621 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5909-1_0_3_load_91 | 71 | 0.0049307 | 0.0012357 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5909-1_0_3_load_89 | 72 | 0.002791 | 0.00069948 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5909-1_0_3_load_90 | 73 | 0.0028343 | 0.00071033 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5909-1_0_3_load_102 | 74 | 0.0028375 | 0.00071114 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5909-1_0_3_load_103 | 75 | 0.0028252 | 0.00070805 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5909-1_0_3_load_105 | 77 | 0.0041368 | 0.0010368 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5909-1_0_3_load_106 | 78 | 0.0018835 | 0.00047204 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5909-1_0_3_load_107 | 79 | 0.0024082 | 0.00060354 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5909-1_0_3_load_131 | 80 | 0.0027454 | 0.00068806 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5909-1_0_3_load_143 | 81 | 0.0025331 | 0.00063485 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5909-1_0_3_line_0 |  | 0 | 1 | 0.029474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5909-1_0_3_line_1 |  | 0 | 2 | 0.073214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5909-1_0_3_line_2 |  | 1 | 3 | 0.023889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5909-1_0_3_line_3 |  | 2 | 4 | 0.05197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5909-1_0_3_line_4 |  | 2 | 5 | 0.078855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5909-1_0_3_line_5 |  | 4 | 11 | 0.064757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5909-1_0_3_line_6 |  | 4 | 12 | 0.070398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5909-1_0_3_line_7 |  | 5 | 17 | 0.057505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5909-1_0_3_line_8 |  | 6 | 7 | 0.014827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5909-1_0_3_line_9 |  | 6 | 8 | 0.020344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5909-1_0_3_line_10 |  | 6 | 9 | 0.049155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5909-1_0_3_line_11 |  | 6 | 10 | 0.024038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5909-1_0_3_line_12 |  | 7 | 15 | 0.034653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5909-1_0_3_line_13 |  | 7 | 16 | 0.074615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5909-1_0_3_line_14 |  | 8 | 13 | 0.018725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5909-1_0_3_line_15 |  | 8 | 14 | 0.049099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5909-1_0_3_line_16 |  | 9 | 22 | 0.022201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5909-1_0_3_line_17 |  | 9 | 23 | 0.065792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5909-1_0_3_line_18 |  | 10 | 24 | 0.054064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5909-1_0_3_line_19 |  | 11 | 25 | 0.013741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5909-1_0_3_line_20 |  | 12 | 26 | 0.0090613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5909-1_0_3_line_21 |  | 13 | 26 | 0.023068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5909-1_0_3_line_22 |  | 15 | 21 | 0.024968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5909-1_0_3_line_23 |  | 15 | 18 | 0.036152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5909-1_0_3_line_24 |  | 17 | 27 | 0.032522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5909-1_0_3_line_25 |  | 18 | 19 | 0.002398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5909-1_0_3_line_26 |  | 18 | 20 | 0.013013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5909-1_0_3_line_27 |  | 19 | 41 | 0.058673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5909-1_0_3_line_28 |  | 19 | 42 | 0.010518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5909-1_0_3_line_29 |  | 20 | 43 | 0.026752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5909-1_0_3_line_30 |  | 21 | 40 | 0.036591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5909-1_0_3_line_31 |  | 22 | 38 | 0.013791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5909-1_0_3_line_32 |  | 23 | 37 | 0.027247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5909-1_0_3_line_33 |  | 24 | 72 | 0.041475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5909-1_0_3_line_34 |  | 28 | 29 | 0.040844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5909-1_0_3_line_35 |  | 28 | 30 | 0.011425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5909-1_0_3_line_36 |  | 29 | 31 | 0.014382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5909-1_0_3_line_37 |  | 29 | 32 | 0.030974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5909-1_0_3_line_38 |  | 30 | 42 | 0.0096141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5909-1_0_3_line_39 |  | 31 | 78 | 0.035252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5909-1_0_3_line_40 |  | 32 | 36 | 0.054141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5909-1_0_3_line_41 |  | 33 | 34 | 0.0040472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5909-1_0_3_line_42 |  | 34 | 42 | 0.035268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5909-1_0_3_line_43 |  | 35 | 36 | 0.03331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5909-1_0_3_line_44 |  | 38 | 39 | 0.032716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5909-1_0_3_line_45 |  | 39 | 44 | 0.075067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5909-1_0_3_line_46 |  | 39 | 45 | 0.0087115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5909-1_0_3_line_47 |  | 41 | 80 | 0.02398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5909-1_0_3_line_48 |  | 43 | 81 | 0.029761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5909-1_0_3_line_49 |  | 44 | 46 | 0.065818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5909-1_0_3_line_50 |  | 45 | 47 | 0.019927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5909-1_0_3_line_51 |  | 46 | 48 | 0.023276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5909-1_0_3_line_52 |  | 47 | 49 | 0.017293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5909-1_0_3_line_53 |  | 49 | 73 | 0.0010568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5909-1_0_3_line_54 |  | 50 | 51 | 0.020604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5909-1_0_3_line_55 |  | 51 | 52 | 0.009155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5909-1_0_3_line_56 |  | 52 | 53 | 0.0086072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5909-1_0_3_line_57 |  | 53 | 56 | 0.10967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5909-1_0_3_line_58 |  | 53 | 54 | 0.0064791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5909-1_0_3_line_59 |  | 54 | 55 | 0.037667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5909-1_0_3_line_60 |  | 55 | 65 | 0.025979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5909-1_0_3_line_61 |  | 56 | 62 | 0.022724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5909-1_0_3_line_62 |  | 56 | 70 | 0.015135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5909-1_0_3_line_63 |  | 57 | 58 | 0.019565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5909-1_0_3_line_64 |  | 57 | 59 | 0.0056324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5909-1_0_3_line_65 |  | 58 | 64 | 0.004192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5909-1_0_3_line_66 |  | 59 | 60 | 0.0058818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5909-1_0_3_line_67 |  | 60 | 61 | 0.002598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5909-1_0_3_line_68 |  | 61 | 62 | 0.01382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5909-1_0_3_line_69 |  | 62 | 63 | 0.006439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5909-1_0_3_line_70 |  | 65 | 66 | 0.0099505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5909-1_0_3_line_71 |  | 66 | 67 | 0.025616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5909-1_0_3_line_72 |  | 67 | 68 | 0.013397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5909-1_0_3_line_73 |  | 68 | 69 | 0.0072955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5909-1_0_3_line_74 |  | 69 | 71 | 0.0060354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5909-1_0_3_line_75 |  | 71 | 73 | 0.0094247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5909-1_0_3_line_76 |  | 74 | 75 | 0.0096559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5909-1_0_3_line_77 |  | 74 | 76 | 0.01573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5909-1_0_3_line_78 |  | 75 | 77 | 0.027743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5909-1_0_3_line_79 |  | 76 | 78 | 0.019925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5909-1_0_3_line_80 |  | 76 | 79 | 0.0097934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5909-1_0_3_trafo_7 | 0.63 MVA 20/0.4 kV | 82 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2540939.0944 | 1181294.8257 | 2540933.086 | 1181291.5454 | 2540915.1468 | 1181283.1066 | 2540912.5462 | 1181282.0597
1 | 2541004.556 | 1181327.2602 | 2540999.0179 | 1181324.0464 | 2540978.3864 | 1181315.9564 | 2540970.3705 | 1181312.4002 | 2540963.3993 | 1181308.6891 | 2540947.3068 | 1181299.3093 | 2540939.0944 | 1181294.8257
2 | 2540912.5462 | 1181282.0597 | 2540901.8587 | 1181277.7571 | 2540890.2086 | 1181273.6049
3 | 2541004.556 | 1181327.2602 | 2540999.7123 | 1181331.7327 | 2541011.3018 | 1181338.3221 | 2541008.4566 | 1181342.5414 | 2541016.7085 | 1181349.1193 | 2541027.4372 | 1181357.496 | 2541029.6686 | 1181359.175
4 | 2541004.556 | 1181327.2602 | 2541018.0309 | 1181312.0744 | 2541028.0163 | 1181300.8253 | 2541032.5507 | 1181298.2903 | 2541040.9131 | 1181297.4852 | 2541044.3048 | 1181297.5629 | 2541065.4935 | 1181296.3313 | 2541070.7489 | 1181295.6569
5 | 2541029.6686 | 1181359.175 | 2541028.3361 | 1181365.0025 | 2541025.5171 | 1181371.1114 | 2541019.6142 | 1181377.362 | 2541015.074 | 1181385.5002 | 2541015.5162 | 1181393.1668 | 2541021.4528 | 1181402.7136 | 2541029.6206 | 1181415.5479
6 | 2541029.6686 | 1181359.175 | 2541030.915 | 1181360.1076 | 2541034.2716 | 1181362.0534 | 2541039.0892 | 1181363.4623 | 2541049.3901 | 1181375.701 | 2541053.3635 | 1181381.3317 | 2541069.7509 | 1181406.7289 | 2541073.3773 | 1181412.5155
7 | 2541070.7489 | 1181295.6569 | 2541079.5136 | 1181295.3704 | 2541085.1064 | 1181294.8373 | 2541097.8332 | 1181293.6113 | 2541104.036 | 1181292.9832 | 2541111.6568 | 1181292.8637 | 2541115.5604 | 1181292.9698 | 2541114.7266 | 1181280.4265
8 | 2541112.8284 | 1181454.4981 | 2541108.4169 | 1181461.7456 | 2541112.9058 | 1181466.2262
9 | 2541096.3542 | 1181456.6949 | 2541098.8833 | 1181456.8256 | 2541103.7353 | 1181457.078 | 2541108.4169 | 1181461.7456 | 2541112.9058 | 1181466.2262
10 | 2541086.8231 | 1181498.5455 | 2541087.2149 | 1181496.4516 | 2541089.9628 | 1181492.4334 | 2541102.4606 | 1181471.1095 | 2541108.4169 | 1181461.7456 | 2541112.9058 | 1181466.2262
11 | 2541112.9058 | 1181466.2262 | 2541108.5765 | 1181468.6479 | 2541104.936 | 1181475.0874 | 2541099.2566 | 1181485.2938
12 | 2541112.8284 | 1181454.4981 | 2541118.1408 | 1181446.4414 | 2541135.4905 | 1181428.4383
13 | 2541112.8284 | 1181454.4981 | 2541126.9762 | 1181464.2199 | 2541140.3301 | 1181471.6482 | 2541151.3965 | 1181476.3531 | 2541162.6977 | 1181480.0774 | 2541180.2691 | 1181483.8401 | 2541180.5422 | 1181483.8687
14 | 2541096.3542 | 1181456.6949 | 2541095.8342 | 1181447.3281 | 2541094.181 | 1181443.8535 | 2541091.0423 | 1181439.3416
15 | 2541096.3542 | 1181456.6949 | 2541096.571 | 1181463.9746 | 2541096.1857 | 1181472.1496 | 2541094.7249 | 1181477.3669 | 2541086.3018 | 1181492.1359 | 2541081.0147 | 1181495.7789 | 2541076.232 | 1181496.0725
16 | 2541086.8231 | 1181498.5455 | 2541082.6465 | 1181500.1764 | 2541074.2214 | 1181500.0148 | 2541068.3433 | 1181497.9271 | 2541065.4693 | 1181496.8993
17 | 2541086.8231 | 1181498.5455 | 2541089.2414 | 1181502.9241 | 2541092.1942 | 1181507.3086 | 2541096.367 | 1181511.4921 | 2541114.8938 | 1181523.8611 | 2541120.2747 | 1181526.643 | 2541125.9391 | 1181529.5333 | 2541137.5471 | 1181535.7226 | 2541139.1243 | 1181536.4746
18 | 2541099.2566 | 1181485.2938 | 2541094.5728 | 1181493.7109 | 2541093.886 | 1181498.4092 | 2541095.6132 | 1181503.962 | 2541098.4205 | 1181508.3034 | 2541111.1368 | 1181516.9164 | 2541122.529 | 1181523.8556
19 | 2541036.9983 | 1181427.1408 | 2541029.6206 | 1181415.5479
20 | 2541078.189 | 1181420.1937 | 2541073.3773 | 1181412.5155
21 | 2541091.0423 | 1181439.3416 | 2541082.4292 | 1181426.9598 | 2541078.189 | 1181420.1937
22 | 2541135.4905 | 1181428.4383 | 2541158.2083 | 1181438.7975
23 | 2541135.4905 | 1181428.4383 | 2541148.4458 | 1181414.7588 | 2541160.5888 | 1181402.3547
24 | 2541114.7266 | 1181280.4265 | 2541113.371 | 1181259.0946 | 2541105.1402 | 1181251.5603
25 | 2541162.2673 | 1181400.6372 | 2541160.5888 | 1181402.3547
26 | 2541160.5888 | 1181402.3547 | 2541166.2612 | 1181405.2672 | 2541172.4487 | 1181407.6678
27 | 2541162.2673 | 1181400.6372 | 2541184.2357 | 1181409.604 | 2541191.0421 | 1181412.1163 | 2541204.8852 | 1181415.7044 | 2541209.6365 | 1181416.5916 | 2541218.1886 | 1181416.8374
28 | 2541162.2673 | 1181400.6372 | 2541170.597 | 1181394.185
29 | 2541172.4487 | 1181407.6678 | 2541179.7309 | 1181410.4932 | 2541182.583 | 1181411.6214 | 2541184.9522 | 1181412.5653 | 2541190.5963 | 1181414.9333 | 2541197.5798 | 1181416.6988
30 | 2541193.1792 | 1181449.1791 | 2541176.41 | 1181445.5455 | 2541166.9775 | 1181442.3587 | 2541163.2458 | 1181441.0946 | 2541158.2083 | 1181438.7975
31 | 2541055.9297 | 1181487.1289 | 2541058.5931 | 1181491.1749 | 2541065.4693 | 1181496.8993
32 | 2541139.1243 | 1181536.4746 | 2541150.637 | 1181541.964 | 2541164.0046 | 1181547.5623
33 | 2541122.529 | 1181523.8556 | 2541124.5897 | 1181525.1108 | 2541127.169 | 1181526.464 | 2541129.5717 | 1181527.7188 | 2541138.4921 | 1181532.4226 | 2541154.2291 | 1181539.9164 | 2541159.7087 | 1181542.1669
34 | 2541180.8409 | 1181375.8185 | 2541181.668 | 1181372.1638 | 2541183.6286 | 1181366.5192 | 2541189.6804 | 1181353.6414 | 2541194.6461 | 1181337.4947
35 | 2541180.8409 | 1181375.8185 | 2541178.4644 | 1181379.555 | 2541175.1487 | 1181385.7167
36 | 2541194.6461 | 1181337.4947 | 2541202.7967 | 1181338.4484 | 2541208.9607 | 1181338.8278
37 | 2541194.6461 | 1181337.4947 | 2541194.8172 | 1181333.1461 | 2541195.2991 | 1181327.7828 | 2541197.2484 | 1181323.3167 | 2541202.6256 | 1181312.5023 | 2541204.7671 | 1181308.789
38 | 2541170.597 | 1181394.185 | 2541173.3644 | 1181389.0327 | 2541175.1487 | 1181385.7167
39 | 2541208.9607 | 1181338.8278 | 2541232.2327 | 1181340.2602 | 2541244.1077 | 1181341.4674
40 | 2541204.7671 | 1181308.789 | 2541219.6489 | 1181282.9851 | 2541224.5748 | 1181275.9773 | 2541228.9856 | 1181274.8444 | 2541233.3459 | 1181275.5687 | 2541239.9481 | 1181277.2516
41 | 2541147.6808 | 1181367.6846 | 2541144.6273 | 1181365.0284
42 | 2541170.597 | 1181394.185 | 2541158.2455 | 1181376.8746 | 2541147.6808 | 1181367.6846
43 | 2541263.6586 | 1181263.9645 | 2541256.8729 | 1181277.5721 | 2541254.329 | 1181279.8317 | 2541249.9756 | 1181279.8077 | 2541239.9481 | 1181277.2516
44 | 2541031.2021 | 1181468.988 | 2541034.9515 | 1181468.1839 | 2541039.5539 | 1181470.2286 | 2541041.5789 | 1181471.1314 | 2541048.2872 | 1181476.8574 | 2541054.4995 | 1181484.9562 | 2541055.9297 | 1181487.1289
45 | 2541031.2021 | 1181468.988 | 2541031.1403 | 1181473.5689 | 2541026.3022 | 1181474.7173 | 2541018.8452 | 1181481.35 | 2541016.1927 | 1181484.2 | 2541013.6311 | 1181486.9712 | 2541010.6833 | 1181490.0687 | 2541002.162 | 1181499.5136 | 2540999.5632 | 1181506.2541 | 2540999.6397 | 1181514.0132 | 2541002.8836 | 1181520.0179 | 2541006.4194 | 1181523.8852 | 2541009.4368 | 1181526.2296
46 | 2541031.2021 | 1181468.988 | 2541027.1173 | 1181469.8621 | 2541023.6168 | 1181472.7442
47 | 2541218.1886 | 1181416.8374 | 2541220.0105 | 1181416.8898 | 2541232.5541 | 1181417.2557 | 2541242.1582 | 1181417.5315
48 | 2541227.0409 | 1181419.587 | 2541207.8443 | 1181419.1773 | 2541206.4741 | 1181418.8573 | 2541204.216 | 1181418.3347 | 2541201.5598 | 1181417.7049 | 2541197.5798 | 1181416.6988
49 | 2541009.4368 | 1181526.2296 | 2541011.845 | 1181528.1008 | 2541014.4349 | 1181529.7428 | 2541017.0939 | 1181531.4287 | 2541023.5513 | 1181534.9559 | 2541051.9551 | 1181545.2484 | 2541062.6099 | 1181551.5914 | 2541068.0069 | 1181555.3632
50 | 2541009.9722 | 1181487.2345 | 2541014.3271 | 1181482.4285 | 2541017.2055 | 1181479.2539 | 2541021.6099 | 1181474.3967 | 2541023.6168 | 1181472.7442
51 | 2541068.0069 | 1181555.3632 | 2541069.2924 | 1181556.2615 | 2541072.3849 | 1181558.5435 | 2541076.8083 | 1181561.8128 | 2541086.4992 | 1181569.4904
52 | 2540998.5259 | 1181500.1943 | 2540998.5259 | 1181500.1943 | 2541003.471 | 1181494.4089 | 2541009.9722 | 1181487.2345
53 | 2540998.5259 | 1181500.1943 | 2540998.332 | 1181501.2332
54 | 2541112.3488 | 1181597.3968 | 2541124.2653 | 1181602.3017 | 2541131.5009 | 1181604.9875 | 2541131.5009 | 1181604.9875
55 | 2541103.9204 | 1181593.8233 | 2541106.0152 | 1181594.7437 | 2541110.6011 | 1181596.6774 | 2541112.3488 | 1181597.3968
56 | 2541103.9204 | 1181593.8233 | 2541102.8475 | 1181593.3519 | 2541100.226 | 1181590.8096 | 2541098.4063 | 1181587.4923
57 | 2541098.4063 | 1181587.4923 | 2541015.6765 | 1181659.481
58 | 2541097.1297 | 1181581.168 | 2541097.4905 | 1181584.4552 | 2541098.4063 | 1181587.4923
59 | 2541097.1297 | 1181581.168 | 2541085.9231 | 1181571.5174 | 2541071.9304 | 1181560.4712 | 2541067.8144 | 1181557.5451
60 | 2541067.8144 | 1181557.5451 | 2541060.8865 | 1181552.6201 | 2541050.9622 | 1181546.7924 | 2541045.3229 | 1181544.8315
61 | 2541007.5105 | 1181676.282 | 2541008.9059 | 1181672.1882 | 2541007.1289 | 1181668.5593 | 2541007.9393 | 1181667.106 | 2541009.8933 | 1181666.2307 | 2541011.7799 | 1181667.0348 | 2541013.0185 | 1181664.8658 | 2541015.6765 | 1181659.481
62 | 2541015.6765 | 1181659.481 | 2541007.3395 | 1181654.3048 | 2541002.7424 | 1181651.6243
63 | 2541046.1204 | 1181697.8358 | 2541039.6636 | 1181694.353 | 2541038.3429 | 1181693.6212 | 2541038.519 | 1181690.5733 | 2541036.8463 | 1181688.2218 | 2541032.6159 | 1181685.9288
64 | 2541032.6159 | 1181685.9288 | 2541027.6805 | 1181683.2149
65 | 2541046.1204 | 1181697.8358 | 2541043.4797 | 1181701.0969
66 | 2541022.5266 | 1181680.3807 | 2541027.6805 | 1181683.2149
67 | 2541020.2461 | 1181679.1247 | 2541022.5266 | 1181680.3807
68 | 2541007.5105 | 1181676.282 | 2541009.0072 | 1181675.4891 | 2541010.8682 | 1181675.2595 | 2541013.0771 | 1181675.4489 | 2541014.9557 | 1181676.2197 | 2541020.2461 | 1181679.1247
69 | 2541007.5105 | 1181676.282 | 2541004.681 | 1181682.0687
70 | 2541035.9409 | 1181541.5178 | 2541037.9349 | 1181542.2626 | 2541045.3229 | 1181544.8315
71 | 2541035.9409 | 1181541.5178 | 2541022.0451 | 1181536.327 | 2541012.5056 | 1181531.3011
72 | 2541002.49 | 1181522.6865 | 2541004.0808 | 1181525.2535 | 2541011.9578 | 1181531.0124 | 2541012.5056 | 1181531.3011
73 | 2540998.6471 | 1181516.4851 | 2541002.49 | 1181522.6865
74 | 2540998.6471 | 1181516.4851 | 2540998.3768 | 1181516.049 | 2540997.8438 | 1181510.5524
75 | 2540998.332 | 1181501.2332 | 2540997.4161 | 1181506.1419 | 2540997.8438 | 1181510.5524
76 | 2541269.9739 | 1181328.423 | 2541273.6602 | 1181319.4985
77 | 2541263.9687 | 1181342.9612 | 2541269.9739 | 1181328.423
78 | 2541284.2519 | 1181293.8569 | 2541273.6602 | 1181319.4985
79 | 2541263.9687 | 1181342.9612 | 2541254.7695 | 1181342.5513 | 2541244.1077 | 1181341.4674
80 | 2541263.9687 | 1181342.9612 | 2541273.752 | 1181343.4041

## bus_geodata
| x | y | coords
0 | 2540939.0944 | 1181294.8257
1 | 2540912.5462 | 1181282.0597
2 | 2541004.556 | 1181327.2602
3 | 2540890.2086 | 1181273.6049
4 | 2541029.6686 | 1181359.175
5 | 2541070.7489 | 1181295.6569
6 | 2541112.9058 | 1181466.2262
7 | 2541112.8284 | 1181454.4981
8 | 2541096.3542 | 1181456.6949
9 | 2541086.8231 | 1181498.5455
10 | 2541099.2566 | 1181485.2938
11 | 2541029.6206 | 1181415.5479
12 | 2541073.3773 | 1181412.5155
13 | 2541091.0423 | 1181439.3416
14 | 2541076.232 | 1181496.0725
15 | 2541135.4905 | 1181428.4383
16 | 2541180.5422 | 1181483.8687
17 | 2541114.7266 | 1181280.4265
18 | 2541160.5888 | 1181402.3547
19 | 2541162.2673 | 1181400.6372
20 | 2541172.4487 | 1181407.6678
21 | 2541158.2083 | 1181438.7975
22 | 2541065.4693 | 1181496.8993
23 | 2541139.1243 | 1181536.4746
24 | 2541122.529 | 1181523.8556
25 | 2541036.9983 | 1181427.1408
26 | 2541078.189 | 1181420.1937
27 | 2541105.1402 | 1181251.5603
28 | 2541180.8409 | 1181375.8185
29 | 2541194.6461 | 1181337.4947
30 | 2541175.1487 | 1181385.7167
31 | 2541208.9607 | 1181338.8278
32 | 2541204.7671 | 1181308.789
33 | 2541144.6273 | 1181365.0284
34 | 2541147.6808 | 1181367.6846
35 | 2541263.6586 | 1181263.9645
36 | 2541239.9481 | 1181277.2516
37 | 2541164.0046 | 1181547.5623
38 | 2541055.9297 | 1181487.1289
39 | 2541031.2021 | 1181468.988
40 | 2541193.1792 | 1181449.1791
41 | 2541218.1886 | 1181416.8374
42 | 2541170.597 | 1181394.185
43 | 2541197.5798 | 1181416.6988
44 | 2541009.4368 | 1181526.2296
45 | 2541023.6168 | 1181472.7442
46 | 2541068.0069 | 1181555.3632
47 | 2541009.9722 | 1181487.2345
48 | 2541086.4992 | 1181569.4904
49 | 2540998.5259 | 1181500.1943
50 | 2541131.5009 | 1181604.9875
51 | 2541112.3488 | 1181597.3968
52 | 2541103.9204 | 1181593.8233
53 | 2541098.4063 | 1181587.4923
54 | 2541097.1297 | 1181581.168
55 | 2541067.8144 | 1181557.5451
56 | 2541015.6765 | 1181659.481
57 | 2541032.6159 | 1181685.9288
58 | 2541046.1204 | 1181697.8358
59 | 2541027.6805 | 1181683.2149
60 | 2541022.5266 | 1181680.3807
61 | 2541020.2461 | 1181679.1247
62 | 2541007.5105 | 1181676.282
63 | 2541004.681 | 1181682.0687
64 | 2541043.4797 | 1181701.0969
65 | 2541045.3229 | 1181544.8315
66 | 2541035.9409 | 1181541.5178
67 | 2541012.5056 | 1181531.3011
68 | 2541002.49 | 1181522.6865
69 | 2540998.6471 | 1181516.4851
70 | 2541002.7424 | 1181651.6243
71 | 2540997.8438 | 1181510.5524
72 | 2541159.7087 | 1181542.1669
73 | 2540998.332 | 1181501.2332
74 | 2541269.9739 | 1181328.423
75 | 2541273.6602 | 1181319.4985
76 | 2541263.9687 | 1181342.9612
77 | 2541284.2519 | 1181293.8569
78 | 2541244.1077 | 1181341.4674
79 | 2541273.752 | 1181343.4041
80 | 2541242.1582 | 1181417.5315
81 | 2541227.0409 | 1181419.587
82 | 2541108.4169 | 1181461.7456

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1