## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5909-2_1_2_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_5909-2_1_2_node_127 | 0.4 | n |  | TRUE
2 | bus_LV_5909-2_1_2_node_129 | 0.4 | n |  | TRUE
3 | bus_LV_5909-2_1_2_node_131 | 0.4 | n |  | TRUE
4 | bus_LV_5909-2_1_2_node_132 | 0.4 | n |  | TRUE
5 | bus_LV_5909-2_1_2_node_177 | 0.4 | n |  | TRUE
6 | bus_LV_5909-2_1_2_node_140 | 0.4 | n |  | TRUE
7 | bus_LV_5909-2_1_2_node_183 | 0.4 | n |  | TRUE
8 | bus_LV_5909-2_1_2_node_133 | 0.4 | n |  | TRUE
9 | bus_LV_5909-2_1_2_node_79 | 0.4 | n |  | TRUE
10 | bus_LV_5909-2_1_2_node_135 | 0.4 | n |  | TRUE
11 | bus_LV_5909-2_1_2_node_134 | 0.4 | n |  | TRUE
12 | bus_LV_5909-2_1_2_node_136 | 0.4 | n |  | TRUE
13 | bus_LV_5909-2_1_2_node_154 | 0.4 | n |  | TRUE
14 | bus_LV_5909-2_1_2_node_137 | 0.4 | n |  | TRUE
15 | bus_LV_5909-2_1_2_node_138 | 0.4 | n |  | TRUE
16 | bus_LV_5909-2_1_2_node_139 | 0.4 | n |  | TRUE
17 | bus_LV_5909-2_1_2_node_162 | 0.4 | n |  | TRUE
18 | bus_LV_5909-2_1_2_node_141 | 0.4 | n |  | TRUE
19 | bus_LV_5909-2_1_2_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_5909-2_1_2_node_150 | 0.4 | n |  | TRUE
21 | bus_LV_5909-2_1_2_node_93 | 0.4 | n |  | TRUE
22 | bus_LV_5909-2_1_2_node_142 | 0.4 | n |  | TRUE
23 | bus_LV_5909-2_1_2_node_175 | 0.4 | n |  | TRUE
24 | bus_LV_5909-2_1_2_node_151 | 0.4 | n |  | TRUE
25 | bus_LV_5909-2_1_2_node_143 | 0.4 | n |  | TRUE
26 | bus_LV_5909-2_1_2_node_144 | 0.4 | n |  | TRUE
27 | bus_LV_5909-2_1_2_node_145 | 0.4 | n |  | TRUE
28 | bus_LV_5909-2_1_2_node_146 | 0.4 | n |  | TRUE
29 | bus_LV_5909-2_1_2_node_147 | 0.4 | n |  | TRUE
30 | bus_LV_5909-2_1_2_node_163 | 0.4 | n |  | TRUE
31 | bus_LV_5909-2_1_2_node_148 | 0.4 | n |  | TRUE
32 | bus_LV_5909-2_1_2_node_149 | 0.4 | n |  | TRUE
33 | bus_LV_5909-2_1_2_node_152 | 0.4 | n |  | TRUE
34 | bus_LV_5909-2_1_2_node_158 | 0.4 | n |  | TRUE
35 | bus_LV_5909-2_1_2_node_160 | 0.4 | n |  | TRUE
36 | bus_LV_5909-2_1_2_node_166 | 0.4 | n |  | TRUE
37 | bus_LV_5909-2_1_2_node_153 | 0.4 | n |  | TRUE
38 | bus_LV_5909-2_1_2_node_155 | 0.4 | n |  | TRUE
39 | bus_LV_5909-2_1_2_node_156 | 0.4 | n |  | TRUE
40 | bus_LV_5909-2_1_2_node_164 | 0.4 | n |  | TRUE
41 | bus_LV_5909-2_1_2_node_157 | 0.4 | n |  | TRUE
42 | bus_LV_5909-2_1_2_node_178 | 0.4 | n |  | TRUE
43 | bus_LV_5909-2_1_2_node_159 | 0.4 | n |  | TRUE
44 | bus_LV_5909-2_1_2_node_179 | 0.4 | n |  | TRUE
45 | bus_LV_5909-2_1_2_node_161 | 0.4 | n |  | TRUE
46 | bus_LV_5909-2_1_2_node_165 | 0.4 | n |  | TRUE
47 | bus_LV_5909-2_1_2_node_176 | 0.4 | n |  | TRUE
48 | bus_LV_5909-2_1_2_node_180 | 0.4 | n |  | TRUE
49 | bus_LV_5909-2_1_2_node_181 | 0.4 | n |  | TRUE
50 | bus_LV_5909-2_1_2_node_92 | 0.4 | n |  | TRUE
51 | bus_LV_5909-2_1_2_node_182 | 0.4 | n |  | TRUE
52 | bus_LV_5909-2_1_2_node_110 | 0.4 | n |  | TRUE
53 | bus_LV_5909-2_1_2_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_5909-2_1_2_node_184 | 0.4 | n |  | TRUE
55 | bus_LV_5909-2_1_2_node_185 | 0.4 | n |  | TRUE
56 | bus_LV_5909-2_1_2_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_5909-2_1_2_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_5909-2_1_2_node_124 | 0.4 | n |  | TRUE
59 | bus_LV_5909-2_1_2_node_94 | 0.4 | n |  | TRUE
60 | bus_LV_5909-2_1_2_node_100 | 0.4 | n |  | TRUE
61 | bus_LV_5909-2_1_2_node_101 | 0.4 | n |  | TRUE
62 | bus_LV_5909-2_1_2_node_102 | 0.4 | n |  | TRUE
63 | bus_LV_5909-2_1_2_node_103 | 0.4 | n |  | TRUE
64 | bus_LV_5909-2_1_2_node_104 | 0.4 | n |  | TRUE
65 | bus_LV_5909-2_1_2_node_116 | 0.4 | n |  | TRUE
66 | bus_LV_5909-2_1_2_node_125 | 0.4 | n |  | TRUE
67 | bus_MV_455_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5909-2_1_2_load_128 | 0 | 0.0028612 | 0.00071708 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5909-2_1_2_load_127 | 1 | 0.0028633 | 0.00071761 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5909-2_1_2_load_131 | 3 | 0.00419 | 0.0010501 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5909-2_1_2_load_132 | 4 | 0.0071335 | 0.0017878 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5909-2_1_2_load_177 | 5 | 0.003191 | 0.00079975 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5909-2_1_2_load_183 | 7 | 0.0055543 | 0.001392 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5909-2_1_2_load_133 | 8 | 0.00036749 | 9.2102e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5909-2_1_2_load_135 | 10 | 0.0034085 | 0.00085426 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5909-2_1_2_load_136 | 12 | 0.0024903 | 0.00062412 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5909-2_1_2_load_154 | 13 | 0.0019415 | 0.00048658 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5909-2_1_2_load_137 | 14 | 0.0045834 | 0.0011487 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5909-2_1_2_load_138 | 15 | 0.003104 | 0.00077792 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5909-2_1_2_load_139 | 16 | 0.0011769 | 0.00029495 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5909-2_1_2_load_141 | 18 | 0.0023781 | 0.000596 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5909-2_1_2_load_15 | 19 | 0.0024059 | 0.00060297 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5909-2_1_2_load_150 | 20 | 0.0024294 | 0.00060887 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5909-2_1_2_load_93 | 21 | 0.0023991 | 0.00060128 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5909-2_1_2_load_142 | 22 | 0.0022314 | 0.00055924 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5909-2_1_2_load_175 | 23 | 0.0034524 | 0.00086526 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5909-2_1_2_load_151 | 24 | 0.0046193 | 0.0011577 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5909-2_1_2_load_143 | 25 | 0.0030045 | 0.00075301 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5909-2_1_2_load_144 | 26 | 0.0030905 | 0.00077456 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5909-2_1_2_load_145 | 27 | 0.0028249 | 0.00070799 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5909-2_1_2_load_146 | 28 | 0.0031994 | 0.00080183 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5909-2_1_2_load_147 | 29 | 0.0017345 | 0.0004347 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5909-2_1_2_load_163 | 30 | 0.0033281 | 0.00083411 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5909-2_1_2_load_148 | 31 | 0.0033773 | 0.00084643 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5909-2_1_2_load_149 | 32 | 0.0024635 | 0.0006174 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5909-2_1_2_load_152 | 33 | 0.003027 | 0.00075864 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5909-2_1_2_load_160 | 35 | 0.0034725 | 0.0008703 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5909-2_1_2_load_166 | 36 | 0.0023686 | 0.00059362 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5909-2_1_2_load_153 | 37 | 0.0020142 | 0.00050481 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5909-2_1_2_load_155 | 38 | 0.0032716 | 0.00081994 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5909-2_1_2_load_156 | 39 | 0.0024875 | 0.00062343 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5909-2_1_2_load_164 | 40 | 0.0023266 | 0.0005831 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5909-2_1_2_load_157 | 41 | 0.0034656 | 0.00086856 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5909-2_1_2_load_178 | 42 | 0.0030626 | 0.00076756 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5909-2_1_2_load_159 | 43 | 0.003279 | 0.00082178 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5909-2_1_2_load_179 | 44 | 0.0033972 | 0.00085143 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5909-2_1_2_load_161 | 45 | 0.0026307 | 0.00065931 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5909-2_1_2_load_165 | 46 | 0.0024876 | 0.00062345 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5909-2_1_2_load_176 | 47 | 0.0038467 | 0.00096408 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5909-2_1_2_load_180 | 48 | 0.0030145 | 0.00075551 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5909-2_1_2_load_181 | 49 | 0.0034159 | 0.00085611 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5909-2_1_2_load_92 | 50 | 0.0045063 | 0.0011294 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5909-2_1_2_load_182 | 51 | 0.0035483 | 0.00088929 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5909-2_1_2_load_110 | 52 | 0.0011386 | 0.00028537 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5909-2_1_2_load_111 | 53 | 0.0020787 | 0.00052097 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5909-2_1_2_load_185 | 55 | 0.0016424 | 0.00041162 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5909-2_1_2_load_66 | 56 | 0.00018173 | 4.5547e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5909-2_1_2_load_67 | 57 | 0.00094859 | 0.00023774 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5909-2_1_2_load_94 | 59 | 0.0011953 | 0.00029956 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5909-2_1_2_load_100 | 60 | 0.0013375 | 0.0003352 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5909-2_1_2_load_101 | 61 | 0.001192 | 0.00029874 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5909-2_1_2_load_102 | 62 | 0.0013168 | 0.00033003 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5909-2_1_2_load_103 | 63 | 0.0012683 | 0.00031786 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5909-2_1_2_load_104 | 64 | 0.000533 | 0.00013358 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5909-2_1_2_load_116 | 65 | 0.0010242 | 0.00025668 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5909-2_1_2_load_125 | 66 | 0.0018936 | 0.00047457 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5909-2_1_2_line_0 |  | 0 | 1 | 0.033139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5909-2_1_2_line_1 |  | 1 | 47 | 0.0053673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5909-2_1_2_line_2 |  | 2 | 3 | 0.015004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5909-2_1_2_line_3 |  | 2 | 4 | 0.020477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5909-2_1_2_line_4 |  | 2 | 5 | 0.0049146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5909-2_1_2_line_5 |  | 3 | 6 | 0.021181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5909-2_1_2_line_6 |  | 4 | 7 | 0.009883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5909-2_1_2_line_7 |  | 5 | 47 | 0.042654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5909-2_1_2_line_8 |  | 6 | 17 | 0.034369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5909-2_1_2_line_9 |  | 6 | 15 | 0.02131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5909-2_1_2_line_10 |  | 7 | 54 | 0.090394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5909-2_1_2_line_11 |  | 8 | 9 | 0.10578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5909-2_1_2_line_12 |  | 8 | 10 | 0.26213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5909-2_1_2_line_13 |  | 9 | 57 | 0.036824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5909-2_1_2_line_14 |  | 10 | 11 | 0.022474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5909-2_1_2_line_15 |  | 11 | 12 | 0.026996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5909-2_1_2_line_16 |  | 12 | 13 | 0.0036142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5909-2_1_2_line_17 |  | 13 | 37 | 0.053821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5909-2_1_2_line_18 |  | 14 | 15 | 0.0059368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5909-2_1_2_line_19 |  | 14 | 16 | 0.004913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5909-2_1_2_line_20 |  | 17 | 30 | 0.010038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5909-2_1_2_line_21 |  | 17 | 45 | 0.016378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5909-2_1_2_line_22 |  | 18 | 19 | 0.08174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5909-2_1_2_line_23 |  | 18 | 20 | 0.049419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5909-2_1_2_line_24 |  | 18 | 21 | 0.037582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5909-2_1_2_line_25 |  | 20 | 33 | 0.020989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5909-2_1_2_line_26 |  | 20 | 31 | 0.017024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5909-2_1_2_line_27 |  | 21 | 59 | 0.040975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5909-2_1_2_line_28 |  | 21 | 48 | 0.018307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5909-2_1_2_line_29 |  | 22 | 23 | 0.017616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5909-2_1_2_line_30 |  | 22 | 24 | 0.057363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5909-2_1_2_line_31 |  | 24 | 34 | 0.055448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5909-2_1_2_line_32 |  | 24 | 32 | 0.023852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5909-2_1_2_line_33 |  | 25 | 26 | 0.01149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5909-2_1_2_line_34 |  | 25 | 27 | 0.016893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5909-2_1_2_line_35 |  | 26 | 28 | 0.02697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5909-2_1_2_line_36 |  | 27 | 29 | 0.004985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5909-2_1_2_line_37 |  | 29 | 30 | 0.020058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5909-2_1_2_line_38 |  | 31 | 32 | 0.010948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5909-2_1_2_line_39 |  | 33 | 35 | 0.027627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5909-2_1_2_line_40 |  | 33 | 36 | 0.047557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5909-2_1_2_line_41 |  | 34 | 43 | 0.018744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5909-2_1_2_line_42 |  | 34 | 44 | 0.011598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5909-2_1_2_line_43 |  | 35 | 39 | 0.0039232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5909-2_1_2_line_44 |  | 37 | 38 | 0.026015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5909-2_1_2_line_45 |  | 38 | 39 | 0.025359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5909-2_1_2_line_46 |  | 38 | 40 | 0.053289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5909-2_1_2_line_47 |  | 40 | 46 | 0.03279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5909-2_1_2_line_48 |  | 41 | 42 | 0.0069717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5909-2_1_2_line_49 |  | 42 | 44 | 0.038072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5909-2_1_2_line_50 |  | 43 | 45 | 0.011832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5909-2_1_2_line_51 |  | 48 | 49 | 0.033366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5909-2_1_2_line_52 |  | 49 | 50 | 0.0080475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5909-2_1_2_line_53 |  | 50 | 58 | 0.07561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5909-2_1_2_line_54 |  | 51 | 52 | 0.0078476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5909-2_1_2_line_55 |  | 51 | 53 | 0.020272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5909-2_1_2_line_56 |  | 52 | 59 | 0.030221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5909-2_1_2_line_57 |  | 54 | 55 | 0.031705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5909-2_1_2_line_58 |  | 56 | 57 | 0.017625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5909-2_1_2_line_59 |  | 58 | 66 | 0.053116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5909-2_1_2_line_60 |  | 58 | 65 | 0.037282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5909-2_1_2_line_61 |  | 60 | 61 | 0.028447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5909-2_1_2_line_62 |  | 60 | 62 | 0.0053379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5909-2_1_2_line_63 |  | 61 | 63 | 0.00030877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5909-2_1_2_line_64 |  | 62 | 64 | 0.0044921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5909-2_1_2_line_65 |  | 63 | 65 | 0.02719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5909-2_1_2_trafo_148 | 0.63 MVA 20/0.4 kV | 67 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2541191.637 | 1181609.0389 | 2541188.1846 | 1181607.6649 | 2541181.4021 | 1181606.0084 | 2541171.4809 | 1181605.1277 | 2541165.4306 | 1181604.9315 | 2541160.4431 | 1181604.8583 | 2541159.0324 | 1181604.5722
1 | 2541191.637 | 1181609.0389 | 2541196.9357 | 1181608.1831
2 | 2541237.5288 | 1181631.271 | 2541247.6046 | 1181629.2376 | 2541251.4999 | 1181626.5628
3 | 2541237.5288 | 1181631.271 | 2541236.7392 | 1181635.6257 | 2541235.1765 | 1181639.7989 | 2541232.9115 | 1181643.2231 | 2541229.6998 | 1181647.457 | 2541228.1126 | 1181648.9446
4 | 2541237.5288 | 1181631.271 | 2541234.2835 | 1181627.5803
5 | 2541262.2739 | 1181608.9266 | 2541259.3419 | 1181617.5269 | 2541256.3251 | 1181622.1702 | 2541253.3697 | 1181625.2788 | 2541251.4999 | 1181626.5628
6 | 2541220.9016 | 1181655.703 | 2541228.1126 | 1181648.9446
7 | 2541196.9357 | 1181608.1831 | 2541205.9106 | 1181613.2049 | 2541219.6306 | 1181622.9644 | 2541231.0619 | 1181627.5325 | 2541234.2835 | 1181627.5803
8 | 2541262.2739 | 1181608.9266 | 2541275.6173 | 1181577.2446
9 | 2541262.2739 | 1181608.9266 | 2541282.1604 | 1181616.5842
10 | 2541157.7619 | 1181718.8707 | 2541161.9643 | 1181717.5509 | 2541165.3406 | 1181716.0835 | 2541169.0169 | 1181713.2902 | 2541191.1486 | 1181690.8379 | 2541211.1909 | 1181664.8041 | 2541220.9016 | 1181655.703
11 | 2541637.4065 | 1181891.2022 | 2541584.583 | 1181799.5576
12 | 2541410.4275 | 1181603.6428 | 2541584.583 | 1181799.5576
13 | 2541637.4065 | 1181891.2022 | 2541638.0074 | 1181899.5677 | 2541643.0544 | 1181910.4468 | 2541653.4535 | 1181923.1854
14 | 2541427.2987 | 1181588.7975 | 2541413.9815 | 1181600.6345 | 2541410.4275 | 1181603.6428
15 | 2541427.2987 | 1181588.7975 | 2541433.9765 | 1181582.8955 | 2541437.1917 | 1181579.0063 | 2541439.3995 | 1181575.1826 | 2541442.0982 | 1181568.4635 | 2541442.4305 | 1181567.1227
16 | 2541442.4305 | 1181567.1227 | 2541443.2997 | 1181563.6145
17 | 2541410.0695 | 1181530.8298 | 2541438.5905 | 1181543.2615 | 2541440.8094 | 1181545.252 | 2541442.863 | 1181547.5221 | 2541444.2025 | 1181550.166 | 2541444.9034 | 1181553.8946 | 2541444.8458 | 1181557.3749 | 2541443.2997 | 1181563.6145
18 | 2541282.1604 | 1181616.5842 | 2541287.7006 | 1181618.7176
19 | 2541292.2854 | 1181620.483 | 2541287.7006 | 1181618.7176
20 | 2541275.6173 | 1181577.2446 | 2541285.314 | 1181579.8387
21 | 2541275.6173 | 1181577.2446 | 2541261.1417 | 1181573.7403 | 2541259.6916 | 1181573.4242
22 | 2541399.689 | 1181465.3198 | 2541396.4247 | 1181464.2858 | 2541372.2551 | 1181458.9863 | 2541358.587 | 1181457.6417 | 2541356.1668 | 1181458.4881 | 2541352.4403 | 1181458.5247 | 2541331.9836 | 1181458.0249 | 2541318.9187 | 1181458.7415
23 | 2541318.9187 | 1181458.7415 | 2541309.7027 | 1181507.2937
24 | 2541318.9187 | 1181458.7415 | 2541309.6225 | 1181422.3272
25 | 2541309.7027 | 1181507.2937 | 2541309.8998 | 1181507.2913 | 2541326.0311 | 1181507.511 | 2541330.6714 | 1181507.9335
26 | 2541292.6796 | 1181507.497 | 2541309.7027 | 1181507.2937
27 | 2541309.6225 | 1181422.3272 | 2541314.0413 | 1181422.7034 | 2541330.8568 | 1181424.1393 | 2541344.3613 | 1181423.5843 | 2541350.3541 | 1181422.2125
28 | 2541309.6225 | 1181422.3272 | 2541291.3208 | 1181422.7814
29 | 2541228.9085 | 1181478.0321 | 2541212.8484 | 1181485.2698
30 | 2541228.9085 | 1181478.0321 | 2541264.075 | 1181523.3516
31 | 2541229.817 | 1181566.9108 | 2541247.9576 | 1181542.3522 | 2541254.8647 | 1181534.1464 | 2541263.223 | 1181524.4034 | 2541264.075 | 1181523.3516
32 | 2541281.8141 | 1181508.3132 | 2541280.618 | 1181508.6571 | 2541277.209 | 1181509.9135 | 2541274.0272 | 1181511.7569 | 2541271.1382 | 1181514.6313 | 2541264.075 | 1181523.3516
33 | 2541335.1253 | 1181599.1115 | 2541324.4514 | 1181594.8595
34 | 2541308.7094 | 1181588.7326 | 2541315.1753 | 1181591.1642 | 2541324.4514 | 1181594.8595
35 | 2541360.2045 | 1181609.0235 | 2541359.5192 | 1181608.7615 | 2541356.4513 | 1181607.4242 | 2541341.8403 | 1181601.7865 | 2541335.1253 | 1181599.1115
36 | 2541304.0435 | 1181586.9779 | 2541308.7094 | 1181588.7326
37 | 2541304.0435 | 1181586.9779 | 2541292.5019 | 1181582.6375 | 2541287.0415 | 1181580.3009 | 2541285.314 | 1181579.8387
38 | 2541292.6796 | 1181507.497 | 2541289.0306 | 1181507.5406 | 2541283.7403 | 1181507.7593 | 2541281.8141 | 1181508.3132
39 | 2541357.8385 | 1181512.8416 | 2541349.3973 | 1181511.1172 | 2541340.2751 | 1181509.1834 | 2541332.8647 | 1181508.1332 | 2541330.6714 | 1181507.9335
40 | 2541340.3402 | 1181461.3702 | 2541330.6714 | 1181507.9335
41 | 2541229.817 | 1181566.9108 | 2541248.1311 | 1181570.9037
42 | 2541229.817 | 1181566.9108 | 2541231.866 | 1181555.4954
43 | 2541361.6234 | 1181513.8601 | 2541359.108 | 1181513.1009 | 2541357.8385 | 1181512.8416
44 | 2541410.0695 | 1181530.8298 | 2541402.6199 | 1181527.5827 | 2541398.0281 | 1181525.8156 | 2541393.3931 | 1181524.3157 | 2541385.7631 | 1181521.6078
45 | 2541361.6234 | 1181513.8601 | 2541377.0544 | 1181518.517 | 2541385.7631 | 1181521.6078
46 | 2541403.9411 | 1181471.5152 | 2541385.7631 | 1181521.6078
47 | 2541403.9411 | 1181471.5152 | 2541415.6756 | 1181475.0032 | 2541429.2616 | 1181480.4511 | 2541434.5684 | 1181483.0541
48 | 2541189.3387 | 1181556.5748 | 2541196.023 | 1181554.594
49 | 2541231.866 | 1181555.4954 | 2541227.0946 | 1181558.7663 | 2541220.8005 | 1181560.9627 | 2541213.9468 | 1181559.8405 | 2541196.6685 | 1181554.7963 | 2541196.023 | 1181554.594
50 | 2541259.6916 | 1181573.4242 | 2541248.1311 | 1181570.9037
51 | 2541291.3208 | 1181422.7814 | 2541281.7667 | 1181421.8751 | 2541277.8075 | 1181421.5471 | 2541275.9655 | 1181421.3984 | 2541268.2624 | 1181420.8849 | 2541259.1071 | 1181420.2633 | 2541258.056 | 1181420.2378
52 | 2541265.9236 | 1181418.5459 | 2541258.056 | 1181420.2378
53 | 2541265.9236 | 1181418.5459 | 2541263.9687 | 1181342.9612
54 | 2541387.6319 | 1181415.8762 | 2541379.7984 | 1181415.4058
55 | 2541387.6319 | 1181415.8762 | 2541407.2368 | 1181410.7166
56 | 2541379.7984 | 1181415.4058 | 2541379.077 | 1181415.5729 | 2541357.2999 | 1181420.6225 | 2541350.3541 | 1181422.2125
57 | 2541157.7619 | 1181718.8707 | 2541153.4771 | 1181711.82 | 2541145.992 | 1181706.2683 | 2541142.2959 | 1181703.9478 | 2541135.3609 | 1181697.0647
58 | 2541664.2653 | 1181937.0952 | 2541659.9727 | 1181931.1711 | 2541653.4535 | 1181923.1854
59 | 2541284.2519 | 1181293.8569 | 2541263.9687 | 1181342.9612
60 | 2541263.9687 | 1181342.9612 | 2541278.096 | 1181343.6007 | 2541282.7851 | 1181343.588 | 2541295.0805 | 1181343.5562 | 2541301.2359 | 1181343.5386
61 | 2541357.0982 | 1181341.5719 | 2541348.8261 | 1181342.3173 | 2541336.3886 | 1181343.4399 | 2541333.4484 | 1181343.4465 | 2541328.7349 | 1181343.46
62 | 2541357.0982 | 1181341.5719 | 2541362.4145 | 1181341.0928
63 | 2541328.4261 | 1181343.4609 | 2541328.7349 | 1181343.46
64 | 2541362.4145 | 1181341.0928 | 2541366.8885 | 1181340.6897
65 | 2541328.4261 | 1181343.4609 | 2541301.2359 | 1181343.5386

## bus_geodata
| x | y | coords
0 | 2541159.0324 | 1181604.5722
1 | 2541191.637 | 1181609.0389
2 | 2541237.5288 | 1181631.271
3 | 2541251.4999 | 1181626.5628
4 | 2541228.1126 | 1181648.9446
5 | 2541234.2835 | 1181627.5803
6 | 2541262.2739 | 1181608.9266
7 | 2541220.9016 | 1181655.703
8 | 2541584.583 | 1181799.5576
9 | 2541637.4065 | 1181891.2022
10 | 2541410.4275 | 1181603.6428
11 | 2541427.2987 | 1181588.7975
12 | 2541442.4305 | 1181567.1227
13 | 2541443.2997 | 1181563.6145
14 | 2541287.7006 | 1181618.7176
15 | 2541282.1604 | 1181616.5842
16 | 2541292.2854 | 1181620.483
17 | 2541275.6173 | 1181577.2446
18 | 2541318.9187 | 1181458.7415
19 | 2541399.689 | 1181465.3198
20 | 2541309.7027 | 1181507.2937
21 | 2541309.6225 | 1181422.3272
22 | 2541228.9085 | 1181478.0321
23 | 2541212.8484 | 1181485.2698
24 | 2541264.075 | 1181523.3516
25 | 2541324.4514 | 1181594.8595
26 | 2541335.1253 | 1181599.1115
27 | 2541308.7094 | 1181588.7326
28 | 2541360.2045 | 1181609.0235
29 | 2541304.0435 | 1181586.9779
30 | 2541285.314 | 1181579.8387
31 | 2541292.6796 | 1181507.497
32 | 2541281.8141 | 1181508.3132
33 | 2541330.6714 | 1181507.9335
34 | 2541229.817 | 1181566.9108
35 | 2541357.8385 | 1181512.8416
36 | 2541340.3402 | 1181461.3702
37 | 2541410.0695 | 1181530.8298
38 | 2541385.7631 | 1181521.6078
39 | 2541361.6234 | 1181513.8601
40 | 2541403.9411 | 1181471.5152
41 | 2541189.3387 | 1181556.5748
42 | 2541196.023 | 1181554.594
43 | 2541248.1311 | 1181570.9037
44 | 2541231.866 | 1181555.4954
45 | 2541259.6916 | 1181573.4242
46 | 2541434.5684 | 1181483.0541
47 | 2541196.9357 | 1181608.1831
48 | 2541291.3208 | 1181422.7814
49 | 2541258.056 | 1181420.2378
50 | 2541265.9236 | 1181418.5458
51 | 2541387.6319 | 1181415.8762
52 | 2541379.7984 | 1181415.4058
53 | 2541407.2368 | 1181410.7166
54 | 2541157.7619 | 1181718.8707
55 | 2541135.3609 | 1181697.0647
56 | 2541664.2653 | 1181937.0952
57 | 2541653.4535 | 1181923.1854
58 | 2541263.9687 | 1181342.9612
59 | 2541350.3541 | 1181422.2125
60 | 2541357.0982 | 1181341.5719
61 | 2541328.7349 | 1181343.46
62 | 2541362.4145 | 1181341.0928
63 | 2541328.4261 | 1181343.4609
64 | 2541366.8885 | 1181340.6897
65 | 2541301.2359 | 1181343.5386
66 | 2541284.2519 | 1181293.8569
67 | 2541229.817 | 1181566.9108

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1