## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5938-12_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5938-12_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5938-12_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5938-12_0_2_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_5938-12_0_2_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_5938-12_0_2_node_59 | 0.4 | n |  | TRUE
6 | bus_LV_5938-12_0_2_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_5938-12_0_2_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_5938-12_0_2_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_5938-12_0_2_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_5938-12_0_2_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_5938-12_0_2_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_5938-12_0_2_node_52 | 0.4 | n |  | TRUE
13 | bus_LV_5938-12_0_2_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_5938-12_0_2_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_5938-12_0_2_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_5938-12_0_2_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_5938-12_0_2_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_5938-12_0_2_node_54 | 0.4 | n |  | TRUE
19 | bus_LV_5938-12_0_2_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_5938-12_0_2_node_49 | 0.4 | n |  | TRUE
21 | bus_LV_5938-12_0_2_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_5938-12_0_2_node_58 | 0.4 | n |  | TRUE
23 | bus_LV_5938-12_0_2_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_5938-12_0_2_node_57 | 0.4 | n |  | TRUE
25 | bus_LV_5938-12_0_2_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_5938-12_0_2_node_56 | 0.4 | n |  | TRUE
27 | bus_LV_5938-12_0_2_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_5938-12_0_2_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_5938-12_0_2_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_5938-12_0_2_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_5938-12_0_2_node_50 | 0.4 | n |  | TRUE
32 | bus_LV_5938-12_0_2_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_5938-12_0_2_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_5938-12_0_2_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_5938-12_0_2_node_55 | 0.4 | n |  | TRUE
36 | bus_LV_5938-12_0_2_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_5938-12_0_2_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_5938-12_0_2_node_51 | 0.4 | n |  | TRUE
39 | bus_LV_5938-12_0_2_node_17 | 0.4 | n |  | TRUE
40 | bus_LV_5938-12_0_2_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_5938-12_0_2_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_5938-12_0_2_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_5938-12_0_2_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_5938-12_0_2_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_5938-12_0_2_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_5938-12_0_2_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_5938-12_0_2_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_5938-12_0_2_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_5938-12_0_2_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_5938-12_0_2_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_5938-12_0_2_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_5938-12_0_2_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_5938-12_0_2_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_5938-12_0_2_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_5938-12_0_2_node_45 | 0.4 | n |  | TRUE
56 | bus_MV_316_1_node_180 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5938-12_0_2_load_0 | 0 | 0.002826 | 0.00070827 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5938-12_0_2_load_1 | 1 | 0.0033716 | 0.00084499 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5938-12_0_2_load_59 | 5 | 0.0055683 | 0.0013956 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5938-12_0_2_load_25 | 8 | 0.0019232 | 0.000482 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5938-12_0_2_load_24 | 10 | 0.0019766 | 0.0004954 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5938-12_0_2_load_52 | 12 | 0.028893 | 0.0072413 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5938-12_0_2_load_32 | 16 | 0.0020807 | 0.00052146 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5938-12_0_2_load_54 | 18 | 0.0051651 | 0.0012945 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5938-12_0_2_load_49 | 20 | 0.0053368 | 0.0013375 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5938-12_0_2_load_48 | 21 | 0.0072543 | 0.0018181 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5938-12_0_2_load_58 | 22 | 0.0066078 | 0.0016561 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5938-12_0_2_load_57 | 24 | 0.0061708 | 0.0015465 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5938-12_0_2_load_56 | 26 | 0.0069035 | 0.0017302 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5938-12_0_2_load_27 | 27 | 0.005242 | 0.0013138 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5938-12_0_2_load_29 | 28 | 0.0015483 | 0.00038804 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5938-12_0_2_load_50 | 31 | 0.0034329 | 0.00086038 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5938-12_0_2_load_26 | 32 | 0.0026961 | 0.00067571 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5938-12_0_2_load_18 | 33 | 0.0038647 | 0.00096859 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5938-12_0_2_load_30 | 34 | 0.0037154 | 0.00093116 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5938-12_0_2_load_55 | 35 | 0.0051904 | 0.0013008 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5938-12_0_2_load_28 | 37 | 0.010212 | 0.0025595 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5938-12_0_2_load_51 | 38 | 0.0018799 | 0.00047114 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5938-12_0_2_load_17 | 39 | 0.0076832 | 0.0019256 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5938-12_0_2_load_20 | 41 | 0.006907 | 0.0017311 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5938-12_0_2_load_23 | 43 | 0.0042946 | 0.0010763 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5938-12_0_2_load_22 | 44 | 0.0047445 | 0.0011891 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5938-12_0_2_load_33 | 45 | 0.00916 | 0.0022957 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5938-12_0_2_load_34 | 46 | 0.0090179 | 0.0022601 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5938-12_0_2_load_39 | 50 | 0.0089504 | 0.0022432 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5938-12_0_2_load_38 | 51 | 0.0088859 | 0.002227 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5938-12_0_2_load_42 | 52 | 0.0077993 | 0.0019547 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5938-12_0_2_load_44 | 54 | 0.0082622 | 0.0020707 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5938-12_0_2_load_45 | 55 | 0.018363 | 0.0046023 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5938-12_0_2_line_0 |  | 0 | 1 | 0.0012313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5938-12_0_2_line_1 |  | 0 | 2 | 0.009442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5938-12_0_2_line_2 |  | 2 | 3 | 0.026741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5938-12_0_2_line_3 |  | 3 | 27 | 0.015052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_5938-12_0_2_line_4 |  | 3 | 28 | 0.025932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5938-12_0_2_line_5 |  | 3 | 21 | 0.015621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_5938-12_0_2_line_6 |  | 4 | 5 | 0.00512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5938-12_0_2_line_7 |  | 4 | 6 | 0.008529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5938-12_0_2_line_8 |  | 6 | 22 | 0.051495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_5938-12_0_2_line_9 |  | 6 | 23 | 0.029023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5938-12_0_2_line_10 |  | 6 | 19 | 0.010742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_5938-12_0_2_line_11 |  | 7 | 8 | 0.0071296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5938-12_0_2_line_12 |  | 7 | 9 | 0.17536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5938-12_0_2_line_13 |  | 7 | 10 | 0.042547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5938-12_0_2_line_14 |  | 8 | 34 | 0.011761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5938-12_0_2_line_15 |  | 9 | 33 | 0.011105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5938-12_0_2_line_16 |  | 9 | 13 | 0.15162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_5938-12_0_2_line_17 |  | 9 | 29 | 0.023517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_5938-12_0_2_line_18 |  | 11 | 12 | 0.003122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5938-12_0_2_line_19 |  | 11 | 13 | 0.06321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5938-12_0_2_line_20 |  | 13 | 17 | 0.023474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5938-12_0_2_line_21 |  | 13 | 18 | 0.012723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5938-12_0_2_line_22 |  | 14 | 15 | 0.00265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5938-12_0_2_line_23 |  | 14 | 16 | 0.0077823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5938-12_0_2_line_24 |  | 15 | 34 | 0.0091552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5938-12_0_2_line_25 |  | 17 | 35 | 0.012558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5938-12_0_2_line_26 |  | 17 | 36 | 0.017956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5938-12_0_2_line_27 |  | 19 | 20 | 0.013257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5938-12_0_2_line_28 |  | 19 | 21 | 0.024346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_5938-12_0_2_line_29 |  | 23 | 24 | 0.005199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5938-12_0_2_line_30 |  | 23 | 25 | 0.008875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5938-12_0_2_line_31 |  | 25 | 26 | 0.051191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5938-12_0_2_line_32 |  | 27 | 30 | 0.025663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_5938-12_0_2_line_33 |  | 28 | 37 | 0.019321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5938-12_0_2_line_34 |  | 29 | 30 | 0.002083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_5938-12_0_2_line_35 |  | 29 | 31 | 0.010971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5938-12_0_2_line_36 |  | 30 | 32 | 0.011841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5938-12_0_2_line_37 |  | 31 | 38 | 0.0073572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5938-12_0_2_line_38 |  | 33 | 39 | 0.024033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5938-12_0_2_line_39 |  | 36 | 51 | 0.017364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5938-12_0_2_line_40 |  | 39 | 40 | 0.0081234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5938-12_0_2_line_41 |  | 40 | 41 | 0.032997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5938-12_0_2_line_42 |  | 40 | 42 | 0.018851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5938-12_0_2_line_43 |  | 42 | 43 | 0.0095517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5938-12_0_2_line_44 |  | 42 | 44 | 0.024841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5938-12_0_2_line_45 |  | 45 | 46 | 0.015838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5938-12_0_2_line_46 |  | 46 | 47 | 0.01736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5938-12_0_2_line_47 |  | 47 | 48 | 0.009689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5938-12_0_2_line_48 |  | 48 | 49 | 0.006213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5938-12_0_2_line_49 |  | 48 | 50 | 0.017445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5938-12_0_2_line_50 |  | 49 | 52 | 0.015209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5938-12_0_2_line_51 |  | 50 | 51 | 0.01568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5938-12_0_2_line_52 |  | 52 | 53 | 0.0070562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5938-12_0_2_line_53 |  | 53 | 54 | 0.0087389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5938-12_0_2_line_54 |  | 53 | 55 | 0.024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5938-12_0_2_trafo_58 | 0.63 MVA 20/0.4 kV | 56 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2538602.3583 | 1182153.3971 | 2538603.4532 | 1182153.9604
1 | 2538593.9623 | 1182149.0775 | 2538602.3583 | 1182153.3971
2 | 2538577.2047 | 1182158.3658 | 2538581.5698 | 1182160.3332 | 2538588.3813 | 1182146.2109 | 2538593.9623 | 1182149.0775
3 | 2538577.2047 | 1182158.3658 | 2538578.9106 | 1182154.9464 | 2538583.926 | 1182144.8978
4 | 2538577.2047 | 1182158.3658 | 2538561.653 | 1182151.2437 | 2538556.5605 | 1182148.3499 | 2538554.502 | 1182146.209
5 | 2538577.2047 | 1182158.3658 | 2538576.4511 | 1182160.8305 | 2538570.6618 | 1182172.5194
6 | 2538577.5215 | 1182194.4163 | 2538572.8792 | 1182192.2294
7 | 2538569.1323 | 1182199.8944 | 2538572.8792 | 1182192.2294
8 | 2538569.1323 | 1182199.8944 | 2538594.7814 | 1182212.4826 | 2538600.4602 | 1182215.2148 | 2538603.1296 | 1182215.6432 | 2538605.5589 | 1182215.0068 | 2538608.5713 | 1182212.3966 | 2538609.7712 | 1182210.2609 | 2538605.1823 | 1182208.0734
9 | 2538556.396 | 1182225.9732 | 2538565.1088 | 1182208.1404 | 2538569.1323 | 1182199.8944
10 | 2538559.9658 | 1182194.3854 | 2538563.7752 | 1182197.259 | 2538569.1323 | 1182199.8944
11 | 2538707.6758 | 1182147.9107 | 2538710.6376 | 1182141.4255
12 | 2538606.8808 | 1182099.0611 | 2538610.6199 | 1182090.6291 | 2538616.4939 | 1182079.6404 | 2538617.6689 | 1182077.3048 | 2538618.5681 | 1182074.8942 | 2538619.9127 | 1182071.9788 | 2538623.1886 | 1182073.4571 | 2538627.6613 | 1182075.479 | 2538627.771 | 1182074.2661 | 2538630.6102 | 1182068.1669 | 2538633.4571 | 1182062.0787 | 2538635.0228 | 1182060.6173 | 2538637.6029 | 1182060.5242 | 2538639.3325 | 1182057.1712 | 2538643.2643 | 1182062.2893 | 2538665.7834 | 1182093.5316 | 2538669.5622 | 1182098.6291 | 2538672.4014 | 1182102.2131 | 2538705.0611 | 1182144.6246 | 2538707.6758 | 1182147.9107
13 | 2538707.6758 | 1182147.9107 | 2538732.9869 | 1182182.1101
14 | 2538715.5235 | 1182130.7271 | 2538710.6376 | 1182141.4255
15 | 2538606.8808 | 1182099.0611 | 2538596.801 | 1182094.4018
16 | 2538606.8808 | 1182099.0611 | 2538610.6199 | 1182090.6291 | 2538616.4939 | 1182079.6404 | 2538617.6689 | 1182077.3048 | 2538618.5681 | 1182074.8942 | 2538621.6566 | 1182076.7191 | 2538625.1423 | 1182082.2754 | 2538648.0574 | 1182111.1677 | 2538665.2454 | 1182134.1378 | 2538671.3541 | 1182142.302 | 2538684.1009 | 1182158.8807 | 2538677.2007 | 1182169.5908 | 2538674.9041 | 1182174.2392
17 | 2538596.3141 | 1182120.0703 | 2538601.9034 | 1182108.8733 | 2538605.3827 | 1182101.9003 | 2538606.8808 | 1182099.0611
18 | 2538708.6894 | 1182196.8836 | 2538711.2675 | 1182195.1117
19 | 2538674.9041 | 1182174.2392 | 2538677.2007 | 1182169.5908 | 2538684.1009 | 1182158.8807 | 2538711.2675 | 1182195.1117
20 | 2538674.9041 | 1182174.2392 | 2538664.4982 | 1182195.2911
21 | 2538663.5357 | 1182168.4636 | 2538674.9041 | 1182174.2392
22 | 2538719.3267 | 1182122.3992 | 2538716.9399 | 1182121.2341
23 | 2538716.9399 | 1182121.2341 | 2538709.9453 | 1182117.8225
24 | 2538719.3267 | 1182122.3992 | 2538715.5235 | 1182130.7271
25 | 2538653.3881 | 1182189.3795 | 2538664.4982 | 1182195.2911
26 | 2538656.5078 | 1182211.371 | 2538660.2486 | 1182203.8395 | 2538664.4982 | 1182195.2911
27 | 2538559.9658 | 1182194.3854 | 2538547.9091 | 1182188.8732
28 | 2538559.9658 | 1182194.3854 | 2538560.584 | 1182192.8671 | 2538570.6618 | 1182172.5194
29 | 2538560.9801 | 1182228.4498 | 2538556.396 | 1182225.9732
30 | 2538552.4996 | 1182233.9511 | 2538556.396 | 1182225.9732
31 | 2538552.4996 | 1182233.9511 | 2538576.1079 | 1182245.6153 | 2538581.7926 | 1182248.1806 | 2538585.5428 | 1182249.7541 | 2538588.8752 | 1182249.3196 | 2538592.5664 | 1182245.146 | 2538592.7623 | 1182244.1435 | 2538588.4662 | 1182242.2087
32 | 2538595.3864 | 1182121.9364 | 2538583.926 | 1182144.8978
33 | 2538539.7632 | 1182134.5604 | 2538545.8104 | 1182137.3653 | 2538549.9748 | 1182139.8572 | 2538551.5623 | 1182142.0088 | 2538554.4224 | 1182146.1262 | 2538554.502 | 1182146.209
34 | 2538596.3141 | 1182120.0703 | 2538595.3864 | 1182121.9364
35 | 2538596.3141 | 1182120.0703 | 2538586.3616 | 1182115.4543
36 | 2538595.3864 | 1182121.9364 | 2538584.6916 | 1182116.8552
37 | 2538579.6873 | 1182112.3588 | 2538586.3616 | 1182115.4543
38 | 2538574.9858 | 1182084.3179 | 2538596.801 | 1182094.4018
39 | 2538656.5078 | 1182211.371 | 2538647.7115 | 1182209.927 | 2538644.9085 | 1182211.3677 | 2538644.1564 | 1182211.7423 | 2538642.2303 | 1182215.7634
40 | 2538567.612 | 1182080.9095 | 2538574.9858 | 1182084.3179
41 | 2538567.612 | 1182080.9095 | 2538561.7129 | 1182084.2386 | 2538556.2288 | 1182088.5752 | 2538552.1145 | 1182092.4529 | 2538550.4382 | 1182094.2934 | 2538548.1257 | 1182095.1621 | 2538545.6855 | 1182094.7536 | 2538543.1104 | 1182093.8462 | 2538540.0883 | 1182092.2584
42 | 2538550.3738 | 1182073.171 | 2538567.612 | 1182080.9095
43 | 2538550.3738 | 1182073.171 | 2538554.9809 | 1182064.8038
44 | 2538550.3738 | 1182073.171 | 2538533.2585 | 1182065.5092 | 2538535.4979 | 1182059.8471
45 | 2538674.4472 | 1182249.8641 | 2538660.1922 | 1182242.9617
46 | 2538644.5671 | 1182235.3959 | 2538660.1922 | 1182242.9617
47 | 2538639.8817 | 1182243.8821 | 2538644.5671 | 1182235.3959
48 | 2538639.8817 | 1182243.8821 | 2538636.8831 | 1182249.327
49 | 2538639.8817 | 1182243.8821 | 2538634.6891 | 1182240.1555 | 2538633.0155 | 1182235.57 | 2538634.3256 | 1182232.2658 | 2538635.4566 | 1182229.9047
50 | 2538636.8831 | 1182249.327 | 2538630.2008 | 1182262.989
51 | 2538642.2303 | 1182215.7634 | 2538635.4566 | 1182229.9047
52 | 2538627.1005 | 1182269.3275 | 2538630.2008 | 1182262.989
53 | 2538627.1005 | 1182269.3275 | 2538623.2563 | 1182277.1756
54 | 2538648.131 | 1182276.1157 | 2538646.6173 | 1182278.1768 | 2538644.1723 | 1182278.0351 | 2538627.1005 | 1182269.3275

## bus_geodata
| x | y | coords
0 | 2538602.3583 | 1182153.3971
1 | 2538603.4532 | 1182153.9604
2 | 2538593.9623 | 1182149.0775
3 | 2538577.2047 | 1182158.3658
4 | 2538572.8792 | 1182192.2294
5 | 2538577.5215 | 1182194.4163
6 | 2538569.1323 | 1182199.8944
7 | 2538707.6758 | 1182147.9107
8 | 2538710.6376 | 1182141.4255
9 | 2538606.8808 | 1182099.0611
10 | 2538732.9869 | 1182182.1101
11 | 2538711.2675 | 1182195.1117
12 | 2538708.6894 | 1182196.8836
13 | 2538674.9041 | 1182174.2392
14 | 2538716.9399 | 1182121.2341
15 | 2538719.3267 | 1182122.3992
16 | 2538709.9453 | 1182117.8225
17 | 2538664.4982 | 1182195.2911
18 | 2538663.5357 | 1182168.4636
19 | 2538559.9658 | 1182194.3854
20 | 2538547.9091 | 1182188.8732
21 | 2538570.6618 | 1182172.5194
22 | 2538605.1823 | 1182208.0734
23 | 2538556.396 | 1182225.9732
24 | 2538560.9801 | 1182228.4498
25 | 2538552.4996 | 1182233.9511
26 | 2538588.4662 | 1182242.2087
27 | 2538583.926 | 1182144.8978
28 | 2538554.502 | 1182146.209
29 | 2538596.3141 | 1182120.0703
30 | 2538595.3864 | 1182121.9364
31 | 2538586.3616 | 1182115.4543
32 | 2538584.6916 | 1182116.8552
33 | 2538596.801 | 1182094.4018
34 | 2538715.5235 | 1182130.7271
35 | 2538653.3881 | 1182189.3795
36 | 2538656.5078 | 1182211.371
37 | 2538539.7632 | 1182134.5604
38 | 2538579.6873 | 1182112.3588
39 | 2538574.9858 | 1182084.3179
40 | 2538567.612 | 1182080.9095
41 | 2538540.0883 | 1182092.2584
42 | 2538550.3738 | 1182073.171
43 | 2538554.9809 | 1182064.8038
44 | 2538535.4979 | 1182059.8471
45 | 2538674.4472 | 1182249.8641
46 | 2538660.1922 | 1182242.9617
47 | 2538644.5671 | 1182235.3959
48 | 2538639.8817 | 1182243.8821
49 | 2538636.8831 | 1182249.327
50 | 2538635.4566 | 1182229.9047
51 | 2538642.2303 | 1182215.7634
52 | 2538630.2008 | 1182262.989
53 | 2538627.1005 | 1182269.3275
54 | 2538623.2563 | 1182277.1756
55 | 2538648.131 | 1182276.1157
56 | 2538569.1323 | 1182199.8944

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1