## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5938-33_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5938-33_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5938-33_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5938-33_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5938-33_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5938-33_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_5938-33_0_6_node_76 | 0.4 | n |  | TRUE
7 | bus_LV_5938-33_0_6_node_42 | 0.4 | n |  | TRUE
8 | bus_LV_5938-33_0_6_node_79 | 0.4 | n |  | TRUE
9 | bus_LV_5938-33_0_6_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_5938-33_0_6_node_88 | 0.4 | n |  | TRUE
11 | bus_LV_5938-33_0_6_node_85 | 0.4 | n |  | TRUE
12 | bus_LV_5938-33_0_6_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_5938-33_0_6_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_5938-33_0_6_node_153 | 0.4 | n |  | TRUE
15 | bus_LV_5938-33_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_5938-33_0_6_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_5938-33_0_6_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_5938-33_0_6_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_5938-33_0_6_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_5938-33_0_6_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_5938-33_0_6_node_151 | 0.4 | n |  | TRUE
22 | bus_LV_5938-33_0_6_node_112 | 0.4 | n |  | TRUE
23 | bus_LV_5938-33_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_5938-33_0_6_node_9 | 0.4 | n |  | TRUE
25 | bus_LV_5938-33_0_6_node_157 | 0.4 | n |  | TRUE
26 | bus_LV_5938-33_0_6_node_7 | 0.4 | n |  | TRUE
27 | bus_LV_5938-33_0_6_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_5938-33_0_6_node_149 | 0.4 | n |  | TRUE
29 | bus_LV_5938-33_0_6_node_106 | 0.4 | n |  | TRUE
30 | bus_LV_5938-33_0_6_node_148 | 0.4 | n |  | TRUE
31 | bus_LV_5938-33_0_6_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_5938-33_0_6_node_95 | 0.4 | n |  | TRUE
33 | bus_LV_5938-33_0_6_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_5938-33_0_6_node_92 | 0.4 | n |  | TRUE
35 | bus_LV_5938-33_0_6_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_5938-33_0_6_node_132 | 0.4 | n |  | TRUE
37 | bus_LV_5938-33_0_6_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_5938-33_0_6_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_5938-33_0_6_node_165 | 0.4 | n |  | TRUE
40 | bus_LV_5938-33_0_6_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_5938-33_0_6_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_5938-33_0_6_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_5938-33_0_6_node_97 | 0.4 | n |  | TRUE
44 | bus_LV_5938-33_0_6_node_96 | 0.4 | n |  | TRUE
45 | bus_LV_5938-33_0_6_node_130 | 0.4 | n |  | TRUE
46 | bus_LV_5938-33_0_6_node_80 | 0.4 | n |  | TRUE
47 | bus_LV_5938-33_0_6_node_87 | 0.4 | n |  | TRUE
48 | bus_LV_5938-33_0_6_node_25 | 0.4 | n |  | TRUE
49 | bus_LV_5938-33_0_6_node_114 | 0.4 | n |  | TRUE
50 | bus_LV_5938-33_0_6_node_28 | 0.4 | n |  | TRUE
51 | bus_LV_5938-33_0_6_node_84 | 0.4 | n |  | TRUE
52 | bus_LV_5938-33_0_6_node_90 | 0.4 | n |  | TRUE
53 | bus_LV_5938-33_0_6_node_10 | 0.4 | n |  | TRUE
54 | bus_LV_5938-33_0_6_node_160 | 0.4 | n |  | TRUE
55 | bus_LV_5938-33_0_6_node_6 | 0.4 | n |  | TRUE
56 | bus_LV_5938-33_0_6_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_5938-33_0_6_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_5938-33_0_6_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_5938-33_0_6_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_5938-33_0_6_node_75 | 0.4 | n |  | TRUE
61 | bus_LV_5938-33_0_6_node_77 | 0.4 | n |  | TRUE
62 | bus_LV_5938-33_0_6_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_5938-33_0_6_node_158 | 0.4 | n |  | TRUE
64 | bus_LV_5938-33_0_6_node_110 | 0.4 | n |  | TRUE
65 | bus_LV_5938-33_0_6_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_5938-33_0_6_node_69 | 0.4 | n |  | TRUE
67 | bus_LV_5938-33_0_6_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_5938-33_0_6_node_113 | 0.4 | n |  | TRUE
69 | bus_LV_5938-33_0_6_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_5938-33_0_6_node_86 | 0.4 | n |  | TRUE
71 | bus_LV_5938-33_0_6_node_150 | 0.4 | n |  | TRUE
72 | bus_LV_5938-33_0_6_node_111 | 0.4 | n |  | TRUE
73 | bus_LV_5938-33_0_6_node_109 | 0.4 | n |  | TRUE
74 | bus_LV_5938-33_0_6_node_152 | 0.4 | n |  | TRUE
75 | bus_LV_5938-33_0_6_node_91 | 0.4 | n |  | TRUE
76 | bus_LV_5938-33_0_6_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_5938-33_0_6_node_121 | 0.4 | n |  | TRUE
78 | bus_LV_5938-33_0_6_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_5938-33_0_6_node_98 | 0.4 | n |  | TRUE
80 | bus_LV_5938-33_0_6_node_89 | 0.4 | n |  | TRUE
81 | bus_LV_5938-33_0_6_node_83 | 0.4 | n |  | TRUE
82 | bus_LV_5938-33_0_6_node_81 | 0.4 | n |  | TRUE
83 | bus_LV_5938-33_0_6_node_133 | 0.4 | n |  | TRUE
84 | bus_LV_5938-33_0_6_node_35 | 0.4 | n |  | TRUE
85 | bus_LV_5938-33_0_6_node_36 | 0.4 | n |  | TRUE
86 | bus_LV_5938-33_0_6_node_37 | 0.4 | n |  | TRUE
87 | bus_LV_5938-33_0_6_node_38 | 0.4 | n |  | TRUE
88 | bus_LV_5938-33_0_6_node_39 | 0.4 | n |  | TRUE
89 | bus_LV_5938-33_0_6_node_154 | 0.4 | n |  | TRUE
90 | bus_LV_5938-33_0_6_node_155 | 0.4 | n |  | TRUE
91 | bus_LV_5938-33_0_6_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_5938-33_0_6_node_156 | 0.4 | n |  | TRUE
93 | bus_LV_5938-33_0_6_node_43 | 0.4 | n |  | TRUE
94 | bus_LV_5938-33_0_6_node_46 | 0.4 | n |  | TRUE
95 | bus_LV_5938-33_0_6_node_47 | 0.4 | n |  | TRUE
96 | bus_LV_5938-33_0_6_node_49 | 0.4 | n |  | TRUE
97 | bus_LV_5938-33_0_6_node_52 | 0.4 | n |  | TRUE
98 | bus_LV_5938-33_0_6_node_53 | 0.4 | n |  | TRUE
99 | bus_LV_5938-33_0_6_node_54 | 0.4 | n |  | TRUE
100 | bus_LV_5938-33_0_6_node_55 | 0.4 | n |  | TRUE
101 | bus_LV_5938-33_0_6_node_131 | 0.4 | n |  | TRUE
102 | bus_LV_5938-33_0_6_node_115 | 0.4 | n |  | TRUE
103 | bus_LV_5938-33_0_6_node_116 | 0.4 | n |  | TRUE
104 | bus_LV_5938-33_0_6_node_58 | 0.4 | n |  | TRUE
105 | bus_LV_5938-33_0_6_node_59 | 0.4 | n |  | TRUE
106 | bus_LV_5938-33_0_6_node_60 | 0.4 | n |  | TRUE
107 | bus_LV_5938-33_0_6_node_62 | 0.4 | n |  | TRUE
108 | bus_LV_5938-33_0_6_node_63 | 0.4 | n |  | TRUE
109 | bus_LV_5938-33_0_6_node_61 | 0.4 | n |  | TRUE
110 | bus_LV_5938-33_0_6_node_64 | 0.4 | n |  | TRUE
111 | bus_LV_5938-33_0_6_node_65 | 0.4 | n |  | TRUE
112 | bus_LV_5938-33_0_6_node_66 | 0.4 | n |  | TRUE
113 | bus_LV_5938-33_0_6_node_67 | 0.4 | n |  | TRUE
114 | bus_LV_5938-33_0_6_node_74 | 0.4 | n |  | TRUE
115 | bus_LV_5938-33_0_6_node_73 | 0.4 | n |  | TRUE
116 | bus_LV_5938-33_0_6_node_166 | 0.4 | n |  | TRUE
117 | bus_LV_5938-33_0_6_node_167 | 0.4 | n |  | TRUE
118 | bus_LV_5938-33_0_6_node_71 | 0.4 | n |  | TRUE
119 | bus_LV_5938-33_0_6_node_70 | 0.4 | n |  | TRUE
120 | bus_LV_5938-33_0_6_node_72 | 0.4 | n |  | TRUE
121 | bus_LV_5938-33_0_6_node_161 | 0.4 | n |  | TRUE
122 | bus_LV_5938-33_0_6_node_162 | 0.4 | n |  | TRUE
123 | bus_LV_5938-33_0_6_node_163 | 0.4 | n |  | TRUE
124 | bus_LV_5938-33_0_6_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_5938-33_0_6_node_82 | 0.4 | n |  | TRUE
126 | bus_LV_5938-33_0_6_node_93 | 0.4 | n |  | TRUE
127 | bus_LV_5938-33_0_6_node_94 | 0.4 | n |  | TRUE
128 | bus_LV_5938-33_0_6_node_102 | 0.4 | n |  | TRUE
129 | bus_LV_5938-33_0_6_node_103 | 0.4 | n |  | TRUE
130 | bus_LV_5938-33_0_6_node_99 | 0.4 | n |  | TRUE
131 | bus_LV_5938-33_0_6_node_100 | 0.4 | n |  | TRUE
132 | bus_LV_5938-33_0_6_node_101 | 0.4 | n |  | TRUE
133 | bus_LV_5938-33_0_6_node_104 | 0.4 | n |  | TRUE
134 | bus_LV_5938-33_0_6_node_105 | 0.4 | n |  | TRUE
135 | bus_LV_5938-33_0_6_node_108 | 0.4 | n |  | TRUE
136 | bus_LV_5938-33_0_6_node_164 | 0.4 | n |  | TRUE
137 | bus_LV_5938-33_0_6_node_129 | 0.4 | n |  | TRUE
138 | bus_LV_5938-33_0_6_node_127 | 0.4 | n |  | TRUE
139 | bus_LV_5938-33_0_6_node_141 | 0.4 | n |  | TRUE
140 | bus_LV_5938-33_0_6_node_128 | 0.4 | n |  | TRUE
141 | bus_LV_5938-33_0_6_node_138 | 0.4 | n |  | TRUE
142 | bus_LV_5938-33_0_6_node_120 | 0.4 | n |  | TRUE
143 | bus_LV_5938-33_0_6_node_119 | 0.4 | n |  | TRUE
144 | bus_LV_5938-33_0_6_node_126 | 0.4 | n |  | TRUE
145 | bus_LV_5938-33_0_6_node_117 | 0.4 | n |  | TRUE
146 | bus_LV_5938-33_0_6_node_118 | 0.4 | n |  | TRUE
147 | bus_LV_5938-33_0_6_node_124 | 0.4 | n |  | TRUE
148 | bus_LV_5938-33_0_6_node_135 | 0.4 | n |  | TRUE
149 | bus_LV_5938-33_0_6_node_146 | 0.4 | n |  | TRUE
150 | bus_LV_5938-33_0_6_node_122 | 0.4 | n |  | TRUE
151 | bus_LV_5938-33_0_6_node_134 | 0.4 | n |  | TRUE
152 | bus_LV_5938-33_0_6_node_145 | 0.4 | n |  | TRUE
153 | bus_LV_5938-33_0_6_node_123 | 0.4 | n |  | TRUE
154 | bus_LV_5938-33_0_6_node_125 | 0.4 | n |  | TRUE
155 | bus_LV_5938-33_0_6_node_139 | 0.4 | n |  | TRUE
156 | bus_LV_5938-33_0_6_node_142 | 0.4 | n |  | TRUE
157 | bus_LV_5938-33_0_6_node_143 | 0.4 | n |  | TRUE
158 | bus_LV_5938-33_0_6_node_147 | 0.4 | n |  | TRUE
159 | bus_LV_5938-33_0_6_node_144 | 0.4 | n |  | TRUE
160 | bus_LV_5938-33_0_6_node_140 | 0.4 | n |  | TRUE
161 | bus_LV_5938-33_0_6_node_159 | 0.4 | n |  | TRUE
162 | bus_MV_455_0_node_55 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5938-33_0_6_load_0 | 0 | 0.0017083 | 0.00042814 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5938-33_0_6_load_1 | 1 | 0.0025785 | 0.00064622 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5938-33_0_6_load_2 | 2 | 0.0028835 | 0.00072268 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5938-33_0_6_load_3 | 3 | 0.0039505 | 0.00099009 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5938-33_0_6_load_76 | 6 | 0.0025667 | 0.00064327 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5938-33_0_6_load_42 | 7 | 0.0013132 | 0.00032913 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5938-33_0_6_load_79 | 8 | 0.0031025 | 0.00077756 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5938-33_0_6_load_88 | 10 | 0.0057292 | 0.0014359 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5938-33_0_6_load_85 | 11 | 0.0014733 | 0.00036925 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5938-33_0_6_load_153 | 14 | 0.0034523 | 0.00086522 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5938-33_0_6_load_151 | 21 | 0.0046481 | 0.0011649 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5938-33_0_6_load_112 | 22 | 0.0013443 | 0.00033692 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5938-33_0_6_load_157 | 25 | 0.00113 | 0.00028321 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5938-33_0_6_load_148 | 30 | 0.0020251 | 0.00050755 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5938-33_0_6_load_95 | 32 | 0.0017842 | 0.00044715 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5938-33_0_6_load_92 | 34 | 0.0017809 | 0.00044634 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5938-33_0_6_load_132 | 36 | 0.00060557 | 0.00015177 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5938-33_0_6_load_165 | 39 | 0.0066535 | 0.0016675 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5938-33_0_6_load_97 | 43 | 0.0017111 | 0.00042885 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5938-33_0_6_load_96 | 44 | 0.001742 | 0.00043659 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5938-33_0_6_load_130 | 45 | 0.01674 | 0.0041954 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5938-33_0_6_load_80 | 46 | 0.0013491 | 0.00033813 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5938-33_0_6_load_87 | 47 | 0.0031003 | 0.00077701 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5938-33_0_6_load_114 | 49 | 0.001047 | 0.00026241 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5938-33_0_6_load_90 | 52 | 0.0012453 | 0.0003121 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5938-33_0_6_load_160 | 54 | 0.0088284 | 0.0022126 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5938-33_0_6_load_6 | 55 | 0.02196 | 0.0055037 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5938-33_0_6_load_40 | 56 | 0.0033839 | 0.00084809 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5938-33_0_6_load_68 | 57 | 0.0011615 | 0.0002911 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5938-33_0_6_load_50 | 58 | 0.0082675 | 0.002072 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5938-33_0_6_load_45 | 59 | 0.0031229 | 0.00078268 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5938-33_0_6_load_75 | 60 | 0.00069661 | 0.00017459 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5938-33_0_6_load_77 | 61 | 0.0014315 | 0.00035876 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5938-33_0_6_load_110 | 64 | 0.0075943 | 0.0019033 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5938-33_0_6_load_44 | 65 | 0.0062416 | 0.0015643 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5938-33_0_6_load_69 | 66 | 0.0028784 | 0.00072139 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5938-33_0_6_load_113 | 68 | 0.0021717 | 0.00054429 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5938-33_0_6_load_51 | 69 | 0.0084868 | 0.002127 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5938-33_0_6_load_86 | 70 | 0.0011643 | 0.0002918 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5938-33_0_6_load_150 | 71 | 0.0018093 | 0.00045346 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5938-33_0_6_load_111 | 72 | 0.0036 | 0.00090225 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5938-33_0_6_load_152 | 74 | 0.0023504 | 0.00058907 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5938-33_0_6_load_91 | 75 | 0.0017282 | 0.00043312 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5938-33_0_6_load_56 | 78 | 0.0030222 | 0.00075743 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5938-33_0_6_load_98 | 79 | 0.0016162 | 0.00040507 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5938-33_0_6_load_89 | 80 | 0.00090259 | 0.00022621 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5938-33_0_6_load_83 | 81 | 0.001266 | 0.0003173 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5938-33_0_6_load_81 | 82 | 0.001251 | 0.00031354 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5938-33_0_6_load_133 | 83 | 0.0040836 | 0.0010234 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5938-33_0_6_load_35 | 84 | 0.009135 | 0.0022894 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5938-33_0_6_load_36 | 85 | 0.0008493 | 0.00021285 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5938-33_0_6_load_37 | 86 | 0.0007678 | 0.00019243 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5938-33_0_6_load_38 | 87 | 0.0015156 | 0.00037985 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5938-33_0_6_load_39 | 88 | 0.00085321 | 0.00021383 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5938-33_0_6_load_154 | 89 | 0.0017253 | 0.0004324 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5938-33_0_6_load_155 | 90 | 0.00092825 | 0.00023264 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5938-33_0_6_load_78 | 91 | 0.0014255 | 0.00035726 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5938-33_0_6_load_156 | 92 | 0.0009532 | 0.00023889 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5938-33_0_6_load_43 | 93 | 0.0032471 | 0.00081379 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5938-33_0_6_load_46 | 94 | 0.0064741 | 0.0016226 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5938-33_0_6_load_47 | 95 | 0.0080344 | 0.0020136 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5938-33_0_6_load_49 | 96 | 0.0071861 | 0.001801 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5938-33_0_6_load_52 | 97 | 0.0045911 | 0.0011506 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5938-33_0_6_load_53 | 98 | 0.0071888 | 0.0018017 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5938-33_0_6_load_54 | 99 | 0.0089492 | 0.0022429 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5938-33_0_6_load_55 | 100 | 0.013245 | 0.0033194 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5938-33_0_6_load_131 | 101 | 0.0018304 | 0.00045875 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5938-33_0_6_load_115 | 102 | 0.0016207 | 0.00040618 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5938-33_0_6_load_58 | 104 | 0.0038033 | 0.0009532 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5938-33_0_6_load_60 | 106 | 0.0062025 | 0.0015545 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5938-33_0_6_load_62 | 107 | 0.0054141 | 0.0013569 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5938-33_0_6_load_63 | 108 | 0.0048339 | 0.0012115 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5938-33_0_6_load_61 | 109 | 0.0065143 | 0.0016326 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5938-33_0_6_load_64 | 110 | 0.0099628 | 0.0024969 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5938-33_0_6_load_66 | 112 | 0.0035568 | 0.00089143 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5938-33_0_6_load_74 | 114 | 0.0027787 | 0.0006964 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5938-33_0_6_load_166 | 116 | 0.0048809 | 0.0012233 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5938-33_0_6_load_167 | 117 | 0.0034423 | 0.00086273 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5938-33_0_6_load_70 | 119 | 0.0026531 | 0.00066494 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5938-33_0_6_load_162 | 122 | 0.0050045 | 0.0012542 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5938-33_0_6_load_163 | 123 | 0.0079276 | 0.0019869 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5938-33_0_6_load_82 | 125 | 0.0012674 | 0.00031765 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5938-33_0_6_load_93 | 126 | 0.0035953 | 0.00090106 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5938-33_0_6_load_94 | 127 | 0.0018182 | 0.00045568 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5938-33_0_6_load_102 | 128 | 0.0018253 | 0.00045745 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5938-33_0_6_load_103 | 129 | 0.0080504 | 0.0020176 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5938-33_0_6_load_99 | 130 | 0.0017661 | 0.00044262 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5938-33_0_6_load_100 | 131 | 0.0016133 | 0.00040433 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5938-33_0_6_load_101 | 132 | 0.0021005 | 0.00052645 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5938-33_0_6_load_104 | 133 | 0.0040813 | 0.0010229 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5938-33_0_6_load_164 | 136 | 0.0057744 | 0.0014472 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5938-33_0_6_load_127 | 138 | 0.0025196 | 0.00063147 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5938-33_0_6_load_141 | 139 | 0.0044614 | 0.0011181 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5938-33_0_6_load_138 | 141 | 0.0024545 | 0.00061515 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5938-33_0_6_load_126 | 144 | 0.0021552 | 0.00054015 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5938-33_0_6_load_117 | 145 | 0.0017128 | 0.00042927 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5938-33_0_6_load_124 | 147 | 0.0016178 | 0.00040547 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5938-33_0_6_load_135 | 148 | 0.0014696 | 0.00036831 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5938-33_0_6_load_146 | 149 | 0.0017116 | 0.00042896 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5938-33_0_6_load_122 | 150 | 0.0016545 | 0.00041467 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5938-33_0_6_load_134 | 151 | 0.0017247 | 0.00043225 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5938-33_0_6_load_145 | 152 | 0.0013966 | 0.00035001 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5938-33_0_6_load_123 | 153 | 0.0015914 | 0.00039883 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5938-33_0_6_load_125 | 154 | 0.0024139 | 0.00060498 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5938-33_0_6_load_139 | 155 | 0.0033201 | 0.00083211 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5938-33_0_6_load_142 | 156 | 0.0014571 | 0.00036519 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5938-33_0_6_load_147 | 158 | 0.0023785 | 0.0005961 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_5938-33_0_6_load_144 | 159 | 0.0014902 | 0.00037348 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_5938-33_0_6_load_140 | 160 | 0.00041316 | 0.00010355 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_5938-33_0_6_load_159 | 161 | 0.0045041 | 0.0011288 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 106 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5938-33_0_6_line_0 |  | 0 | 1 | 0.025909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_5938-33_0_6_line_1 |  | 0 | 2 | 0.020391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5938-33_0_6_line_2 |  | 1 | 3 | 0.0102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_5938-33_0_6_line_3 |  | 2 | 4 | 0.0037677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5938-33_0_6_line_4 |  | 3 | 5 | 0.019971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_5938-33_0_6_line_5 |  | 4 | 6 | 0.013246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5938-33_0_6_line_6 |  | 5 | 7 | 0.0050654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_5938-33_0_6_line_7 |  | 5 | 8 | 0.011371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5938-33_0_6_line_8 |  | 6 | 61 | 0.036886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5938-33_0_6_line_9 |  | 7 | 62 | 0.014146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_5938-33_0_6_line_10 |  | 9 | 10 | 0.034384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_5938-33_0_6_line_11 |  | 9 | 11 | 0.030641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_5938-33_0_6_line_12 |  | 10 | 17 | 0.02421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_5938-33_0_6_line_13 |  | 11 | 70 | 0.027249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_5938-33_0_6_line_14 |  | 12 | 13 | 0.058698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5938-33_0_6_line_15 |  | 12 | 14 | 0.01559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_5938-33_0_6_line_16 |  | 12 | 15 | 0.11419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_5938-33_0_6_line_17 |  | 12 | 16 | 0.024171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5938-33_0_6_line_18 |  | 13 | 60 | 0.0046309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5938-33_0_6_line_19 |  | 14 | 69 | 0.018651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_5938-33_0_6_line_20 |  | 15 | 55 | 0.04031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_5938-33_0_6_line_21 |  | 16 | 59 | 0.015984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5938-33_0_6_line_22 |  | 17 | 18 | 0.0094809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_5938-33_0_6_line_23 |  | 17 | 19 | 0.035795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_5938-33_0_6_line_24 |  | 18 | 22 | 0.011023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_5938-33_0_6_line_25 |  | 18 | 23 | 0.003262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_5938-33_0_6_line_26 |  | 19 | 56 | 0.019324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_5938-33_0_6_line_27 |  | 19 | 20 | 0.022307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5938-33_0_6_line_28 |  | 20 | 21 | 0.026127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5938-33_0_6_line_29 |  | 21 | 74 | 0.0019486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5938-33_0_6_line_30 |  | 22 | 68 | 0.011575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_5938-33_0_6_line_31 |  | 23 | 57 | 0.0085844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5938-33_0_6_line_32 |  | 23 | 58 | 0.020247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_5938-33_0_6_line_33 |  | 24 | 25 | 0.031749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5938-33_0_6_line_34 |  | 24 | 26 | 0.016167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5938-33_0_6_line_35 |  | 25 | 63 | 0.013049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5938-33_0_6_line_36 |  | 26 | 53 | 0.001621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5938-33_0_6_line_37 |  | 26 | 55 | 0.0573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5938-33_0_6_line_38 |  | 27 | 28 | 0.015083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5938-33_0_6_line_39 |  | 27 | 29 | 0.00615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5938-33_0_6_line_40 |  | 27 | 30 | 0.037481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5938-33_0_6_line_41 |  | 28 | 71 | 0.0020148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5938-33_0_6_line_42 |  | 29 | 72 | 0.027886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5938-33_0_6_line_43 |  | 29 | 64 | 0.014968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5938-33_0_6_line_44 |  | 30 | 73 | 0.0050888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5938-33_0_6_line_45 |  | 31 | 32 | 0.008896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5938-33_0_6_line_46 |  | 31 | 33 | 0.041481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5938-33_0_6_line_47 |  | 31 | 34 | 0.01058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5938-33_0_6_line_48 |  | 32 | 44 | 0.0078246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5938-33_0_6_line_49 |  | 33 | 47 | 0.012292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5938-33_0_6_line_50 |  | 33 | 48 | 0.023271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5938-33_0_6_line_51 |  | 34 | 75 | 0.0069393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5938-33_0_6_line_52 |  | 35 | 36 | 0.008563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5938-33_0_6_line_53 |  | 35 | 37 | 0.0063188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5938-33_0_6_line_54 |  | 36 | 83 | 0.01404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5938-33_0_6_line_55 |  | 37 | 46 | 0.015556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5938-33_0_6_line_56 |  | 38 | 39 | 0.008464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5938-33_0_6_line_57 |  | 38 | 40 | 0.027017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_5938-33_0_6_line_58 |  | 38 | 41 | 0.004514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_5938-33_0_6_line_59 |  | 40 | 45 | 0.0054401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_5938-33_0_6_line_60 |  | 41 | 49 | 0.026372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_5938-33_0_6_line_61 |  | 42 | 43 | 0.010238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5938-33_0_6_line_62 |  | 42 | 44 | 0.011997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5938-33_0_6_line_63 |  | 43 | 79 | 0.0062075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5938-33_0_6_line_64 |  | 45 | 77 | 0.027008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_5938-33_0_6_line_65 |  | 46 | 82 | 0.003401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5938-33_0_6_line_66 |  | 47 | 70 | 0.023373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_5938-33_0_6_line_67 |  | 48 | 52 | 0.011163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5938-33_0_6_line_68 |  | 49 | 68 | 0.011123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_5938-33_0_6_line_69 |  | 50 | 51 | 0.040385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5938-33_0_6_line_70 |  | 50 | 52 | 0.01241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5938-33_0_6_line_71 |  | 51 | 80 | 0.013649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5938-33_0_6_line_72 |  | 51 | 81 | 0.013728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5938-33_0_6_line_73 |  | 53 | 54 | 0.035909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5938-33_0_6_line_74 |  | 56 | 62 | 0.011256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_5938-33_0_6_line_75 |  | 57 | 66 | 0.00014176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5938-33_0_6_line_76 |  | 58 | 67 | 0.017697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_5938-33_0_6_line_77 |  | 59 | 65 | 0.010474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5938-33_0_6_line_78 |  | 61 | 91 | 0.019674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5938-33_0_6_line_79 |  | 62 | 93 | 0.011132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5938-33_0_6_line_80 |  | 63 | 161 | 0.019066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5938-33_0_6_line_81 |  | 67 | 69 | 0.01925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_5938-33_0_6_line_82 |  | 67 | 94 | 0.046197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5938-33_0_6_line_83 |  | 73 | 134 | 0.007495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5938-33_0_6_line_84 |  | 75 | 126 | 0.0026659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_5938-33_0_6_line_85 |  | 76 | 77 | 0.005009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5938-33_0_6_line_86 |  | 76 | 78 | 0.021248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_5938-33_0_6_line_87 |  | 77 | 101 | 0.026192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_5938-33_0_6_line_88 |  | 78 | 100 | 0.058405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_5938-33_0_6_line_89 |  | 79 | 130 | 0.0061912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5938-33_0_6_line_90 |  | 81 | 125 | 0.014865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5938-33_0_6_line_91 |  | 82 | 125 | 0.023852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5938-33_0_6_line_92 |  | 84 | 85 | 0.0039941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5938-33_0_6_line_93 |  | 84 | 86 | 0.0012908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5938-33_0_6_line_94 |  | 85 | 87 | 0.0056116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5938-33_0_6_line_95 |  | 86 | 88 | 0.0053796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5938-33_0_6_line_96 |  | 87 | 89 | 0.0060787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5938-33_0_6_line_97 |  | 88 | 90 | 0.0056339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5938-33_0_6_line_98 |  | 89 | 91 | 0.0059709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5938-33_0_6_line_99 |  | 90 | 92 | 0.0041473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5938-33_0_6_line_100 |  | 94 | 95 | 0.0056084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5938-33_0_6_line_101 |  | 95 | 96 | 0.0070452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5938-33_0_6_line_102 |  | 96 | 97 | 0.017399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5938-33_0_6_line_103 |  | 97 | 98 | 0.001498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_5938-33_0_6_line_104 |  | 98 | 99 | 0.00099942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_5938-33_0_6_line_105 |  | 101 | 146 | 0.020569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_5938-33_0_6_line_106 |  | 102 | 103 | 0.015624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_5938-33_0_6_line_107 |  | 103 | 145 | 0.01049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_5938-33_0_6_line_108 |  | 103 | 146 | 0.003862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_5938-33_0_6_line_109 |  | 104 | 105 | 0.014773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_5938-33_0_6_line_110 |  | 105 | 106 | 0.012363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_5938-33_0_6_line_111 |  | 105 | 107 | 0.050264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_5938-33_0_6_line_112 |  | 106 | 108 | 0.0028692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_5938-33_0_6_line_113 |  | 107 | 111 | 0.032485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_5938-33_0_6_line_114 |  | 108 | 110 | 0.017799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_5938-33_0_6_line_115 |  | 109 | 110 | 0.012956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_5938-33_0_6_line_116 |  | 111 | 112 | 0.0074668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_5938-33_0_6_line_117 |  | 111 | 113 | 0.005923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_5938-33_0_6_line_118 |  | 112 | 114 | 0.013075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_5938-33_0_6_line_119 |  | 113 | 115 | 0.009434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_5938-33_0_6_line_120 |  | 113 | 116 | 0.017389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_5938-33_0_6_line_121 |  | 115 | 117 | 0.015117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_5938-33_0_6_line_122 |  | 115 | 118 | 0.024573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_5938-33_0_6_line_123 |  | 118 | 120 | 0.007494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_5938-33_0_6_line_124 |  | 118 | 119 | 0.011204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_5938-33_0_6_line_125 |  | 120 | 121 | 0.017915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_5938-33_0_6_line_126 |  | 120 | 122 | 0.020281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_5938-33_0_6_line_127 |  | 121 | 123 | 0.020159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_5938-33_0_6_line_128 |  | 121 | 124 | 0.013617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
129 | LV_5938-33_0_6_line_129 |  | 124 | 136 | 0.022597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_5938-33_0_6_line_130 |  | 124 | 134 | 0.019812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_5938-33_0_6_line_131 |  | 126 | 127 | 0.0032973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_5938-33_0_6_line_132 |  | 127 | 128 | 0.0064278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_5938-33_0_6_line_133 |  | 128 | 129 | 0.0043642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_5938-33_0_6_line_134 |  | 130 | 131 | 0.0062692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_5938-33_0_6_line_135 |  | 131 | 132 | 0.00084759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_5938-33_0_6_line_136 |  | 133 | 134 | 0.004261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_5938-33_0_6_line_137 |  | 134 | 135 | 0.008835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
138 | LV_5938-33_0_6_line_138 |  | 135 | 137 | 0.021964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_5938-33_0_6_line_139 |  | 135 | 138 | 0.0078521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
140 | LV_5938-33_0_6_line_140 |  | 137 | 139 | 0.0053767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_5938-33_0_6_line_141 |  | 138 | 142 | 0.038854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
142 | LV_5938-33_0_6_line_142 |  | 139 | 156 | 0.026998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_5938-33_0_6_line_143 |  | 140 | 141 | 0.017125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_5938-33_0_6_line_144 |  | 140 | 142 | 0.021568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
145 | LV_5938-33_0_6_line_145 |  | 140 | 143 | 0.002773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
146 | LV_5938-33_0_6_line_146 |  | 141 | 155 | 0.014509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_5938-33_0_6_line_147 |  | 142 | 144 | 0.013315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_5938-33_0_6_line_148 |  | 143 | 149 | 0.070611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_5938-33_0_6_line_149 |  | 143 | 146 | 0.006665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
150 | LV_5938-33_0_6_line_150 |  | 145 | 147 | 0.0079748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_5938-33_0_6_line_151 |  | 146 | 148 | 0.041329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_5938-33_0_6_line_152 |  | 147 | 150 | 0.00041787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_5938-33_0_6_line_153 |  | 148 | 151 | 0.029358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_5938-33_0_6_line_154 |  | 149 | 152 | 0.022789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_5938-33_0_6_line_155 |  | 150 | 153 | 0.0064549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_5938-33_0_6_line_156 |  | 152 | 159 | 0.00010861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_5938-33_0_6_line_157 |  | 153 | 154 | 0.0067575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_5938-33_0_6_line_158 |  | 155 | 160 | 0.0042149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_5938-33_0_6_line_159 |  | 156 | 157 | 0.016386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_5938-33_0_6_line_160 |  | 157 | 158 | 0.020599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5938-33_0_6_trafo_60 | 0.63 MVA 20/0.4 kV | 162 | 106 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2538955.927 | 1180599.2046 | 2538975.9338 | 1180582.7423
1 | 2538955.927 | 1180599.2046 | 2538940.1809 | 1180612.1611
2 | 2538975.9338 | 1180582.7423 | 2538983.8099 | 1180576.2615
3 | 2538937.2715 | 1180614.555 | 2538940.1809 | 1180612.1611
4 | 2538999.2313 | 1180563.5722 | 2538983.8099 | 1180576.2615
5 | 2538937.2715 | 1180614.555 | 2538945.7473 | 1180624.7344
6 | 2538999.2313 | 1180563.5722 | 2539003.1419 | 1180560.3526
7 | 2538999.2313 | 1180563.5722 | 2539005.5488 | 1180573.0263
8 | 2538945.7473 | 1180624.7344 | 2538952.9306 | 1180633.3614 | 2538954.3421 | 1180634.7033 | 2538956.0266 | 1180635.1086 | 2538958.13 | 1180635.3984 | 2538974.366 | 1180635.1437 | 2538975.6533 | 1180635.542 | 2538976.9006 | 1180636.5187 | 2538977.3587 | 1180637.0304
9 | 2539014.496 | 1180551.9434 | 2539012.6357 | 1180553.0297 | 2539005.6848 | 1180558.259 | 2539003.1419 | 1180560.3526
10 | 2539009.6777 | 1180460.6968 | 2539011.5218 | 1180463.2683 | 2539013.4051 | 1180462.1819 | 2539016.6638 | 1180461.1592 | 2539018.4236 | 1180461.4525 | 2539020.3047 | 1180462.4006 | 2539021.6163 | 1180463.6879 | 2539023.7556 | 1180467.4905 | 2539027.5671 | 1180476.4789 | 2539029.6199 | 1180481.8773
11 | 2539009.6777 | 1180460.6968 | 2538986.9495 | 1180481.2463
12 | 2539036.5889 | 1180505.0475 | 2539031.256 | 1180486.1801 | 2539029.6199 | 1180481.8773
13 | 2538986.9495 | 1180481.2463 | 2538966.7374 | 1180499.5208
14 | 2539065.5696 | 1180637.1155 | 2539065.67 | 1180636.4696 | 2539066.0279 | 1180634.1091 | 2539066.3203 | 1180631.3268 | 2539064.2558 | 1180628.1127 | 2539059.2309 | 1180622.205 | 2539073.2733 | 1180609.8106 | 2539069.8774 | 1180598.1164 | 2539072.6951 | 1180597.2872 | 2539074.6169 | 1180595.5 | 2539074.978 | 1180593.4507 | 2539075.4882 | 1180591.0553 | 2539075.5465 | 1180590.7767
15 | 2539075.5465 | 1180590.7767 | 2539070.7549 | 1180588.2797 | 2539067.5424 | 1180584.0989 | 2539066.219 | 1180579.366
16 | 2539075.5465 | 1180590.7767 | 2539075.4882 | 1180591.0553 | 2539074.978 | 1180593.4507 | 2539074.6169 | 1180595.5 | 2539076.1319 | 1180598.753 | 2539080.2267 | 1180602.5802 | 2539085.6072 | 1180607.3948 | 2539086.5399 | 1180608.2302 | 2539087.9238 | 1180605.3701 | 2539089.2944 | 1180603.455 | 2539091.6344 | 1180600.7186 | 2539100.0487 | 1180592.1837 | 2539140.2321 | 1180550.8072 | 2539141.2847 | 1180551.419 | 2539150.7044 | 1180558.3494
17 | 2539075.5465 | 1180590.7767 | 2539075.4882 | 1180591.0553 | 2539074.978 | 1180593.4507 | 2539084.8311 | 1180593.4393 | 2539094.6212 | 1180587.2473
18 | 2539065.5696 | 1180637.1155 | 2539068.9619 | 1180637.9592 | 2539069.9875 | 1180638.4461
19 | 2539066.219 | 1180579.366 | 2539061.1964 | 1180561.4043
20 | 2539150.7044 | 1180558.3494 | 2539171.1348 | 1180523.6009
21 | 2539094.6212 | 1180587.2473 | 2539105.8049 | 1180575.827
22 | 2539036.5889 | 1180505.0475 | 2539040.9041 | 1180504.2587 | 2539045.825 | 1180502.9411
23 | 2539042.4516 | 1180539.9296 | 2539041.8862 | 1180537.6675 | 2539042.7391 | 1180535.9133 | 2539042.2245 | 1180530.3932 | 2539036.5889 | 1180505.0475
24 | 2539045.825 | 1180502.9411 | 2539043.1332 | 1180492.2514
25 | 2539045.825 | 1180502.9411 | 2539046.5372 | 1180506.1246
26 | 2539042.4516 | 1180539.9296 | 2539037.5371 | 1180541.1248 | 2539024.2769 | 1180546.3873
27 | 2539048.6354 | 1180561.3565 | 2539043.9081 | 1180545.6958 | 2539042.4516 | 1180539.9296
28 | 2539048.6354 | 1180561.3565 | 2539029.0944 | 1180578.6986
29 | 2539027.637 | 1180579.992 | 2539029.0944 | 1180578.6986
30 | 2539043.1332 | 1180492.2514 | 2539040.3068 | 1180481.0272
31 | 2539046.5372 | 1180506.1246 | 2539054.8408 | 1180503.9466
32 | 2539046.5372 | 1180506.1246 | 2539047.1578 | 1180508.5529 | 2539051.6091 | 1180525.7265
33 | 2539212.3888 | 1180464.2585 | 2539224.6382 | 1180482.8112 | 2539230.2795 | 1180490.4761
34 | 2539200.6074 | 1180474.4617 | 2539205.2361 | 1180467.6887 | 2539208.7654 | 1180465.4738 | 2539212.3888 | 1180464.2585
35 | 2539238.0142 | 1180500.9856 | 2539230.2795 | 1180490.4761
36 | 2539201.4009 | 1180475.8767 | 2539200.6074 | 1180474.4617
37 | 2539200.6074 | 1180474.4617 | 2539178.5019 | 1180511.2403 | 2539173.2593 | 1180519.9874 | 2539171.1348 | 1180523.6009
38 | 2539171.9274 | 1180255.3301 | 2539183.8463 | 1180264.6142
39 | 2539183.8463 | 1180264.6142 | 2539188.7575 | 1180268.333
40 | 2539183.8463 | 1180264.6142 | 2539162.0838 | 1180295.1306
41 | 2539171.9274 | 1180255.3301 | 2539170.3364 | 1180254.094
42 | 2539211.0122 | 1180285.2164 | 2539188.7575 | 1180268.333
43 | 2539188.7575 | 1180268.333 | 2539190.8217 | 1180265.4993 | 2539197.7258 | 1180256.3503
44 | 2539159.1291 | 1180299.2737 | 2539162.0838 | 1180295.1306
45 | 2538953.1453 | 1180551.8689 | 2538953.2625 | 1180552.8794 | 2538952.3752 | 1180554.2559 | 2538950.3898 | 1180557.3001 | 2538949.0835 | 1180559.5558
46 | 2538940.2825 | 1180523.4397 | 2538931.617 | 1180532.0441 | 2538936.428 | 1180536.4308 | 2538945.4834 | 1180545.0655 | 2538953.1453 | 1180551.8689
47 | 2538953.1453 | 1180551.8689 | 2538954.3192 | 1180552.3906 | 2538955.5947 | 1180552.3776 | 2538957.0726 | 1180551.9956 | 2538958.8745 | 1180551.1768 | 2538960.4998 | 1180549.5259 | 2538961.9186 | 1180547.8479
48 | 2538949.0835 | 1180559.5558 | 2538947.4625 | 1180562.355 | 2538945.6337 | 1180565.0196 | 2538944.7509 | 1180566.0517
49 | 2538940.2825 | 1180523.4397 | 2538949.4005 | 1180515.1959
50 | 2538923.9053 | 1180506.8976 | 2538936.8185 | 1180519.3172 | 2538940.2825 | 1180523.4397
51 | 2538966.1074 | 1180542.3182 | 2538962.7564 | 1180546.857 | 2538961.9186 | 1180547.8479
52 | 2538992.1692 | 1180408.1346 | 2538986.888 | 1180401.3942
53 | 2538992.1692 | 1180408.1346 | 2538988.523 | 1180411.6071 | 2538987.5461 | 1180412.4397
54 | 2538986.888 | 1180401.3942 | 2538978.229 | 1180390.3428
55 | 2538987.5461 | 1180412.4397 | 2538976.374 | 1180423.264
56 | 2539046.8543 | 1180447.2994 | 2539041.176 | 1180441.0093
57 | 2539053.5545 | 1180421.1943 | 2539056.5274 | 1180425.0995 | 2539041.176 | 1180441.0093
58 | 2539041.176 | 1180441.0093 | 2539040.337 | 1180441.8738 | 2539038.6705 | 1180444.7369
59 | 2539053.5545 | 1180421.1943 | 2539057.3256 | 1180417.2734
60 | 2539038.6705 | 1180444.7369 | 2539037.0667 | 1180447.766 | 2539035.9879 | 1180451.3346 | 2539035.2004 | 1180457.257 | 2539035.6833 | 1180462.6663 | 2539037.5907 | 1180470.2408
61 | 2538934.4249 | 1180569.1585 | 2538934.6522 | 1180570.4792 | 2538934.0765 | 1180571.6969 | 2538931.8626 | 1180573.3092 | 2538928.0197 | 1180576.2056 | 2538928.0197 | 1180576.2056
62 | 2538934.4249 | 1180569.1585 | 2538935.9162 | 1180570.0883 | 2538937.3543 | 1180570.2959 | 2538939.4191 | 1180569.7968 | 2538941.4278 | 1180569.0315 | 2538943.1201 | 1180567.958 | 2538944.7509 | 1180566.0517
63 | 2538928.0197 | 1180576.2056 | 2538925.606 | 1180579.1986 | 2538924.0883 | 1180581.0092
64 | 2539076.048 | 1180397.8076 | 2539057.3256 | 1180417.2734
65 | 2538976.374 | 1180423.264 | 2538973.9314 | 1180425.6305
66 | 2538966.7374 | 1180499.5208 | 2538949.4005 | 1180515.1959
67 | 2538923.9053 | 1180506.8976 | 2538915.8588 | 1180499.1605
68 | 2539040.3068 | 1180481.0272 | 2539037.5907 | 1180470.2408
69 | 2538936.2652 | 1180462.124 | 2538907.2138 | 1180490.2586
70 | 2538907.2138 | 1180490.2586 | 2538911.0969 | 1180494.2767 | 2538915.119 | 1180498.4491 | 2538915.8588 | 1180499.1605
71 | 2538936.2652 | 1180462.124 | 2538945.8757 | 1180471.8153
72 | 2538936.2652 | 1180462.124 | 2538946.1246 | 1180452.5716
73 | 2539194.2272 | 1180511.0582 | 2539201.4009 | 1180475.8767
74 | 2539014.496 | 1180551.9434 | 2539023.5927 | 1180546.6589 | 2539024.2769 | 1180546.3873
75 | 2539054.8408 | 1180503.9466 | 2539054.9779 | 1180503.9107
76 | 2539055.9936 | 1180542.8711 | 2539055.2279 | 1180539.6883 | 2539051.6091 | 1180525.7265
77 | 2539113.1333 | 1180568.3437 | 2539105.8049 | 1180575.827
78 | 2538977.3587 | 1180637.0304 | 2538978.5772 | 1180638.3915 | 2538981.1792 | 1180641.1332 | 2538982.5543 | 1180641.9085 | 2538984.052 | 1180641.971 | 2538985.4612 | 1180641.5898 | 2538986.9277 | 1180640.8411 | 2538992.9943 | 1180635.8075
79 | 2539014.496 | 1180551.9434 | 2539021.504 | 1180560.593
80 | 2539254.1104 | 1180490.6941 | 2539238.0142 | 1180500.9856
81 | 2539055.9936 | 1180542.8711 | 2539056.8013 | 1180545.6867 | 2539061.1964 | 1180561.4043
82 | 2539055.9936 | 1180542.8711 | 2539060.0793 | 1180542.0513 | 2539073.073 | 1180538.4169 | 2539077.1648 | 1180538.1863 | 2539080.5764 | 1180537.9292 | 2539083.7517 | 1180536.963 | 2539086.863 | 1180535.7084 | 2539089.9483 | 1180534.1539 | 2539092.8181 | 1180532.4459 | 2539096.8887 | 1180529.3917 | 2539098.7225 | 1180527.751
83 | 2539159.1291 | 1180299.2737 | 2539164.4157 | 1180304.6008
84 | 2538966.1074 | 1180542.3182 | 2538966.7344 | 1180541.4689 | 2538967.7511 | 1180540.2202
85 | 2539076.048 | 1180397.8076 | 2539079.2496 | 1180401.6661
86 | 2539079.2496 | 1180401.6661 | 2539092.5225 | 1180417.9068 | 2539092.6891 | 1180418.1234
87 | 2539076.048 | 1180397.8076 | 2539094.4437 | 1180379.1632
88 | 2539092.6891 | 1180418.1234 | 2539115.0404 | 1180447.1719 | 2539116.586 | 1180448.9349 | 2539118.2785 | 1180450.1184 | 2539120.1708 | 1180450.6772 | 2539121.8544 | 1180450.2376 | 2539123.6202 | 1180448.8633 | 2539130.0806 | 1180443.4501 | 2539132.2027 | 1180441.3809
89 | 2538924.0883 | 1180581.0092 | 2538920.1111 | 1180585.754
90 | 2538956.801 | 1180442.2276 | 2538946.1246 | 1180452.5716
91 | 2538956.801 | 1180442.2276 | 2538973.9314 | 1180425.6305
92 | 2539006.5862 | 1180624.5303 | 2539009.6601 | 1180621.9799
93 | 2539010.6534 | 1180621.1557 | 2539009.6601 | 1180621.9799
94 | 2539002.2676 | 1180628.1135 | 2539006.5862 | 1180624.5303
95 | 2539010.6534 | 1180621.1557 | 2539014.7936 | 1180617.7206
96 | 2539002.2676 | 1180628.1135 | 2538997.5895 | 1180631.9949
97 | 2539014.7936 | 1180617.7206 | 2539019.1294 | 1180614.1231
98 | 2538992.9943 | 1180635.8075 | 2538997.5895 | 1180631.9949
99 | 2539022.3211 | 1180611.4749 | 2539019.1294 | 1180614.1231
100 | 2539102.7479 | 1180523.853 | 2539100.961 | 1180525.7482 | 2539098.7225 | 1180527.751
101 | 2539102.7479 | 1180523.853 | 2539107.5811 | 1180518.7271
102 | 2539107.5811 | 1180518.7271 | 2539114.4345 | 1180511.4586 | 2539119.5095 | 1180506.0606
103 | 2539120.5356 | 1180504.9692 | 2539119.5095 | 1180506.0606
104 | 2539120.5356 | 1180504.9692 | 2539121.2202 | 1180504.2411
105 | 2539108.8903 | 1180364.5214 | 2539094.4437 | 1180379.1632
106 | 2539111.1981 | 1180367.6218 | 2539107.9881 | 1180371.1898 | 2539100.5782 | 1180379.0811
107 | 2539111.1981 | 1180367.6218 | 2539113.0102 | 1180370.0492 | 2539117.7829 | 1180375.7834
108 | 2539108.8903 | 1180364.5214 | 2539111.1981 | 1180367.6218
109 | 2539136.6861 | 1180468.0634 | 2539139.1892 | 1180466.337 | 2539140.5588 | 1180465.8117 | 2539142.2423 | 1180466.1169 | 2539143.3123 | 1180466.9287 | 2539148.5061 | 1180471.9315
110 | 2539136.6861 | 1180468.0634 | 2539132.4973 | 1180472.264 | 2539129.2599 | 1180476.1435 | 2539128.9298 | 1180477.4809
111 | 2539136.6861 | 1180468.0634 | 2539135.5833 | 1180466.2736 | 2539135.1022 | 1180464.0328 | 2539135.2102 | 1180461.8861 | 2539135.7923 | 1180459.7901 | 2539137.4308 | 1180457.172 | 2539163.3951 | 1180428.8031
112 | 2539128.9298 | 1180477.4809 | 2539129.1801 | 1180478.8125 | 2539129.613 | 1180480.0643 | 2539129.7339 | 1180480.2105
113 | 2539169.8191 | 1180397.2757 | 2539168.9634 | 1180401.0087 | 2539167.7045 | 1180406.4023 | 2539166.5297 | 1180420.8223 | 2539165.3164 | 1180425.4484 | 2539163.3951 | 1180428.8031
114 | 2539129.7339 | 1180480.2105 | 2539130.7807 | 1180481.4755 | 2539136.6459 | 1180487.3747 | 2539138.1024 | 1180487.8935 | 2539140.0428 | 1180487.9182 | 2539142.0872 | 1180486.908 | 2539143.5622 | 1180485.4538
115 | 2539151.3216 | 1180475.6223 | 2539151.3369 | 1180477.1195 | 2539150.5647 | 1180478.5504 | 2539143.5622 | 1180485.4538
116 | 2539169.8191 | 1180397.2757 | 2539165.4649 | 1180391.2098
117 | 2539171.143 | 1180391.5034 | 2539169.8191 | 1180397.2757
118 | 2539157.8404 | 1180380.5881 | 2539165.4649 | 1180391.2098
119 | 2539171.143 | 1180391.5034 | 2539171.2893 | 1180390.8682 | 2539173.5173 | 1180382.3742
120 | 2539184.3808 | 1180402.8197 | 2539171.143 | 1180391.5034
121 | 2539188.341 | 1180384.3802 | 2539184.8407 | 1180384.9494 | 2539173.5173 | 1180382.3742
122 | 2539173.5173 | 1180382.3742 | 2539174.5174 | 1180378.5619 | 2539177.7722 | 1180359.8627 | 2539177.977 | 1180358.2264
123 | 2539178.8944 | 1180350.7907 | 2539177.977 | 1180358.2264
124 | 2539177.977 | 1180358.2264 | 2539166.8584 | 1180356.8491
125 | 2539178.8944 | 1180350.7907 | 2539180.144 | 1180340.7167 | 2539180.1873 | 1180332.9564
126 | 2539198.9923 | 1180353.9104 | 2539178.8944 | 1180350.7907
127 | 2539200.2512 | 1180330.4733 | 2539180.1873 | 1180332.9564
128 | 2539176.7101 | 1180320.0178 | 2539179.0974 | 1180324.9296 | 2539180.1484 | 1180329.1324 | 2539180.1873 | 1180332.9564
129 | 2539196.3252 | 1180308.701 | 2539176.7101 | 1180320.0178
130 | 2539176.7101 | 1180320.0178 | 2539175.3837 | 1180317.2853 | 2539169.1698 | 1180309.3996 | 2539164.4157 | 1180304.6008
131 | 2538969.8329 | 1180537.6632 | 2538967.7511 | 1180540.2202
132 | 2538973.8913 | 1180532.6787 | 2538969.8329 | 1180537.6632
133 | 2538976.6468 | 1180529.2943 | 2538973.8913 | 1180532.6787
134 | 2538920.1111 | 1180585.754 | 2538916.0838 | 1180590.5586
135 | 2538915.5394 | 1180591.2081 | 2538916.0838 | 1180590.5586
136 | 2539164.4157 | 1180304.6008 | 2539166.932 | 1180301.1622 | 2539166.932 | 1180301.1622
137 | 2539164.4157 | 1180304.6008 | 2539162.4117 | 1180307.3338 | 2539160.6146 | 1180307.1408 | 2539158.4291 | 1180307.7968 | 2539157.5769 | 1180308.8727
138 | 2539138.1146 | 1180306.6805 | 2539148.5672 | 1180306.2406 | 2539152.1499 | 1180304.014 | 2539154.2621 | 1180305.9047 | 2539157.5769 | 1180308.8727
139 | 2539157.5769 | 1180308.8727 | 2539155.1558 | 1180311.9101 | 2539152.7089 | 1180315.0337
140 | 2539138.1146 | 1180306.6805 | 2539134.8707 | 1180302.3925
141 | 2539128.7488 | 1180345.6198 | 2539152.7089 | 1180315.0337
142 | 2539134.8707 | 1180302.3925 | 2539118.5825 | 1180280.8613
143 | 2539114.7114 | 1180357.0802 | 2539109.435 | 1180348.996 | 2539105.1591 | 1180342.8689
144 | 2539114.7114 | 1180357.0802 | 2539125.5394 | 1180343.24 | 2539128.7488 | 1180345.6198
145 | 2539114.7114 | 1180357.0802 | 2539112.9998 | 1180359.2655
146 | 2539105.1591 | 1180342.8689 | 2539096.8556 | 1180330.9707
147 | 2539128.7488 | 1180345.6198 | 2539136.638 | 1180351.4873 | 2539139.1804 | 1180353.8682
148 | 2539112.9998 | 1180359.2655 | 2539109.814 | 1180356.2073 | 2539106.5309 | 1180354.851 | 2539100.8302 | 1180350.8624 | 2539065.4993 | 1180307.8206
149 | 2539108.8903 | 1180364.5214 | 2539112.9998 | 1180359.2655
150 | 2539117.7829 | 1180375.7834 | 2539120.7819 | 1180379.3865 | 2539122.7661 | 1180382.007
151 | 2539108.8903 | 1180364.5214 | 2539100.8605 | 1180356.8432 | 2539082.3563 | 1180332.9524
152 | 2539123.0183 | 1180382.3401 | 2539122.7661 | 1180382.007
153 | 2539064.3791 | 1180309.7421 | 2539082.3563 | 1180332.9524
154 | 2539051.3688 | 1180289.9477 | 2539057.2543 | 1180297.7761 | 2539065.4993 | 1180307.8206
155 | 2539123.0183 | 1180382.3401 | 2539126.9149 | 1180387.4863
156 | 2539051.3688 | 1180289.9477 | 2539051.3035 | 1180289.8609
157 | 2539126.9149 | 1180387.4863 | 2539130.9941 | 1180392.8737
158 | 2539094.4435 | 1180327.5142 | 2539096.8556 | 1180330.9707
159 | 2539108.8213 | 1180267.701 | 2539115.4052 | 1180276.6613 | 2539118.5825 | 1180280.8613
160 | 2539093.6417 | 1180281.0296 | 2539100.3613 | 1180277.8039 | 2539108.8213 | 1180267.701

## bus_geodata
| x | y | coords
0 | 2538955.927 | 1180599.2046
1 | 2538975.9338 | 1180582.7423
2 | 2538940.1809 | 1180612.1611
3 | 2538983.8099 | 1180576.2615
4 | 2538937.2715 | 1180614.555
5 | 2538999.2313 | 1180563.5722
6 | 2538945.7473 | 1180624.7344
7 | 2539003.1419 | 1180560.3526
8 | 2539005.5488 | 1180573.0263
9 | 2539009.6777 | 1180460.6968
10 | 2539029.6199 | 1180481.8773
11 | 2538986.9495 | 1180481.2463
12 | 2539075.5465 | 1180590.7767
13 | 2539065.5696 | 1180637.1155
14 | 2539066.219 | 1180579.366
15 | 2539150.7044 | 1180558.3494
16 | 2539094.6212 | 1180587.2473
17 | 2539036.5889 | 1180505.0475
18 | 2539045.825 | 1180502.9411
19 | 2539042.4516 | 1180539.9296
20 | 2539048.6354 | 1180561.3565
21 | 2539029.0944 | 1180578.6986
22 | 2539043.1332 | 1180492.2514
23 | 2539046.5372 | 1180506.1246
24 | 2539212.3888 | 1180464.2585
25 | 2539230.2795 | 1180490.4761
26 | 2539200.6074 | 1180474.4617
27 | 2539183.8463 | 1180264.6142
28 | 2539171.9274 | 1180255.3301
29 | 2539188.7575 | 1180268.333
30 | 2539162.0838 | 1180295.1306
31 | 2538953.1453 | 1180551.8689
32 | 2538949.0835 | 1180559.5558
33 | 2538940.2825 | 1180523.4397
34 | 2538961.9186 | 1180547.8479
35 | 2538992.1692 | 1180408.1346
36 | 2538986.888 | 1180401.3942
37 | 2538987.5461 | 1180412.4397
38 | 2539041.1761 | 1180441.0093
39 | 2539046.8543 | 1180447.2994
40 | 2539053.5545 | 1180421.1943
41 | 2539038.6705 | 1180444.7369
42 | 2538934.4249 | 1180569.1585
43 | 2538928.0197 | 1180576.2056
44 | 2538944.7509 | 1180566.0517
45 | 2539057.3256 | 1180417.2734
46 | 2538976.374 | 1180423.264
47 | 2538949.4005 | 1180515.1959
48 | 2538923.9053 | 1180506.8976
49 | 2539037.5907 | 1180470.2408
50 | 2538907.2138 | 1180490.2586
51 | 2538936.2652 | 1180462.124
52 | 2538915.8588 | 1180499.1605
53 | 2539201.4009 | 1180475.8767
54 | 2539194.2272 | 1180511.0582
55 | 2539171.1348 | 1180523.6009
56 | 2539024.2769 | 1180546.3873
57 | 2539054.8408 | 1180503.9466
58 | 2539051.6091 | 1180525.7265
59 | 2539105.8049 | 1180575.827
60 | 2539069.9875 | 1180638.4461
61 | 2538977.3587 | 1180637.0304
62 | 2539014.496 | 1180551.9434
63 | 2539238.0142 | 1180500.9856
64 | 2539197.7258 | 1180256.3503
65 | 2539113.1333 | 1180568.3437
66 | 2539054.9779 | 1180503.9107
67 | 2539055.9936 | 1180542.8711
68 | 2539040.3068 | 1180481.0272
69 | 2539061.1964 | 1180561.4043
70 | 2538966.7374 | 1180499.5208
71 | 2539170.3364 | 1180254.094
72 | 2539211.0122 | 1180285.2164
73 | 2539159.1291 | 1180299.2738
74 | 2539027.637 | 1180579.992
75 | 2538966.1074 | 1180542.3182
76 | 2539079.2496 | 1180401.6661
77 | 2539076.048 | 1180397.8076
78 | 2539092.6891 | 1180418.1234
79 | 2538924.0883 | 1180581.0092
80 | 2538945.8757 | 1180471.8153
81 | 2538946.1246 | 1180452.5716
82 | 2538973.9314 | 1180425.6305
83 | 2538978.229 | 1180390.3428
84 | 2539009.6601 | 1180621.9799
85 | 2539006.5862 | 1180624.5303
86 | 2539010.6534 | 1180621.1557
87 | 2539002.2676 | 1180628.1135
88 | 2539014.7936 | 1180617.7206
89 | 2538997.5895 | 1180631.9949
90 | 2539019.1294 | 1180614.1231
91 | 2538992.9943 | 1180635.8075
92 | 2539022.3211 | 1180611.4749
93 | 2539021.504 | 1180560.593
94 | 2539098.7225 | 1180527.751
95 | 2539102.7479 | 1180523.853
96 | 2539107.5811 | 1180518.7271
97 | 2539119.5095 | 1180506.0606
98 | 2539120.5356 | 1180504.9692
99 | 2539121.2202 | 1180504.2411
100 | 2539132.2027 | 1180441.3809
101 | 2539094.4437 | 1180379.1632
102 | 2539100.5782 | 1180379.0811
103 | 2539111.1981 | 1180367.6218
104 | 2539148.5061 | 1180471.9315
105 | 2539136.6861 | 1180468.0634
106 | 2539128.9298 | 1180477.4809
107 | 2539163.3951 | 1180428.8031
108 | 2539129.7339 | 1180480.2105
109 | 2539151.3216 | 1180475.6223
110 | 2539143.5622 | 1180485.4538
111 | 2539169.8191 | 1180397.2757
112 | 2539165.4649 | 1180391.2098
113 | 2539171.143 | 1180391.5034
114 | 2539157.8404 | 1180380.5881
115 | 2539173.5173 | 1180382.3742
116 | 2539184.3808 | 1180402.8197
117 | 2539188.341 | 1180384.3802
118 | 2539177.977 | 1180358.2264
119 | 2539166.8584 | 1180356.8491
120 | 2539178.8944 | 1180350.7907
121 | 2539180.1873 | 1180332.9564
122 | 2539198.9923 | 1180353.9104
123 | 2539200.2512 | 1180330.4733
124 | 2539176.7101 | 1180320.0178
125 | 2538956.801 | 1180442.2276
126 | 2538967.7511 | 1180540.2202
127 | 2538969.8329 | 1180537.6632
128 | 2538973.8913 | 1180532.6787
129 | 2538976.6468 | 1180529.2943
130 | 2538920.1111 | 1180585.754
131 | 2538916.0838 | 1180590.5586
132 | 2538915.5394 | 1180591.2081
133 | 2539166.932 | 1180301.1622
134 | 2539164.4157 | 1180304.6008
135 | 2539157.5769 | 1180308.8727
136 | 2539196.3252 | 1180308.701
137 | 2539138.1146 | 1180306.6805
138 | 2539152.7089 | 1180315.0337
139 | 2539134.8707 | 1180302.3925
140 | 2539114.7114 | 1180357.0802
141 | 2539105.1591 | 1180342.8689
142 | 2539128.7488 | 1180345.6198
143 | 2539112.9998 | 1180359.2655
144 | 2539139.1804 | 1180353.8682
145 | 2539117.7829 | 1180375.7834
146 | 2539108.8903 | 1180364.5214
147 | 2539122.7661 | 1180382.007
148 | 2539082.3563 | 1180332.9524
149 | 2539065.4993 | 1180307.8206
150 | 2539123.0183 | 1180382.3401
151 | 2539064.3791 | 1180309.7421
152 | 2539051.3688 | 1180289.9477
153 | 2539126.9149 | 1180387.4863
154 | 2539130.9941 | 1180392.8737
155 | 2539096.8556 | 1180330.9707
156 | 2539118.5825 | 1180280.8613
157 | 2539108.8213 | 1180267.701
158 | 2539093.6417 | 1180281.0296
159 | 2539051.3035 | 1180289.8609
160 | 2539094.4435 | 1180327.5142
161 | 2539254.1104 | 1180490.6941
162 | 2539136.6861 | 1180468.0634

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1