## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_616-23_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_616-23_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_616-23_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_616-23_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_616-23_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_616-23_0_6_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_616-23_0_6_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_616-23_0_6_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_616-23_0_6_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_616-23_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_616-23_0_6_node_134 | 0.4 | n |  | TRUE
11 | bus_LV_616-23_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_616-23_0_6_node_112 | 0.4 | n |  | TRUE
13 | bus_LV_616-23_0_6_node_143 | 0.4 | n |  | TRUE
14 | bus_LV_616-23_0_6_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_616-23_0_6_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_616-23_0_6_node_81 | 0.4 | n |  | TRUE
17 | bus_LV_616-23_0_6_node_142 | 0.4 | n |  | TRUE
18 | bus_LV_616-23_0_6_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_616-23_0_6_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_616-23_0_6_node_90 | 0.4 | n |  | TRUE
21 | bus_LV_616-23_0_6_node_92 | 0.4 | n |  | TRUE
22 | bus_LV_616-23_0_6_node_91 | 0.4 | n |  | TRUE
23 | bus_LV_616-23_0_6_node_88 | 0.4 | n |  | TRUE
24 | bus_LV_616-23_0_6_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_616-23_0_6_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_616-23_0_6_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_616-23_0_6_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_616-23_0_6_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_616-23_0_6_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_616-23_0_6_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_616-23_0_6_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_616-23_0_6_node_102 | 0.4 | n |  | TRUE
33 | bus_LV_616-23_0_6_node_113 | 0.4 | n |  | TRUE
34 | bus_LV_616-23_0_6_node_103 | 0.4 | n |  | TRUE
35 | bus_LV_616-23_0_6_node_114 | 0.4 | n |  | TRUE
36 | bus_LV_616-23_0_6_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_616-23_0_6_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_616-23_0_6_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_616-23_0_6_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_616-23_0_6_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_616-23_0_6_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_616-23_0_6_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_616-23_0_6_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_616-23_0_6_node_144 | 0.4 | n |  | TRUE
45 | bus_LV_616-23_0_6_node_109 | 0.4 | n |  | TRUE
46 | bus_LV_616-23_0_6_node_110 | 0.4 | n |  | TRUE
47 | bus_LV_616-23_0_6_node_173 | 0.4 | n |  | TRUE
48 | bus_LV_616-23_0_6_node_108 | 0.4 | n |  | TRUE
49 | bus_LV_616-23_0_6_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_616-23_0_6_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_616-23_0_6_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_616-23_0_6_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_616-23_0_6_node_89 | 0.4 | n |  | TRUE
54 | bus_LV_616-23_0_6_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_616-23_0_6_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_616-23_0_6_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_616-23_0_6_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_616-23_0_6_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_616-23_0_6_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_616-23_0_6_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_616-23_0_6_node_82 | 0.4 | n |  | TRUE
62 | bus_LV_616-23_0_6_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_616-23_0_6_node_66 | 0.4 | n |  | TRUE
64 | bus_LV_616-23_0_6_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_616-23_0_6_node_87 | 0.4 | n |  | TRUE
66 | bus_LV_616-23_0_6_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_616-23_0_6_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_616-23_0_6_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_616-23_0_6_node_49 | 0.4 | n |  | TRUE
70 | bus_LV_616-23_0_6_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_616-23_0_6_node_51 | 0.4 | n |  | TRUE
72 | bus_LV_616-23_0_6_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_616-23_0_6_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_616-23_0_6_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_616-23_0_6_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_616-23_0_6_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_616-23_0_6_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_616-23_0_6_node_83 | 0.4 | n |  | TRUE
79 | bus_LV_616-23_0_6_node_84 | 0.4 | n |  | TRUE
80 | bus_LV_616-23_0_6_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_616-23_0_6_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_616-23_0_6_node_59 | 0.4 | n |  | TRUE
83 | bus_LV_616-23_0_6_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_616-23_0_6_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_616-23_0_6_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_616-23_0_6_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_616-23_0_6_node_65 | 0.4 | n |  | TRUE
88 | bus_LV_616-23_0_6_node_67 | 0.4 | n |  | TRUE
89 | bus_LV_616-23_0_6_node_86 | 0.4 | n |  | TRUE
90 | bus_LV_616-23_0_6_node_149 | 0.4 | n |  | TRUE
91 | bus_LV_616-23_0_6_node_148 | 0.4 | n |  | TRUE
92 | bus_LV_616-23_0_6_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_616-23_0_6_node_71 | 0.4 | n |  | TRUE
94 | bus_LV_616-23_0_6_node_72 | 0.4 | n |  | TRUE
95 | bus_LV_616-23_0_6_node_73 | 0.4 | n |  | TRUE
96 | bus_LV_616-23_0_6_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_616-23_0_6_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_616-23_0_6_node_76 | 0.4 | n |  | TRUE
99 | bus_LV_616-23_0_6_node_150 | 0.4 | n |  | TRUE
100 | bus_LV_616-23_0_6_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_616-23_0_6_node_151 | 0.4 | n |  | TRUE
102 | bus_LV_616-23_0_6_node_77 | 0.4 | n |  | TRUE
103 | bus_LV_616-23_0_6_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_616-23_0_6_node_80 | 0.4 | n |  | TRUE
105 | bus_LV_616-23_0_6_node_85 | 0.4 | n |  | TRUE
106 | bus_LV_616-23_0_6_node_96 | 0.4 | n |  | TRUE
107 | bus_LV_616-23_0_6_node_98 | 0.4 | n |  | TRUE
108 | bus_LV_616-23_0_6_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_616-23_0_6_node_95 | 0.4 | n |  | TRUE
110 | bus_LV_616-23_0_6_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_616-23_0_6_node_99 | 0.4 | n |  | TRUE
112 | bus_LV_616-23_0_6_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_616-23_0_6_node_101 | 0.4 | n |  | TRUE
114 | bus_LV_616-23_0_6_node_172 | 0.4 | n |  | TRUE
115 | bus_LV_616-23_0_6_node_145 | 0.4 | n |  | TRUE
116 | bus_LV_616-23_0_6_node_171 | 0.4 | n |  | TRUE
117 | bus_LV_616-23_0_6_node_176 | 0.4 | n |  | TRUE
118 | bus_LV_616-23_0_6_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_616-23_0_6_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_616-23_0_6_node_106 | 0.4 | n |  | TRUE
121 | bus_LV_616-23_0_6_node_107 | 0.4 | n |  | TRUE
122 | bus_LV_616-23_0_6_node_115 | 0.4 | n |  | TRUE
123 | bus_LV_616-23_0_6_node_116 | 0.4 | n |  | TRUE
124 | bus_LV_616-23_0_6_node_129 | 0.4 | n |  | TRUE
125 | bus_LV_616-23_0_6_node_146 | 0.4 | n |  | TRUE
126 | bus_LV_616-23_0_6_node_130 | 0.4 | n |  | TRUE
127 | bus_LV_616-23_0_6_node_147 | 0.4 | n |  | TRUE
128 | bus_LV_616-23_0_6_node_117 | 0.4 | n |  | TRUE
129 | bus_LV_616-23_0_6_node_118 | 0.4 | n |  | TRUE
130 | bus_LV_616-23_0_6_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_616-23_0_6_node_120 | 0.4 | n |  | TRUE
132 | bus_LV_616-23_0_6_node_121 | 0.4 | n |  | TRUE
133 | bus_LV_616-23_0_6_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_616-23_0_6_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_616-23_0_6_node_124 | 0.4 | n |  | TRUE
136 | bus_LV_616-23_0_6_node_125 | 0.4 | n |  | TRUE
137 | bus_LV_616-23_0_6_node_152 | 0.4 | n |  | TRUE
138 | bus_LV_616-23_0_6_node_126 | 0.4 | n |  | TRUE
139 | bus_LV_616-23_0_6_node_133 | 0.4 | n |  | TRUE
140 | bus_LV_616-23_0_6_node_153 | 0.4 | n |  | TRUE
141 | bus_LV_616-23_0_6_node_131 | 0.4 | n |  | TRUE
142 | bus_LV_616-23_0_6_node_127 | 0.4 | n |  | TRUE
143 | bus_LV_616-23_0_6_node_128 | 0.4 | n |  | TRUE
144 | bus_LV_616-23_0_6_node_168 | 0.4 | n |  | TRUE
145 | bus_LV_616-23_0_6_node_167 | 0.4 | n |  | TRUE
146 | bus_LV_616-23_0_6_node_132 | 0.4 | n |  | TRUE
147 | bus_LV_616-23_0_6_node_165 | 0.4 | n |  | TRUE
148 | bus_LV_616-23_0_6_node_160 | 0.4 | n |  | TRUE
149 | bus_LV_616-23_0_6_node_174 | 0.4 | n |  | TRUE
150 | bus_LV_616-23_0_6_node_161 | 0.4 | n |  | TRUE
151 | bus_LV_616-23_0_6_node_159 | 0.4 | n |  | TRUE
152 | bus_LV_616-23_0_6_node_135 | 0.4 | n |  | TRUE
153 | bus_LV_616-23_0_6_node_136 | 0.4 | n |  | TRUE
154 | bus_LV_616-23_0_6_node_137 | 0.4 | n |  | TRUE
155 | bus_LV_616-23_0_6_node_138 | 0.4 | n |  | TRUE
156 | bus_LV_616-23_0_6_node_139 | 0.4 | n |  | TRUE
157 | bus_LV_616-23_0_6_node_140 | 0.4 | n |  | TRUE
158 | bus_LV_616-23_0_6_node_141 | 0.4 | n |  | TRUE
159 | bus_LV_616-23_0_6_node_155 | 0.4 | n |  | TRUE
160 | bus_LV_616-23_0_6_node_154 | 0.4 | n |  | TRUE
161 | bus_LV_616-23_0_6_node_158 | 0.4 | n |  | TRUE
162 | bus_LV_616-23_0_6_node_177 | 0.4 | n |  | TRUE
163 | bus_LV_616-23_0_6_node_162 | 0.4 | n |  | TRUE
164 | bus_LV_616-23_0_6_node_163 | 0.4 | n |  | TRUE
165 | bus_LV_616-23_0_6_node_156 | 0.4 | n |  | TRUE
166 | bus_LV_616-23_0_6_node_157 | 0.4 | n |  | TRUE
167 | bus_LV_616-23_0_6_node_170 | 0.4 | n |  | TRUE
168 | bus_LV_616-23_0_6_node_164 | 0.4 | n |  | TRUE
169 | bus_LV_616-23_0_6_node_166 | 0.4 | n |  | TRUE
170 | bus_LV_616-23_0_6_node_175 | 0.4 | n |  | TRUE
171 | bus_LV_616-23_0_6_node_169 | 0.4 | n |  | TRUE
172 | bus_LV_616-23_0_6_node_178 | 0.4 | n |  | TRUE
173 | bus_MV_98_0_node_87 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_616-23_0_6_load_0 | 0 | 0.0052152 | 0.0013071 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_616-23_0_6_load_1 | 1 | 0.01227 | 0.0030752 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_616-23_0_6_load_6 | 5 | 0.0041207 | 0.0010328 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_616-23_0_6_load_9 | 6 | 0.001629 | 0.00040828 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_616-23_0_6_load_10 | 7 | 0.014701 | 0.0036844 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_616-23_0_6_load_11 | 8 | 0.0053096 | 0.0013307 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_616-23_0_6_load_7 | 9 | 0.0051706 | 0.0012959 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_616-23_0_6_load_134 | 10 | 0.0022124 | 0.00055449 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_616-23_0_6_load_112 | 12 | 0.0087326 | 0.0021886 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_616-23_0_6_load_143 | 13 | 0.0032437 | 0.00081296 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_616-23_0_6_load_35 | 14 | 0.0017478 | 0.00043803 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_616-23_0_6_load_32 | 15 | 0.0035143 | 0.00088076 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_616-23_0_6_load_81 | 16 | 0.0021539 | 0.00053983 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_616-23_0_6_load_142 | 17 | 0.0036524 | 0.00091538 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_616-23_0_6_load_14 | 19 | 0.0030252 | 0.0007582 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_616-23_0_6_load_90 | 20 | 0.0055291 | 0.0013857 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_616-23_0_6_load_92 | 21 | 0.0024841 | 0.00062257 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_616-23_0_6_load_91 | 22 | 0.0096954 | 0.0024299 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_616-23_0_6_load_88 | 23 | 0.0064237 | 0.0016099 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_616-23_0_6_load_15 | 24 | 0.00077974 | 0.00019542 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_616-23_0_6_load_16 | 25 | 0.0048789 | 0.0012228 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_616-23_0_6_load_18 | 27 | 0.0057515 | 0.0014415 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_616-23_0_6_load_19 | 28 | 0.0024963 | 0.00062563 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_616-23_0_6_load_20 | 29 | 0.0024751 | 0.00062033 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_616-23_0_6_load_21 | 30 | 0.0018413 | 0.00046146 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_616-23_0_6_load_22 | 31 | 0.013338 | 0.0033428 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_616-23_0_6_load_102 | 32 | 0.0012899 | 0.00032329 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_616-23_0_6_load_113 | 33 | 0.020728 | 0.005195 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_616-23_0_6_load_103 | 34 | 0.0025096 | 0.00062896 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_616-23_0_6_load_23 | 36 | 0.0037394 | 0.00093717 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_616-23_0_6_load_24 | 37 | 0.010562 | 0.0026471 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_616-23_0_6_load_28 | 39 | 0.0020757 | 0.00052021 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_616-23_0_6_load_29 | 40 | 0.0069617 | 0.0017448 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_616-23_0_6_load_30 | 42 | 0.0049571 | 0.0012424 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_616-23_0_6_load_31 | 43 | 0.010372 | 0.0025994 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_616-23_0_6_load_144 | 44 | 0.0031276 | 0.00078384 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_616-23_0_6_load_109 | 45 | 0.0067564 | 0.0016933 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_616-23_0_6_load_110 | 46 | 0.011457 | 0.0028713 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_616-23_0_6_load_173 | 47 | 0.0027807 | 0.00069691 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_616-23_0_6_load_108 | 48 | 0.0028487 | 0.00071396 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_616-23_0_6_load_33 | 49 | 0.0038894 | 0.00097477 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_616-23_0_6_load_34 | 50 | 0.001725 | 0.00043233 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_616-23_0_6_load_42 | 51 | 0.0018301 | 0.00045867 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_616-23_0_6_load_39 | 52 | 0.0015341 | 0.00038448 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_616-23_0_6_load_89 | 53 | 0.0036331 | 0.00091054 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_616-23_0_6_load_41 | 54 | 0.0026488 | 0.00066385 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_616-23_0_6_load_36 | 55 | 0.0035678 | 0.00089419 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_616-23_0_6_load_37 | 56 | 0.0019666 | 0.00049288 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_616-23_0_6_load_44 | 60 | 0.0042037 | 0.0010535 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_616-23_0_6_load_82 | 61 | 0.0032825 | 0.00082267 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_616-23_0_6_load_56 | 62 | 0.0021049 | 0.00052755 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_616-23_0_6_load_66 | 63 | 0.0087519 | 0.0021934 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_616-23_0_6_load_52 | 64 | 0.0024059 | 0.00060299 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_616-23_0_6_load_87 | 65 | 0.0024699 | 0.00061901 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_616-23_0_6_load_46 | 66 | 0.0024552 | 0.00061534 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_616-23_0_6_load_47 | 67 | 0.0037109 | 0.00093004 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_616-23_0_6_load_49 | 69 | 0.0033682 | 0.00084414 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_616-23_0_6_load_50 | 70 | 0.0030137 | 0.00075531 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_616-23_0_6_load_53 | 72 | 0.0022945 | 0.00057506 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_616-23_0_6_load_54 | 73 | 0.0028239 | 0.00070775 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_616-23_0_6_load_55 | 74 | 0.0057473 | 0.0014404 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_616-23_0_6_load_60 | 75 | 0.002848 | 0.00071378 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_616-23_0_6_load_70 | 76 | 0.0028508 | 0.00071447 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_616-23_0_6_load_58 | 77 | 0.0029584 | 0.00074145 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_616-23_0_6_load_83 | 78 | 0.0049169 | 0.0012323 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_616-23_0_6_load_84 | 79 | 0.0031178 | 0.0007814 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_616-23_0_6_load_68 | 80 | 0.0036794 | 0.00092214 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_616-23_0_6_load_57 | 81 | 0.0018965 | 0.00047532 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_616-23_0_6_load_59 | 82 | 0.0023875 | 0.00059836 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_616-23_0_6_load_61 | 83 | 0.0023974 | 0.00060084 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_616-23_0_6_load_64 | 86 | 0.0013883 | 0.00034795 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_616-23_0_6_load_65 | 87 | 0.002592 | 0.00064961 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_616-23_0_6_load_67 | 88 | 0.0044264 | 0.0011094 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_616-23_0_6_load_86 | 89 | 0.0022181 | 0.00055592 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_616-23_0_6_load_148 | 91 | 0.006261 | 0.0015692 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_616-23_0_6_load_69 | 92 | 0.0057386 | 0.0014382 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_616-23_0_6_load_71 | 93 | 0.0052379 | 0.0013127 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_616-23_0_6_load_73 | 95 | 0.0040854 | 0.0010239 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_616-23_0_6_load_74 | 96 | 0.0041268 | 0.0010343 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_616-23_0_6_load_75 | 97 | 0.0013984 | 0.00035047 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_616-23_0_6_load_76 | 98 | 0.0035468 | 0.00088891 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_616-23_0_6_load_150 | 99 | 0.0027886 | 0.00069889 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_616-23_0_6_load_78 | 100 | 0.0035385 | 0.00088683 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_616-23_0_6_load_151 | 101 | 0.00281 | 0.00070425 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_616-23_0_6_load_77 | 102 | 0.0031258 | 0.0007834 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_616-23_0_6_load_79 | 103 | 0.0040006 | 0.0010026 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_616-23_0_6_load_80 | 104 | 0.0042882 | 0.0010747 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_616-23_0_6_load_85 | 105 | 0.0050329 | 0.0012614 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_616-23_0_6_load_98 | 107 | 0.0033098 | 0.00082951 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_616-23_0_6_load_94 | 108 | 0.0065924 | 0.0016522 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_616-23_0_6_load_95 | 109 | 0.0034545 | 0.00086579 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_616-23_0_6_load_97 | 110 | 0.013984 | 0.0035047 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_616-23_0_6_load_100 | 112 | 0.002923 | 0.00073256 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_616-23_0_6_load_101 | 113 | 0.0050412 | 0.0012635 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_616-23_0_6_load_172 | 114 | 0.0024263 | 0.0006081 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_616-23_0_6_load_145 | 115 | 0.003262 | 0.00081754 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_616-23_0_6_load_171 | 116 | 0.0042538 | 0.0010661 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_616-23_0_6_load_176 | 117 | 0.0026367 | 0.00066083 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_616-23_0_6_load_104 | 118 | 0.0026683 | 0.00066874 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_616-23_0_6_load_105 | 119 | 0.0011717 | 0.00029365 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_616-23_0_6_load_106 | 120 | 0.0028013 | 0.00070208 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_616-23_0_6_load_107 | 121 | 0.0035188 | 0.0008819 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_616-23_0_6_load_115 | 122 | 0.0021949 | 0.00055009 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_616-23_0_6_load_116 | 123 | 0.0011121 | 0.00027872 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_616-23_0_6_load_129 | 124 | 0.0021726 | 0.00054449 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_616-23_0_6_load_146 | 125 | 0.0023451 | 0.00058774 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_616-23_0_6_load_130 | 126 | 0.0039866 | 0.00099914 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_616-23_0_6_load_147 | 127 | 0.0025775 | 0.00064599 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_616-23_0_6_load_117 | 128 | 0.0053826 | 0.001349 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_616-23_0_6_load_120 | 131 | 0.0025737 | 0.00064502 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_616-23_0_6_load_121 | 132 | 0.0032205 | 0.00080712 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_616-23_0_6_load_122 | 133 | 0.0018681 | 0.00046819 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_616-23_0_6_load_124 | 135 | 0.0030757 | 0.00077084 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_616-23_0_6_load_125 | 136 | 0.00099579 | 0.00024957 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_616-23_0_6_load_152 | 137 | 0.0025054 | 0.0006279 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_616-23_0_6_load_126 | 138 | 0.0043915 | 0.0011006 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_616-23_0_6_load_133 | 139 | 0.0042176 | 0.001057 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_616-23_0_6_load_153 | 140 | 0.0024229 | 0.00060722 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_616-23_0_6_load_127 | 142 | 0.0068795 | 0.0017242 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_616-23_0_6_load_128 | 143 | 0.0043622 | 0.0010933 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_616-23_0_6_load_168 | 144 | 0.0064928 | 0.0016273 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_616-23_0_6_load_165 | 147 | 0.0019939 | 0.00049971 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_616-23_0_6_load_174 | 149 | 0.0030523 | 0.00076498 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_616-23_0_6_load_161 | 150 | 0.0022135 | 0.00055475 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_616-23_0_6_load_159 | 151 | 0.0028304 | 0.00070938 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_616-23_0_6_load_135 | 152 | 0.0011594 | 0.00029058 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_616-23_0_6_load_136 | 153 | 0.0014169 | 0.00035511 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_616-23_0_6_load_137 | 154 | 0.0012772 | 0.00032008 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_616-23_0_6_load_138 | 155 | 0.0012604 | 0.00031588 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_616-23_0_6_load_139 | 156 | 0.0013384 | 0.00033544 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_616-23_0_6_load_140 | 157 | 0.0010649 | 0.00026688 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_616-23_0_6_load_141 | 158 | 0.0029519 | 0.00073983 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_616-23_0_6_load_155 | 159 | 0.0028327 | 0.00070994 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_616-23_0_6_load_154 | 160 | 0.0033885 | 0.00084923 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_616-23_0_6_load_158 | 161 | 0.0031632 | 0.00079278 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_616-23_0_6_load_177 | 162 | 0.0023678 | 0.00059343 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_616-23_0_6_load_162 | 163 | 0.0034219 | 0.0008576 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_616-23_0_6_load_163 | 164 | 0.0024837 | 0.00062248 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_616-23_0_6_load_156 | 165 | 0.0027198 | 0.00068165 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_616-23_0_6_load_157 | 166 | 0.002849 | 0.00071403 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_616-23_0_6_load_170 | 167 | 0.0043509 | 0.0010904 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_616-23_0_6_load_166 | 169 | 0.0022901 | 0.00057395 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_616-23_0_6_load_175 | 170 | 0.0053145 | 0.0013319 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_616-23_0_6_load_169 | 171 | 0.0034432 | 0.00086295 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_616-23_0_6_load_178 | 172 | 0.0084121 | 0.0021083 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 80 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_616-23_0_6_line_0 |  | 0 | 1 | 0.0097094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_616-23_0_6_line_1 |  | 0 | 2 | 0.015969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_616-23_0_6_line_2 |  | 1 | 3 | 0.0096222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_616-23_0_6_line_3 |  | 2 | 4 | 0.013915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_616-23_0_6_line_4 |  | 3 | 5 | 0.016888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_616-23_0_6_line_5 |  | 4 | 6 | 0.011552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_616-23_0_6_line_6 |  | 4 | 7 | 0.045654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_616-23_0_6_line_7 |  | 5 | 8 | 0.034546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_616-23_0_6_line_8 |  | 6 | 14 | 0.0055228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_616-23_0_6_line_9 |  | 7 | 15 | 0.0056567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_616-23_0_6_line_10 |  | 9 | 10 | 0.023871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_616-23_0_6_line_11 |  | 10 | 16 | 0.00074685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_616-23_0_6_line_12 |  | 11 | 12 | 0.024786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_616-23_0_6_line_13 |  | 11 | 13 | 0.041583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_616-23_0_6_line_14 |  | 13 | 17 | 0.016263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_616-23_0_6_line_15 |  | 14 | 18 | 0.018422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_616-23_0_6_line_16 |  | 16 | 104 | 0.023397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_616-23_0_6_line_17 |  | 17 | 40 | 0.023691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_616-23_0_6_line_18 |  | 18 | 53 | 0.013676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_616-23_0_6_line_19 |  | 18 | 54 | 0.043784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_616-23_0_6_line_20 |  | 19 | 20 | 0.032683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_616-23_0_6_line_21 |  | 20 | 23 | 0.0097046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_616-23_0_6_line_22 |  | 21 | 22 | 0.024235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_616-23_0_6_line_23 |  | 22 | 60 | 0.0058147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_616-23_0_6_line_24 |  | 23 | 65 | 0.0076436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_616-23_0_6_line_25 |  | 24 | 25 | 0.0092523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_616-23_0_6_line_26 |  | 24 | 26 | 0.049326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_616-23_0_6_line_27 |  | 25 | 27 | 0.0096664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_616-23_0_6_line_28 |  | 26 | 28 | 0.0056573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_616-23_0_6_line_29 |  | 26 | 29 | 0.011714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_616-23_0_6_line_30 |  | 28 | 30 | 0.017671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_616-23_0_6_line_31 |  | 29 | 31 | 0.037168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_616-23_0_6_line_32 |  | 30 | 32 | 0.0064567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_616-23_0_6_line_33 |  | 31 | 33 | 0.001517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_616-23_0_6_line_34 |  | 32 | 34 | 0.021115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_616-23_0_6_line_35 |  | 33 | 35 | 0.019778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_616-23_0_6_line_36 |  | 34 | 118 | 0.017883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_616-23_0_6_line_37 |  | 35 | 122 | 0.013763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_616-23_0_6_line_38 |  | 35 | 123 | 0.0069727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_616-23_0_6_line_39 |  | 36 | 37 | 0.0017754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_616-23_0_6_line_40 |  | 37 | 38 | 0.011408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_616-23_0_6_line_41 |  | 38 | 39 | 0.015322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_616-23_0_6_line_42 |  | 38 | 40 | 0.028447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_616-23_0_6_line_43 |  | 39 | 44 | 0.002117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_616-23_0_6_line_44 |  | 41 | 42 | 0.0081806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_616-23_0_6_line_45 |  | 41 | 43 | 0.015276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_616-23_0_6_line_46 |  | 42 | 45 | 0.013976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_616-23_0_6_line_47 |  | 43 | 46 | 0.029886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_616-23_0_6_line_48 |  | 44 | 47 | 0.0052647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_616-23_0_6_line_49 |  | 45 | 48 | 0.030922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_616-23_0_6_line_50 |  | 47 | 161 | 0.013148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_616-23_0_6_line_51 |  | 48 | 121 | 0.0028114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_616-23_0_6_line_52 |  | 49 | 50 | 0.0082973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_616-23_0_6_line_53 |  | 50 | 51 | 0.0001404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_616-23_0_6_line_54 |  | 51 | 52 | 0.00098736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_616-23_0_6_line_55 |  | 52 | 56 | 0.00012379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_616-23_0_6_line_56 |  | 53 | 65 | 0.0081318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_616-23_0_6_line_57 |  | 54 | 57 | 0.006264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_616-23_0_6_line_58 |  | 55 | 56 | 0.030669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_616-23_0_6_line_59 |  | 55 | 57 | 0.024216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_616-23_0_6_line_60 |  | 57 | 58 | 0.003833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_616-23_0_6_line_61 |  | 58 | 59 | 0.021296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_616-23_0_6_line_62 |  | 58 | 60 | 0.025333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_616-23_0_6_line_63 |  | 59 | 61 | 0.0273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_616-23_0_6_line_64 |  | 59 | 62 | 0.0086958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_616-23_0_6_line_65 |  | 61 | 63 | 0.0070428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_616-23_0_6_line_66 |  | 62 | 64 | 0.012573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_616-23_0_6_line_67 |  | 63 | 85 | 0.021946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_616-23_0_6_line_68 |  | 64 | 69 | 0.02504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_616-23_0_6_line_69 |  | 66 | 67 | 0.0038032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_616-23_0_6_line_70 |  | 66 | 68 | 0.01657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_616-23_0_6_line_71 |  | 67 | 69 | 0.015867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_616-23_0_6_line_72 |  | 68 | 70 | 0.012513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_616-23_0_6_line_73 |  | 71 | 72 | 0.017403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_616-23_0_6_line_74 |  | 71 | 73 | 0.013643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_616-23_0_6_line_75 |  | 71 | 74 | 0.013051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_616-23_0_6_line_76 |  | 72 | 75 | 0.0034687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_616-23_0_6_line_77 |  | 74 | 76 | 0.025741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_616-23_0_6_line_78 |  | 75 | 77 | 0.02257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_616-23_0_6_line_79 |  | 76 | 80 | 0.011319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_616-23_0_6_line_80 |  | 77 | 81 | 0.00077628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_616-23_0_6_line_81 |  | 78 | 79 | 0.0071861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_616-23_0_6_line_82 |  | 79 | 105 | 0.02369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_616-23_0_6_line_83 |  | 80 | 92 | 0.0084916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_616-23_0_6_line_84 |  | 81 | 82 | 0.024401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_616-23_0_6_line_85 |  | 82 | 83 | 0.0037719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_616-23_0_6_line_86 |  | 83 | 84 | 0.024256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_616-23_0_6_line_87 |  | 84 | 85 | 0.017022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_616-23_0_6_line_88 |  | 84 | 86 | 0.0099835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_616-23_0_6_line_89 |  | 85 | 87 | 0.048555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_616-23_0_6_line_90 |  | 86 | 88 | 0.0078333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_616-23_0_6_line_91 |  | 87 | 89 | 0.014848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_616-23_0_6_line_92 |  | 88 | 90 | 0.0039609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_616-23_0_6_line_93 |  | 90 | 91 | 0.020448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_616-23_0_6_line_94 |  | 92 | 93 | 0.002614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_616-23_0_6_line_95 |  | 93 | 94 | 0.021245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_616-23_0_6_line_96 |  | 94 | 95 | 0.012623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_616-23_0_6_line_97 |  | 94 | 96 | 0.0081101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_616-23_0_6_line_98 |  | 95 | 97 | 0.013392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_616-23_0_6_line_99 |  | 96 | 98 | 0.025423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_616-23_0_6_line_100 |  | 97 | 99 | 0.022859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_616-23_0_6_line_101 |  | 98 | 100 | 0.021435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_616-23_0_6_line_102 |  | 99 | 101 | 0.0061694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_616-23_0_6_line_103 |  | 100 | 102 | 0.0046111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_616-23_0_6_line_104 |  | 101 | 151 | 0.021961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_616-23_0_6_line_105 |  | 102 | 103 | 0.015504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_616-23_0_6_line_106 |  | 103 | 104 | 0.020294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_616-23_0_6_line_107 |  | 105 | 106 | 0.0053377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_616-23_0_6_line_108 |  | 106 | 107 | 0.0086833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_616-23_0_6_line_109 |  | 106 | 108 | 0.023497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_616-23_0_6_line_110 |  | 107 | 112 | 0.0035321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_616-23_0_6_line_111 |  | 108 | 109 | 0.020521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_616-23_0_6_line_112 |  | 109 | 110 | 0.017381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_616-23_0_6_line_113 |  | 110 | 111 | 0.0066924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_616-23_0_6_line_114 |  | 111 | 113 | 0.0057667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_616-23_0_6_line_115 |  | 112 | 114 | 9.7676e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_616-23_0_6_line_116 |  | 113 | 115 | 0.029897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_616-23_0_6_line_117 |  | 114 | 116 | 0.0078633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_616-23_0_6_line_118 |  | 115 | 117 | 0.016453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_616-23_0_6_line_119 |  | 116 | 167 | 0.023294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_616-23_0_6_line_120 |  | 117 | 162 | 0.0062105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_616-23_0_6_line_121 |  | 118 | 119 | 0.0014061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_616-23_0_6_line_122 |  | 119 | 120 | 0.012726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_616-23_0_6_line_123 |  | 120 | 121 | 0.02983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_616-23_0_6_line_124 |  | 122 | 124 | 0.014194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_616-23_0_6_line_125 |  | 123 | 125 | 0.020551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_616-23_0_6_line_126 |  | 124 | 126 | 0.0072185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_616-23_0_6_line_127 |  | 125 | 127 | 0.0007964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_616-23_0_6_line_128 |  | 126 | 141 | 0.010337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
129 | LV_616-23_0_6_line_129 |  | 127 | 157 | 0.023651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_616-23_0_6_line_130 |  | 128 | 129 | 0.025836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_616-23_0_6_line_131 |  | 128 | 130 | 0.014442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_616-23_0_6_line_132 |  | 129 | 131 | 0.024672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_616-23_0_6_line_133 |  | 130 | 132 | 0.020471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_616-23_0_6_line_134 |  | 130 | 133 | 0.01736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_616-23_0_6_line_135 |  | 131 | 134 | 0.033492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_616-23_0_6_line_136 |  | 132 | 135 | 0.011588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_616-23_0_6_line_137 |  | 133 | 136 | 0.010235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_616-23_0_6_line_138 |  | 134 | 137 | 0.0067837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_616-23_0_6_line_139 |  | 135 | 138 | 0.010046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_616-23_0_6_line_140 |  | 136 | 139 | 0.015398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_616-23_0_6_line_141 |  | 137 | 140 | 0.013695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_616-23_0_6_line_142 |  | 139 | 141 | 0.010467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_616-23_0_6_line_143 |  | 140 | 163 | 0.012995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_616-23_0_6_line_144 |  | 141 | 146 | 0.019131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
145 | LV_616-23_0_6_line_145 |  | 142 | 143 | 0.0056997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_616-23_0_6_line_146 |  | 143 | 144 | 0.024977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_616-23_0_6_line_147 |  | 144 | 145 | 0.021645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_616-23_0_6_line_148 |  | 145 | 171 | 0.0014908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_616-23_0_6_line_149 |  | 145 | 169 | 0.018924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_616-23_0_6_line_150 |  | 146 | 147 | 0.015101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_616-23_0_6_line_151 |  | 146 | 148 | 0.024478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
152 | LV_616-23_0_6_line_152 |  | 147 | 149 | 0.00042996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_616-23_0_6_line_153 |  | 148 | 150 | 0.017106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_616-23_0_6_line_154 |  | 148 | 151 | 0.0063727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
155 | LV_616-23_0_6_line_155 |  | 149 | 170 | 0.0051484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_616-23_0_6_line_156 |  | 150 | 167 | 0.022059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_616-23_0_6_line_157 |  | 152 | 153 | 0.013085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_616-23_0_6_line_158 |  | 152 | 154 | 0.0056886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_616-23_0_6_line_159 |  | 153 | 155 | 0.0060955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_616-23_0_6_line_160 |  | 154 | 156 | 0.0061069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_616-23_0_6_line_161 |  | 155 | 157 | 0.0052945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_616-23_0_6_line_162 |  | 156 | 158 | 0.012754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_616-23_0_6_line_163 |  | 158 | 159 | 0.0055392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_616-23_0_6_line_164 |  | 159 | 160 | 0.005958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_616-23_0_6_line_165 |  | 160 | 165 | 0.012902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_616-23_0_6_line_166 |  | 161 | 166 | 0.0060981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_616-23_0_6_line_167 |  | 162 | 172 | 0.024654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_616-23_0_6_line_168 |  | 163 | 164 | 0.021486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_616-23_0_6_line_169 |  | 164 | 168 | 0.0021121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_616-23_0_6_line_170 |  | 165 | 166 | 0.0056449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_616-23_0_6_line_171 |  | 168 | 169 | 0.02526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_616-23_0_6_trafo_68 | 0.63 MVA 20/0.4 kV | 173 | 80 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2609674.8228 | 1191822.473 | 2609665.7061 | 1191819.1326
1 | 2609689.7737 | 1191828.0818 | 2609682.9706 | 1191825.4583 | 2609674.8228 | 1191822.473
2 | 2609656.6713 | 1191815.8222 | 2609665.7061 | 1191819.1326
3 | 2609689.7737 | 1191828.0818 | 2609690.4222 | 1191841.979
4 | 2609656.6713 | 1191815.8222 | 2609648.2785 | 1191830.4775
5 | 2609690.4222 | 1191841.979 | 2609691.0339 | 1191853.5144
6 | 2609690.4222 | 1191841.979 | 2609703.8712 | 1191826.5148 | 2609710.0066 | 1191822.5448 | 2609714.9164 | 1191822.1525 | 2609724.5745 | 1191830.7439
7 | 2609630.1602 | 1191859.878 | 2609641.8258 | 1191841.7454 | 2609648.2785 | 1191830.4775
8 | 2609691.943 | 1191858.9493 | 2609691.1102 | 1191854.9536 | 2609691.0339 | 1191853.5144
9 | 2609728.8009 | 1191834.5036 | 2609724.5745 | 1191830.7439
10 | 2609738.6734 | 1191789.3443 | 2609716.1049 | 1191781.5675
11 | 2609739.3796 | 1191789.5876 | 2609738.6734 | 1191789.3443
12 | 2609718.6101 | 1191739.3038 | 2609721.0776 | 1191736.0505 | 2609733.041 | 1191720.2615 | 2609733.5973 | 1191719.5627
13 | 2609718.6101 | 1191739.3038 | 2609757.2669 | 1191754.6281
14 | 2609772.3855 | 1191760.6214 | 2609757.2669 | 1191754.6281
15 | 2609695.7019 | 1191876.9837 | 2609691.943 | 1191858.9493
16 | 2609739.3796 | 1191789.5876 | 2609761.5 | 1191797.21
17 | 2609794.4094 | 1191769.3521 | 2609772.3855 | 1191760.6214
18 | 2609695.7019 | 1191876.9837 | 2609688.8465 | 1191888.8171
19 | 2609695.7019 | 1191876.9837 | 2609700.1138 | 1191887.5964 | 2609710.5448 | 1191904.7889 | 2609717.4959 | 1191914.7921
20 | 2609674.5563 | 1191909.8892 | 2609663.9095 | 1191927.3813 | 2609657.8478 | 1191937.9746
21 | 2609674.5563 | 1191909.8892 | 2609674.5563 | 1191909.8892 | 2609680.1751 | 1191901.9767
22 | 2609708.9467 | 1191950.7019 | 2609698.3264 | 1191972.4858
23 | 2609708.9467 | 1191950.7019 | 2609711.4949 | 1191945.4753
24 | 2609684.6007 | 1191895.7445 | 2609680.1751 | 1191901.9767
25 | 2610047.5263 | 1191814.0997 | 2610055.4176 | 1191818.9301
26 | 2610009.8725 | 1191782.4034 | 2610021.4404 | 1191793.9509 | 2610034.9165 | 1191804.0342 | 2610046.0233 | 1191813.1797 | 2610047.5263 | 1191814.0997
27 | 2610063.7706 | 1191823.7684 | 2610062.2133 | 1191823.0898 | 2610055.4176 | 1191818.9301
28 | 2610009.8725 | 1191782.4034 | 2610005.6361 | 1191778.654
29 | 2610009.8725 | 1191782.4034 | 2610006.8082 | 1191793.7092
30 | 2610005.6361 | 1191778.654 | 2609997.0236 | 1191771.0316 | 2609991.7562 | 1191767.8198
31 | 2609990.2358 | 1191824.6435 | 2610000.7697 | 1191801.2871 | 2610004.8639 | 1191800.8825 | 2610006.8082 | 1191793.7092
32 | 2609986.2435 | 1191764.4585 | 2609991.7562 | 1191767.8198
33 | 2609990.2358 | 1191824.6435 | 2609989.6121 | 1191826.0264
34 | 2609986.2435 | 1191764.4585 | 2609985.7071 | 1191764.1314 | 2609973.2657 | 1191759.7974 | 2609966.0294 | 1191758.7499
35 | 2609981.481 | 1191844.0553 | 2609989.6121 | 1191826.0264
36 | 2609948.2103 | 1191757.7624 | 2609959.9818 | 1191757.8744 | 2609966.0294 | 1191758.7499
37 | 2609981.481 | 1191844.0553 | 2609976.4484 | 1191856.8652
38 | 2609981.481 | 1191844.0553 | 2609975.0066 | 1191841.4668
39 | 2609825.2978 | 1191769.328 | 2609825.9893 | 1191767.6928
40 | 2609820.8544 | 1191779.8353 | 2609825.2978 | 1191769.328
41 | 2609820.8544 | 1191779.8353 | 2609835.0814 | 1191785.5235
42 | 2609820.8544 | 1191779.8353 | 2609794.4094 | 1191769.3521
43 | 2609835.0814 | 1191785.5235 | 2609837.0471 | 1191786.3094
44 | 2609850.6141 | 1191738.4399 | 2609858.1445 | 1191741.6362
45 | 2609850.6141 | 1191738.4399 | 2609839.5377 | 1191733.7305 | 2609836.5548 | 1191732.4642
46 | 2609858.1445 | 1191741.6362 | 2609859.2908 | 1191742.1227 | 2609871.7746 | 1191744.6175
47 | 2609809.0449 | 1191720.7862 | 2609836.5548 | 1191732.4642
48 | 2609841.9356 | 1191788.2638 | 2609837.0471 | 1191786.3094
49 | 2609902.0461 | 1191750.9268 | 2609874.715 | 1191745.2052 | 2609871.7746 | 1191744.6175
50 | 2609841.9356 | 1191788.2638 | 2609854.1438 | 1191793.1448
51 | 2609902.0461 | 1191750.9268 | 2609904.7979 | 1191751.5028
52 | 2609747.1715 | 1191870.2364 | 2609751.0452 | 1191862.8988
53 | 2609747.106 | 1191870.3605 | 2609747.1715 | 1191870.2364
54 | 2609746.6455 | 1191871.234 | 2609746.7703 | 1191870.9963 | 2609747.106 | 1191870.3605
55 | 2609746.588 | 1191871.3435 | 2609746.6455 | 1191871.234
56 | 2609688.8465 | 1191888.8171 | 2609685.8638 | 1191893.9657 | 2609684.6007 | 1191895.7445
57 | 2609721.0705 | 1191919.936 | 2609717.4959 | 1191914.7921
58 | 2609746.588 | 1191871.3435 | 2609732.329 | 1191898.4966
59 | 2609721.0705 | 1191919.936 | 2609732.329 | 1191898.4966
60 | 2609723.2913 | 1191923.0635 | 2609721.0705 | 1191919.936
61 | 2609723.2913 | 1191923.0635 | 2609735.2689 | 1191940.6921
62 | 2609723.2913 | 1191923.0635 | 2609715.2788 | 1191937.7138 | 2609711.4949 | 1191945.4753
63 | 2609735.2689 | 1191940.6921 | 2609739.0415 | 1191945.8342 | 2609751.4157 | 1191962.7053
64 | 2609735.2689 | 1191940.6921 | 2609739.2521 | 1191932.9622
65 | 2609751.4157 | 1191962.7053 | 2609755.5809 | 1191968.3843
66 | 2609745.0113 | 1191921.786 | 2609739.2521 | 1191932.9622
67 | 2609768.5607 | 1191986.081 | 2609755.5809 | 1191968.3843
68 | 2609745.0113 | 1191921.786 | 2609756.4815 | 1191899.527 | 2609756.4815 | 1191899.527
69 | 2609771.6212 | 1191904.2746 | 2609775.2502 | 1191905.4126
70 | 2609787.5589 | 1191900.4001 | 2609782.6378 | 1191907.7293 | 2609775.2502 | 1191905.4126
71 | 2609771.6212 | 1191904.2746 | 2609756.4815 | 1191899.527
72 | 2609787.5589 | 1191900.4001 | 2609791.664 | 1191888.5783
73 | 2609815.1222 | 1191910.528 | 2609808.5196 | 1191926.6299
74 | 2609815.1222 | 1191910.528 | 2609827.7734 | 1191915.6335
75 | 2609815.1222 | 1191910.528 | 2609820.4635 | 1191898.6198
76 | 2609808.5196 | 1191926.6299 | 2609807.2036 | 1191929.8393
77 | 2609820.4635 | 1191898.6198 | 2609830.9981 | 1191875.1329
78 | 2609807.2036 | 1191929.8393 | 2609798.641 | 1191950.7215
79 | 2609835.6304 | 1191864.8055 | 2609830.9981 | 1191875.1329
80 | 2609798.3464 | 1191951.4398 | 2609798.641 | 1191950.7215
81 | 2609860.6482 | 1191928.9002 | 2609853.9843 | 1191926.2109
82 | 2609860.6482 | 1191928.9002 | 2609875.9739 | 1191935.0849 | 2609882.6395 | 1191937.7075
83 | 2609835.6304 | 1191864.8055 | 2609839.1056 | 1191857.0575
84 | 2609789.089 | 1191974.0163 | 2609798.3464 | 1191951.4398
85 | 2609787.658 | 1191977.5062 | 2609789.089 | 1191974.0163
86 | 2609778.4555 | 1191999.9488 | 2609787.658 | 1191977.5062
87 | 2609768.5607 | 1191986.081 | 2609778.4555 | 1191999.9488
88 | 2609778.4555 | 1191999.9488 | 2609784.0402 | 1192008.2241
89 | 2609768.5607 | 1191986.081 | 2609740.2863 | 1192024.5888 | 2609739.9119 | 1192025.2745
90 | 2609788.4222 | 1192014.7171 | 2609784.0402 | 1192008.2241
91 | 2609739.9119 | 1192025.2745 | 2609732.7974 | 1192038.307
92 | 2609790.6379 | 1192018.0003 | 2609788.4222 | 1192014.7171
93 | 2609790.6379 | 1192018.0003 | 2609802.8307 | 1192034.4155
94 | 2609840.1754 | 1191854.6725 | 2609839.1056 | 1191857.0575
95 | 2609848.87 | 1191835.288 | 2609840.1754 | 1191854.6725
96 | 2609848.87 | 1191835.288 | 2609860.3466 | 1191840.5453
97 | 2609848.87 | 1191835.288 | 2609841.4963 | 1191831.9114
98 | 2609860.3466 | 1191840.5453 | 2609872.5216 | 1191846.1225
99 | 2609841.4963 | 1191831.9114 | 2609818.3819 | 1191821.327
100 | 2609892.8809 | 1191856.4989 | 2609878.2424 | 1191848.7432 | 2609872.5216 | 1191846.1225
101 | 2609798.8929 | 1191812.4027 | 2609818.3819 | 1191821.327
102 | 2609898.3324 | 1191859.3872 | 2609892.8809 | 1191856.4989
103 | 2609794.7005 | 1191810.4829 | 2609798.8929 | 1191812.4027
104 | 2609898.3324 | 1191859.3872 | 2609917.7382 | 1191869.6687
105 | 2609794.7005 | 1191810.4829 | 2609780.604 | 1191804.0279
106 | 2609761.5 | 1191797.21 | 2609778.5313 | 1191803.0787 | 2609780.604 | 1191804.0279
107 | 2609887.6066 | 1191939.6619 | 2609882.6395 | 1191937.7075
108 | 2609887.6066 | 1191939.6619 | 2609894.2799 | 1191942.2854 | 2609894.8631 | 1191940.8894
109 | 2609887.6066 | 1191939.6619 | 2609879.7726 | 1191961.814
110 | 2609894.8631 | 1191940.8894 | 2609896.2246 | 1191937.6303
111 | 2609879.7726 | 1191961.814 | 2609872.9307 | 1191981.1611
112 | 2609872.9307 | 1191981.1611 | 2609867.1357 | 1191997.5477 | 2609867.1357 | 1191997.5477
113 | 2609873.4284 | 1191999.8258 | 2609867.1357 | 1191997.5477
114 | 2609873.4284 | 1191999.8258 | 2609875.6202 | 1191994.4919
115 | 2609896.2622 | 1191937.5402 | 2609896.2246 | 1191937.6303
116 | 2609875.6202 | 1191994.4919 | 2609881.9466 | 1191979.0956 | 2609886.2583 | 1191976.1789 | 2609890.4113 | 1191977.0973 | 2609893.8265 | 1191978.7473
117 | 2609899.2933 | 1191930.2845 | 2609896.2622 | 1191937.5402
118 | 2609908.641 | 1191985.9048 | 2609893.8265 | 1191978.7473
119 | 2609899.2933 | 1191930.2845 | 2609908.2723 | 1191908.7909
120 | 2609908.641 | 1191985.9048 | 2609914.2331 | 1191988.6065
121 | 2609946.8043 | 1191757.749 | 2609948.2103 | 1191757.7624
122 | 2609946.8043 | 1191757.749 | 2609944.4385 | 1191757.7265 | 2609934.1225 | 1191756.769
123 | 2609904.7979 | 1191751.5028 | 2609926.6336 | 1191756.074 | 2609934.1225 | 1191756.769
124 | 2609976.4484 | 1191856.8652 | 2609971.258 | 1191870.0765
125 | 2609955.9245 | 1191833.8376 | 2609975.0066 | 1191841.4668
126 | 2609971.258 | 1191870.0765 | 2609968.6185 | 1191876.7952
127 | 2609955.9245 | 1191833.8376 | 2609955.185 | 1191833.542
128 | 2609964.8384 | 1191886.4167 | 2609968.6185 | 1191876.7952
129 | 2609955.185 | 1191833.542 | 2609933.2238 | 1191824.7617
130 | 2610055.4046 | 1191910.5911 | 2610030.4248 | 1191903.9962
131 | 2610016.4609 | 1191900.3097 | 2610030.4248 | 1191903.9962
132 | 2610055.4046 | 1191910.5911 | 2610046.8794 | 1191925.9516 | 2610043.7939 | 1191932.3509
133 | 2610016.4609 | 1191900.3097 | 2610008.5583 | 1191919.1935
134 | 2610016.4609 | 1191900.3097 | 2609999.6977 | 1191895.7982
135 | 2610029.2477 | 1191962.5192 | 2610043.7939 | 1191932.3509
136 | 2610008.5583 | 1191919.1935 | 2610004.0846 | 1191929.8836
137 | 2609989.8147 | 1191893.1385 | 2609999.6977 | 1191895.7982
138 | 2610029.2477 | 1191962.5192 | 2610026.1651 | 1191968.5621
139 | 2610004.0846 | 1191929.8836 | 2610000.2063 | 1191939.151
140 | 2609974.9458 | 1191889.1369 | 2609989.8147 | 1191893.1385
141 | 2610026.1651 | 1191968.5621 | 2610019.9422 | 1191980.7614
142 | 2609964.8384 | 1191886.4167 | 2609974.9458 | 1191889.1369
143 | 2610019.9422 | 1191980.7614 | 2610014.037 | 1191992.3376
144 | 2609964.8384 | 1191886.4167 | 2609964.0688 | 1191886.2153 | 2609952.7919 | 1191883.1729 | 2609946.4762 | 1191880.9168
145 | 2609985.8872 | 1191973.6734 | 2609983.758 | 1191978.9604
146 | 2609983.758 | 1191978.9604 | 2609974.4272 | 1192002.1286
147 | 2609966.7021 | 1192022.3469 | 2609973.0186 | 1192005.6263 | 2609974.4272 | 1192002.1286
148 | 2609966.7021 | 1192022.3469 | 2609966.1247 | 1192023.7214
149 | 2609966.7021 | 1192022.3469 | 2609973.684 | 1192022.6808 | 2609982.4238 | 1192024.8298 | 2609985.3073 | 1192025.3716
150 | 2609946.4762 | 1191880.9168 | 2609940.547 | 1191894.8053
151 | 2609923.3693 | 1191872.6521 | 2609946.4762 | 1191880.9168
152 | 2609940.3782 | 1191895.2007 | 2609940.547 | 1191894.8053
153 | 2609923.3693 | 1191872.6521 | 2609916.7755 | 1191888.4363
154 | 2609923.3693 | 1191872.6521 | 2609917.7382 | 1191869.6687
155 | 2609938.3568 | 1191899.9356 | 2609940.3782 | 1191895.2007
156 | 2609916.7755 | 1191888.4363 | 2609908.2723 | 1191908.7909
157 | 2609922.6478 | 1191820.5333 | 2609910.4983 | 1191815.6758
158 | 2609905.2162 | 1191813.564 | 2609910.4983 | 1191815.6758
159 | 2609922.6478 | 1191820.5333 | 2609928.3076 | 1191822.7961
160 | 2609899.5457 | 1191811.2968 | 2609905.2162 | 1191813.564
161 | 2609928.3076 | 1191822.7961 | 2609933.2238 | 1191824.7617
162 | 2609899.5457 | 1191811.2968 | 2609887.7031 | 1191806.5621
163 | 2609882.5598 | 1191804.5057 | 2609887.7031 | 1191806.5621
164 | 2609882.5598 | 1191804.5057 | 2609877.0275 | 1191802.2939
165 | 2609865.0477 | 1191797.5042 | 2609877.0275 | 1191802.2939
166 | 2609859.8061 | 1191795.4086 | 2609854.1438 | 1191793.1448
167 | 2609917.7143 | 1192006.0685 | 2609923.6357 | 1191993.1493 | 2609914.2331 | 1191988.6065
168 | 2610004.2738 | 1192011.4769 | 2610014.037 | 1191992.3376
169 | 2610003.3141 | 1192013.3584 | 2610004.2738 | 1192011.4769
170 | 2609859.8061 | 1191795.4086 | 2609865.0477 | 1191797.5042
171 | 2610003.3141 | 1192013.3584 | 2609998.1366 | 1192023.5107 | 2609995.1061 | 1192026.0625 | 2609990.6005 | 1192026.3663 | 2609985.3073 | 1192025.3716

## bus_geodata
| x | y | coords
0 | 2609674.8228 | 1191822.473
1 | 2609665.7061 | 1191819.1326
2 | 2609689.7737 | 1191828.0818
3 | 2609656.6713 | 1191815.8222
4 | 2609690.4222 | 1191841.979
5 | 2609648.2785 | 1191830.4775
6 | 2609691.0339 | 1191853.5144
7 | 2609724.5745 | 1191830.7439
8 | 2609630.1602 | 1191859.878
9 | 2609716.1049 | 1191781.5675
10 | 2609738.6734 | 1191789.3443
11 | 2609718.6101 | 1191739.3038
12 | 2609733.5973 | 1191719.5627
13 | 2609757.2669 | 1191754.6281
14 | 2609691.943 | 1191858.9493
15 | 2609728.8009 | 1191834.5036
16 | 2609739.3796 | 1191789.5876
17 | 2609772.3855 | 1191760.6214
18 | 2609695.7019 | 1191876.9837
19 | 2609657.8478 | 1191937.9746
20 | 2609674.5563 | 1191909.8892
21 | 2609698.3264 | 1191972.4858
22 | 2609708.9467 | 1191950.7019
23 | 2609680.1751 | 1191901.9767
24 | 2610047.5263 | 1191814.0997
25 | 2610055.4176 | 1191818.9301
26 | 2610009.8725 | 1191782.4034
27 | 2610063.7705 | 1191823.7684
28 | 2610005.6361 | 1191778.654
29 | 2610006.8082 | 1191793.7092
30 | 2609991.7562 | 1191767.8198
31 | 2609990.2358 | 1191824.6435
32 | 2609986.2435 | 1191764.4585
33 | 2609989.6121 | 1191826.0264
34 | 2609966.0294 | 1191758.7499
35 | 2609981.481 | 1191844.0553
36 | 2609825.9893 | 1191767.6928
37 | 2609825.2978 | 1191769.328
38 | 2609820.8544 | 1191779.8353
39 | 2609835.0814 | 1191785.5235
40 | 2609794.4094 | 1191769.3521
41 | 2609850.6141 | 1191738.4399
42 | 2609858.1445 | 1191741.6362
43 | 2609836.5548 | 1191732.4643
44 | 2609837.0471 | 1191786.3094
45 | 2609871.7746 | 1191744.6175
46 | 2609809.0449 | 1191720.7862
47 | 2609841.9356 | 1191788.2638
48 | 2609902.0461 | 1191750.9268
49 | 2609751.0452 | 1191862.8988
50 | 2609747.1715 | 1191870.2364
51 | 2609747.106 | 1191870.3605
52 | 2609746.6455 | 1191871.234
53 | 2609688.8465 | 1191888.8171
54 | 2609717.4959 | 1191914.7921
55 | 2609732.329 | 1191898.4966
56 | 2609746.588 | 1191871.3435
57 | 2609721.0705 | 1191919.936
58 | 2609723.2913 | 1191923.0635
59 | 2609735.2689 | 1191940.6921
60 | 2609711.4949 | 1191945.4753
61 | 2609751.4157 | 1191962.7053
62 | 2609739.2521 | 1191932.9622
63 | 2609755.5809 | 1191968.3843
64 | 2609745.0113 | 1191921.786
65 | 2609684.6007 | 1191895.7445
66 | 2609775.2502 | 1191905.4126
67 | 2609771.6212 | 1191904.2746
68 | 2609787.5589 | 1191900.4001
69 | 2609756.4815 | 1191899.527
70 | 2609791.664 | 1191888.5783
71 | 2609815.1222 | 1191910.528
72 | 2609808.5196 | 1191926.6299
73 | 2609827.7734 | 1191915.6335
74 | 2609820.4635 | 1191898.6198
75 | 2609807.2036 | 1191929.8393
76 | 2609830.9981 | 1191875.1329
77 | 2609798.641 | 1191950.7215
78 | 2609853.9843 | 1191926.2109
79 | 2609860.6482 | 1191928.9002
80 | 2609835.6304 | 1191864.8055
81 | 2609798.3464 | 1191951.4398
82 | 2609789.089 | 1191974.0163
83 | 2609787.658 | 1191977.5062
84 | 2609778.4555 | 1191999.9488
85 | 2609768.5607 | 1191986.081
86 | 2609784.0402 | 1192008.2241
87 | 2609739.9119 | 1192025.2745
88 | 2609788.4222 | 1192014.7171
89 | 2609732.7974 | 1192038.307
90 | 2609790.6379 | 1192018.0003
91 | 2609802.8307 | 1192034.4155
92 | 2609839.1056 | 1191857.0575
93 | 2609840.1754 | 1191854.6725
94 | 2609848.87 | 1191835.288
95 | 2609860.3466 | 1191840.5453
96 | 2609841.4963 | 1191831.9114
97 | 2609872.5216 | 1191846.1226
98 | 2609818.3819 | 1191821.327
99 | 2609892.8809 | 1191856.4989
100 | 2609798.8929 | 1191812.4027
101 | 2609898.3324 | 1191859.3872
102 | 2609794.7005 | 1191810.4829
103 | 2609780.604 | 1191804.0279
104 | 2609761.5 | 1191797.21
105 | 2609882.6395 | 1191937.7075
106 | 2609887.6066 | 1191939.6619
107 | 2609894.8631 | 1191940.8894
108 | 2609879.7726 | 1191961.814
109 | 2609872.9307 | 1191981.1611
110 | 2609867.1357 | 1191997.5477
111 | 2609873.4284 | 1191999.8258
112 | 2609896.2246 | 1191937.6303
113 | 2609875.6202 | 1191994.4919
114 | 2609896.2622 | 1191937.5402
115 | 2609893.8265 | 1191978.7473
116 | 2609899.2933 | 1191930.2845
117 | 2609908.641 | 1191985.9048
118 | 2609948.2103 | 1191757.7624
119 | 2609946.8043 | 1191757.749
120 | 2609934.1225 | 1191756.769
121 | 2609904.7979 | 1191751.5028
122 | 2609976.4484 | 1191856.8652
123 | 2609975.0066 | 1191841.4668
124 | 2609971.258 | 1191870.0765
125 | 2609955.9245 | 1191833.8376
126 | 2609968.6185 | 1191876.7952
127 | 2609955.185 | 1191833.542
128 | 2610030.4248 | 1191903.9962
129 | 2610055.4046 | 1191910.5911
130 | 2610016.4609 | 1191900.3097
131 | 2610043.7939 | 1191932.3509
132 | 2610008.5583 | 1191919.1935
133 | 2609999.6977 | 1191895.7982
134 | 2610029.2477 | 1191962.5192
135 | 2610004.0846 | 1191929.8836
136 | 2609989.8147 | 1191893.1385
137 | 2610026.1651 | 1191968.5621
138 | 2610000.2063 | 1191939.151
139 | 2609974.9458 | 1191889.1369
140 | 2610019.9422 | 1191980.7614
141 | 2609964.8384 | 1191886.4167
142 | 2609985.8872 | 1191973.6734
143 | 2609983.758 | 1191978.9604
144 | 2609974.4272 | 1192002.1286
145 | 2609966.7021 | 1192022.3469
146 | 2609946.4762 | 1191880.9168
147 | 2609940.547 | 1191894.8053
148 | 2609923.3693 | 1191872.6521
149 | 2609940.3782 | 1191895.2007
150 | 2609916.7755 | 1191888.4363
151 | 2609917.7382 | 1191869.6687
152 | 2609910.4983 | 1191815.6758
153 | 2609922.6478 | 1191820.5333
154 | 2609905.2162 | 1191813.564
155 | 2609928.3076 | 1191822.7961
156 | 2609899.5456 | 1191811.2968
157 | 2609933.2238 | 1191824.7617
158 | 2609887.7031 | 1191806.5621
159 | 2609882.5598 | 1191804.5057
160 | 2609877.0275 | 1191802.2939
161 | 2609854.1438 | 1191793.1448
162 | 2609914.2331 | 1191988.6065
163 | 2610014.037 | 1191992.3376
164 | 2610004.2738 | 1192011.4769
165 | 2609865.0477 | 1191797.5042
166 | 2609859.8061 | 1191795.4086
167 | 2609908.2723 | 1191908.7909
168 | 2610003.3141 | 1192013.3584
169 | 2609985.3073 | 1192025.3716
170 | 2609938.3568 | 1191899.9356
171 | 2609966.1247 | 1192023.7214
172 | 2609917.7143 | 1192006.0685
173 | 2609848.87 | 1191835.288

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1