## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_62-43_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_62-43_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_62-43_0_5_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_62-43_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_62-43_0_5_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_62-43_0_5_node_97 | 0.4 | n |  | TRUE
6 | bus_LV_62-43_0_5_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_62-43_0_5_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_62-43_0_5_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_62-43_0_5_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_62-43_0_5_node_90 | 0.4 | n |  | TRUE
11 | bus_LV_62-43_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_62-43_0_5_node_75 | 0.4 | n |  | TRUE
13 | bus_LV_62-43_0_5_node_73 | 0.4 | n |  | TRUE
14 | bus_LV_62-43_0_5_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_62-43_0_5_node_67 | 0.4 | n |  | TRUE
16 | bus_LV_62-43_0_5_node_78 | 0.4 | n |  | TRUE
17 | bus_LV_62-43_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_62-43_0_5_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_62-43_0_5_node_65 | 0.4 | n |  | TRUE
20 | bus_LV_62-43_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_62-43_0_5_node_46 | 0.4 | n |  | TRUE
22 | bus_LV_62-43_0_5_node_83 | 0.4 | n |  | TRUE
23 | bus_LV_62-43_0_5_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_62-43_0_5_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_62-43_0_5_node_63 | 0.4 | n |  | TRUE
26 | bus_LV_62-43_0_5_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_62-43_0_5_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_62-43_0_5_node_41 | 0.4 | n |  | TRUE
29 | bus_LV_62-43_0_5_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_62-43_0_5_node_94 | 0.4 | n |  | TRUE
31 | bus_LV_62-43_0_5_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_62-43_0_5_node_93 | 0.4 | n |  | TRUE
33 | bus_LV_62-43_0_5_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_62-43_0_5_node_55 | 0.4 | n |  | TRUE
35 | bus_LV_62-43_0_5_node_52 | 0.4 | n |  | TRUE
36 | bus_LV_62-43_0_5_node_81 | 0.4 | n |  | TRUE
37 | bus_LV_62-43_0_5_node_91 | 0.4 | n |  | TRUE
38 | bus_LV_62-43_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_62-43_0_5_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_62-43_0_5_node_82 | 0.4 | n |  | TRUE
41 | bus_LV_62-43_0_5_node_88 | 0.4 | n |  | TRUE
42 | bus_LV_62-43_0_5_node_20 | 0.4 | n |  | TRUE
43 | bus_LV_62-43_0_5_node_72 | 0.4 | n |  | TRUE
44 | bus_LV_62-43_0_5_node_74 | 0.4 | n |  | TRUE
45 | bus_LV_62-43_0_5_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_62-43_0_5_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_62-43_0_5_node_57 | 0.4 | n |  | TRUE
48 | bus_LV_62-43_0_5_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_62-43_0_5_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_62-43_0_5_node_96 | 0.4 | n |  | TRUE
51 | bus_LV_62-43_0_5_node_76 | 0.4 | n |  | TRUE
52 | bus_LV_62-43_0_5_node_77 | 0.4 | n |  | TRUE
53 | bus_LV_62-43_0_5_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_62-43_0_5_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_62-43_0_5_node_66 | 0.4 | n |  | TRUE
56 | bus_LV_62-43_0_5_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_62-43_0_5_node_84 | 0.4 | n |  | TRUE
58 | bus_LV_62-43_0_5_node_32 | 0.4 | n |  | TRUE
59 | bus_LV_62-43_0_5_node_29 | 0.4 | n |  | TRUE
60 | bus_LV_62-43_0_5_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_62-43_0_5_node_95 | 0.4 | n |  | TRUE
62 | bus_LV_62-43_0_5_node_64 | 0.4 | n |  | TRUE
63 | bus_LV_62-43_0_5_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_62-43_0_5_node_80 | 0.4 | n |  | TRUE
65 | bus_LV_62-43_0_5_node_71 | 0.4 | n |  | TRUE
66 | bus_LV_62-43_0_5_node_87 | 0.4 | n |  | TRUE
67 | bus_LV_62-43_0_5_node_70 | 0.4 | n |  | TRUE
68 | bus_LV_62-43_0_5_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_62-43_0_5_node_92 | 0.4 | n |  | TRUE
70 | bus_LV_62-43_0_5_node_79 | 0.4 | n |  | TRUE
71 | bus_LV_62-43_0_5_node_89 | 0.4 | n |  | TRUE
72 | bus_LV_62-43_0_5_node_28 | 0.4 | n |  | TRUE
73 | bus_LV_62-43_0_5_node_31 | 0.4 | n |  | TRUE
74 | bus_LV_62-43_0_5_node_98 | 0.4 | n |  | TRUE
75 | bus_LV_62-43_0_5_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_62-43_0_5_node_49 | 0.4 | n |  | TRUE
77 | bus_LV_62-43_0_5_node_86 | 0.4 | n |  | TRUE
78 | bus_LV_62-43_0_5_node_47 | 0.4 | n |  | TRUE
79 | bus_LV_62-43_0_5_node_48 | 0.4 | n |  | TRUE
80 | bus_LV_62-43_0_5_node_50 | 0.4 | n |  | TRUE
81 | bus_LV_62-43_0_5_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_62-43_0_5_node_59 | 0.4 | n |  | TRUE
83 | bus_LV_62-43_0_5_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_62-43_0_5_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_62-43_0_5_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_62-43_0_5_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_62-43_0_5_node_85 | 0.4 | n |  | TRUE
88 | bus_MV_640_0_node_63 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_62-43_0_5_load_0 | 0 | 0.0012761 | 0.00031982 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_62-43_0_5_load_97 | 5 | 0.035378 | 0.0088665 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_62-43_0_5_load_39 | 7 | 0.0011383 | 0.00028529 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_62-43_0_5_load_37 | 8 | 0.0034026 | 0.00085276 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_62-43_0_5_load_90 | 10 | 0.0028689 | 0.00071901 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_62-43_0_5_load_75 | 12 | 0.0035376 | 0.00088661 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_62-43_0_5_load_73 | 13 | 0.0051046 | 0.0012793 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_62-43_0_5_load_67 | 15 | 0.0043672 | 0.0010945 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_62-43_0_5_load_78 | 16 | 0.0049622 | 0.0012436 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_62-43_0_5_load_65 | 19 | 0.0072845 | 0.0018257 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_62-43_0_5_load_83 | 22 | 0.0031773 | 0.00079631 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_62-43_0_5_load_63 | 25 | 0.0028447 | 0.00071295 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_62-43_0_5_load_43 | 27 | 0.0066842 | 0.0016752 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_62-43_0_5_load_41 | 28 | 0.030161 | 0.007559 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_62-43_0_5_load_94 | 30 | 0.0065918 | 0.0016521 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_62-43_0_5_load_93 | 32 | 0.0065929 | 0.0016523 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_62-43_0_5_load_55 | 34 | 0.0052163 | 0.0013073 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_62-43_0_5_load_52 | 35 | 0.0014833 | 0.00037176 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_62-43_0_5_load_81 | 36 | 0.007338 | 0.0018391 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_62-43_0_5_load_91 | 37 | 0.0028692 | 0.00071909 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_62-43_0_5_load_88 | 41 | 0.014177 | 0.0035531 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_62-43_0_5_load_74 | 44 | 0.004976 | 0.0012471 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_62-43_0_5_load_57 | 47 | 0.0037556 | 0.00094124 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_62-43_0_5_load_44 | 48 | 0.0031779 | 0.00079646 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_62-43_0_5_load_42 | 49 | 0.045356 | 0.011367 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_62-43_0_5_load_96 | 50 | 0.0065921 | 0.0016521 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_62-43_0_5_load_76 | 51 | 0.0035821 | 0.00089777 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_62-43_0_5_load_77 | 52 | 0.0048589 | 0.0012177 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_62-43_0_5_load_51 | 53 | 0.0029863 | 0.00074845 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_62-43_0_5_load_38 | 54 | 0.0011395 | 0.00028559 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_62-43_0_5_load_66 | 55 | 0.0074839 | 0.0018756 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_62-43_0_5_load_45 | 56 | 0.0029721 | 0.00074489 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_62-43_0_5_load_84 | 57 | 0.0031773 | 0.00079631 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_62-43_0_5_load_62 | 60 | 0.0039893 | 0.00099982 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_62-43_0_5_load_95 | 61 | 0.006591 | 0.0016519 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_62-43_0_5_load_64 | 62 | 0.0048312 | 0.0012108 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_62-43_0_5_load_53 | 63 | 0.0040677 | 0.0010195 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_62-43_0_5_load_80 | 64 | 0.0026886 | 0.00067382 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_62-43_0_5_load_71 | 65 | 0.0055089 | 0.0013806 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_62-43_0_5_load_87 | 66 | 0.0076343 | 0.0019133 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_62-43_0_5_load_70 | 67 | 0.0054679 | 0.0013704 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_62-43_0_5_load_56 | 68 | 0.0040319 | 0.0010105 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_62-43_0_5_load_92 | 69 | 0.0031777 | 0.00079641 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_62-43_0_5_load_79 | 70 | 0.0026922 | 0.00067473 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_62-43_0_5_load_89 | 71 | 0.0074968 | 0.0018789 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_62-43_0_5_load_28 | 72 | 0.00093919 | 0.00023538 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_62-43_0_5_load_98 | 74 | 0.011279 | 0.0028267 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_62-43_0_5_load_61 | 75 | 0.0039486 | 0.00098962 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_62-43_0_5_load_49 | 76 | 0.0029934 | 0.00075023 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_62-43_0_5_load_86 | 77 | 0.0056306 | 0.0014112 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_62-43_0_5_load_47 | 78 | 0.00088104 | 0.00022081 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_62-43_0_5_load_48 | 79 | 0.0029863 | 0.00074844 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_62-43_0_5_load_50 | 80 | 0.0054252 | 0.0013597 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_62-43_0_5_load_58 | 81 | 0.0010603 | 0.00026575 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_62-43_0_5_load_59 | 82 | 0.0066307 | 0.0016618 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_62-43_0_5_load_54 | 83 | 0.0037701 | 0.00094486 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_62-43_0_5_load_60 | 84 | 0.0071574 | 0.0017938 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_62-43_0_5_load_68 | 85 | 0.0043672 | 0.0010945 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_62-43_0_5_load_69 | 86 | 0.0055067 | 0.0013801 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_62-43_0_5_load_85 | 87 | 0.0056289 | 0.0014107 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_62-43_0_5_line_0 |  | 0 | 1 | 0.087449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_62-43_0_5_line_1 |  | 1 | 2 | 0.1343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_62-43_0_5_line_2 |  | 2 | 9 | 0.023154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_62-43_0_5_line_3 |  | 2 | 10 | 0.0063107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_62-43_0_5_line_4 |  | 3 | 4 | 0.10554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_62-43_0_5_line_5 |  | 3 | 5 | 0.036996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_62-43_0_5_line_6 |  | 4 | 48 | 0.025497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_62-43_0_5_line_7 |  | 4 | 49 | 0.051668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_62-43_0_5_line_8 |  | 5 | 9 | 0.0081322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_62-43_0_5_line_9 |  | 6 | 7 | 0.035443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_62-43_0_5_line_10 |  | 6 | 8 | 0.041433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_62-43_0_5_line_11 |  | 7 | 53 | 0.035012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_62-43_0_5_line_12 |  | 8 | 54 | 0.01258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_62-43_0_5_line_13 |  | 10 | 37 | 0.023317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_62-43_0_5_line_14 |  | 11 | 12 | 0.0062265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_62-43_0_5_line_15 |  | 11 | 13 | 0.013964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_62-43_0_5_line_16 |  | 12 | 51 | 0.017387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_62-43_0_5_line_17 |  | 13 | 44 | 0.018244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_62-43_0_5_line_18 |  | 14 | 15 | 0.0062684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_62-43_0_5_line_19 |  | 14 | 16 | 0.032717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_62-43_0_5_line_20 |  | 15 | 17 | 0.010313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_62-43_0_5_line_21 |  | 16 | 52 | 0.01823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_62-43_0_5_line_22 |  | 17 | 18 | 0.010611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_62-43_0_5_line_23 |  | 17 | 19 | 0.017273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_62-43_0_5_line_24 |  | 18 | 38 | 0.00429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_62-43_0_5_line_25 |  | 18 | 32 | 0.040283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_62-43_0_5_line_26 |  | 19 | 55 | 0.018293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_62-43_0_5_line_27 |  | 20 | 21 | 0.020454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_62-43_0_5_line_28 |  | 20 | 22 | 0.036688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_62-43_0_5_line_29 |  | 21 | 56 | 0.023909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_62-43_0_5_line_30 |  | 21 | 27 | 0.022415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_62-43_0_5_line_31 |  | 22 | 57 | 0.021177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_62-43_0_5_line_32 |  | 23 | 24 | 0.034715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_62-43_0_5_line_33 |  | 23 | 25 | 0.043896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_62-43_0_5_line_34 |  | 24 | 60 | 0.038874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_62-43_0_5_line_35 |  | 25 | 45 | 0.025521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_62-43_0_5_line_36 |  | 26 | 27 | 0.0091203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_62-43_0_5_line_37 |  | 26 | 28 | 0.0056872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_62-43_0_5_line_38 |  | 28 | 49 | 0.0094022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_62-43_0_5_line_39 |  | 29 | 30 | 0.014642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_62-43_0_5_line_40 |  | 29 | 31 | 0.011677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_62-43_0_5_line_41 |  | 29 | 32 | 0.029246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_62-43_0_5_line_42 |  | 30 | 61 | 0.042716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_62-43_0_5_line_43 |  | 31 | 36 | 0.01684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_62-43_0_5_line_44 |  | 31 | 37 | 0.030253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_62-43_0_5_line_45 |  | 33 | 34 | 0.003916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_62-43_0_5_line_46 |  | 33 | 35 | 0.0042802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_62-43_0_5_line_47 |  | 34 | 62 | 0.0093583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_62-43_0_5_line_48 |  | 35 | 63 | 0.017277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_62-43_0_5_line_49 |  | 36 | 64 | 0.025393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_62-43_0_5_line_50 |  | 38 | 50 | 0.026877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_62-43_0_5_line_51 |  | 39 | 40 | 0.026606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_62-43_0_5_line_52 |  | 39 | 41 | 0.015734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_62-43_0_5_line_53 |  | 40 | 65 | 0.043917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_62-43_0_5_line_54 |  | 41 | 66 | 0.018065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_62-43_0_5_line_55 |  | 42 | 43 | 0.005808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_62-43_0_5_line_56 |  | 42 | 44 | 0.035023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_62-43_0_5_line_57 |  | 43 | 67 | 0.030889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_62-43_0_5_line_58 |  | 45 | 46 | 0.04383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_62-43_0_5_line_59 |  | 45 | 47 | 0.035502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_62-43_0_5_line_60 |  | 46 | 51 | 0.016925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_62-43_0_5_line_61 |  | 46 | 52 | 0.01627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_62-43_0_5_line_62 |  | 47 | 68 | 0.0045532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_62-43_0_5_line_63 |  | 48 | 69 | 0.021114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_62-43_0_5_line_64 |  | 53 | 76 | 0.007052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_62-43_0_5_line_65 |  | 54 | 58 | 0.15974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_62-43_0_5_line_66 |  | 58 | 59 | 0.042034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_62-43_0_5_line_67 |  | 59 | 73 | 0.041396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_62-43_0_5_line_68 |  | 59 | 72 | 0.045982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_62-43_0_5_line_69 |  | 60 | 75 | 0.043849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_62-43_0_5_line_70 |  | 62 | 84 | 0.028088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_62-43_0_5_line_71 |  | 63 | 83 | 0.0034898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_62-43_0_5_line_72 |  | 64 | 70 | 0.00071737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_62-43_0_5_line_73 |  | 65 | 86 | 0.018366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_62-43_0_5_line_74 |  | 66 | 71 | 0.0081479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_62-43_0_5_line_75 |  | 67 | 85 | 0.0030067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_62-43_0_5_line_76 |  | 68 | 83 | 0.028237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_62-43_0_5_line_77 |  | 69 | 77 | 0.035102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_62-43_0_5_line_78 |  | 73 | 74 | 0.0038353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_62-43_0_5_line_79 |  | 76 | 78 | 0.011273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_62-43_0_5_line_80 |  | 77 | 87 | 0.023956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_62-43_0_5_line_81 |  | 78 | 79 | 0.016619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_62-43_0_5_line_82 |  | 79 | 80 | 0.007159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_62-43_0_5_line_83 |  | 80 | 81 | 0.012569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_62-43_0_5_line_84 |  | 81 | 82 | 0.018061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_62-43_0_5_line_85 |  | 82 | 84 | 0.0095482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_62-43_0_5_line_86 |  | 85 | 86 | 0.01528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_62-43_0_5_trafo_44 | 0.63 MVA 20/0.4 kV | 88 | 48 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2686703.9964 | 1255702.1195 | 2686711.9095 | 1255695.408 | 2686728.5041 | 1255684.6316 | 2686742.5624 | 1255678.088 | 2686757.599 | 1255672.226 | 2686780.6774 | 1255666.3151 | 2686782.4899 | 1255666.175
1 | 2686703.9964 | 1255702.1195 | 2686653.0118 | 1255656.2936 | 2686665.7786 | 1255641.6247 | 2686696.8467 | 1255607.2975
2 | 2686677.0784 | 1255601.4481 | 2686679.8797 | 1255602.8124 | 2686683.0329 | 1255603.3145 | 2686686.2701 | 1255602.7281 | 2686689.6923 | 1255600.8323 | 2686693.7496 | 1255604.5056 | 2686696.8467 | 1255607.2975
3 | 2686696.8467 | 1255607.2975 | 2686701.0927 | 1255602.6289
4 | 2686636.4741 | 1255583.329 | 2686629.3552 | 1255582.6799 | 2686622.2943 | 1255582.6989 | 2686623.7064 | 1255578.9944 | 2686623.4242 | 1255573.0191 | 2686624.7797 | 1255568.5355 | 2686626.8677 | 1255564.5185 | 2686629.313 | 1255561.3407 | 2686671.7412 | 1255507.9871
5 | 2686636.4741 | 1255583.329 | 2686639.3007 | 1255584.5046 | 2686643.3879 | 1255585.1093 | 2686650.8314 | 1255586.775 | 2686657.0374 | 1255588.9786 | 2686663.7268 | 1255592.179 | 2686670.795 | 1255596.2855
6 | 2686671.7412 | 1255507.9871 | 2686687.6114 | 1255488.0319
7 | 2686671.7412 | 1255507.9871 | 2686620.2544 | 1255512.315
8 | 2686677.0784 | 1255601.4481 | 2686670.795 | 1255596.2855
9 | 2686554.0444 | 1255467.546 | 2686565.7233 | 1255462.7908 | 2686586.3868 | 1255453.0755
10 | 2686554.0444 | 1255467.546 | 2686554.1785 | 1255452.7032 | 2686558.5343 | 1255426.4726
11 | 2686586.3868 | 1255453.0755 | 2686618.0716 | 1255438.1784
12 | 2686558.5343 | 1255426.4726 | 2686560.595 | 1255414.0627
13 | 2686701.0927 | 1255602.6289 | 2686716.7811 | 1255585.3789
14 | 2686767.7498 | 1255403.8241 | 2686769.6475 | 1255403.0179 | 2686773.801 | 1255402.7119
15 | 2686767.7498 | 1255403.8241 | 2686766.3076 | 1255404.4368 | 2686763.398 | 1255407.8857 | 2686761.1106 | 1255412.6336 | 2686760.2446 | 1255415.1006
16 | 2686773.801 | 1255402.7119 | 2686780.9467 | 1255405.6633 | 2686790.2158 | 1255408.3679
17 | 2686760.2446 | 1255415.1006 | 2686759.7469 | 1255417.6619 | 2686758.3629 | 1255424.0799 | 2686756.9951 | 1255429.3862 | 2686755.5664 | 1255432.6789
18 | 2686784.1653 | 1255478.3663 | 2686782.1108 | 1255484.2885
19 | 2686784.1653 | 1255478.3663 | 2686792.0011 | 1255454.8297 | 2686794.5912 | 1255447.3559
20 | 2686778.7306 | 1255494.032 | 2686782.1108 | 1255484.2885
21 | 2686800.5604 | 1255430.1313 | 2686794.5912 | 1255447.3559
22 | 2686778.7306 | 1255494.032 | 2686784.0449 | 1255497.3791 | 2686787.7073 | 1255499.6901
23 | 2686778.7306 | 1255494.032 | 2686770.0646 | 1255508.974
24 | 2686787.7073 | 1255499.6901 | 2686790.0607 | 1255496.0996
25 | 2686787.7073 | 1255499.6901 | 2686775.9865 | 1255517.5766 | 2686770.795 | 1255524.895 | 2686765.6102 | 1255531.235 | 2686764.4536 | 1255532.5283
26 | 2686770.0646 | 1255508.974 | 2686769.3431 | 1255510.218 | 2686760.024 | 1255522.7689 | 2686759.2234 | 1255523.6926
27 | 2686615.2375 | 1255465.9616 | 2686612.9703 | 1255445.6351
28 | 2686612.9703 | 1255445.6351 | 2686646.2674 | 1255430.2311
29 | 2686615.2375 | 1255465.9616 | 2686608.6109 | 1255470.3236 | 2686592.7182 | 1255471.9515
30 | 2686615.2375 | 1255465.9616 | 2686617.7157 | 1255488.239
31 | 2686646.2674 | 1255430.2311 | 2686665.4877 | 1255421.3394
32 | 2686847.2515 | 1255313.3421 | 2686844.7554 | 1255308.6575 | 2686842.8109 | 1255298.2543 | 2686839.3869 | 1255290.487 | 2686833.7966 | 1255281.7762
33 | 2686847.2515 | 1255313.3421 | 2686831.2203 | 1255354.2061
34 | 2686833.7966 | 1255281.7762 | 2686797.7497 | 1255278.3785 | 2686795.1115 | 1255277.9878
35 | 2686821.8997 | 1255377.9645 | 2686831.2203 | 1255354.2061
36 | 2686618.724 | 1255497.3033 | 2686617.7157 | 1255488.239
37 | 2686618.724 | 1255497.3033 | 2686619.3008 | 1255502.9612
38 | 2686619.3008 | 1255502.9612 | 2686620.2544 | 1255512.315 | 2686620.2544 | 1255512.315
39 | 2686744.9573 | 1255554.328 | 2686748.6611 | 1255561.0207 | 2686753.2613 | 1255566.287
40 | 2686737.136 | 1255562.9979 | 2686740.5324 | 1255559.267 | 2686744.9573 | 1255554.328
41 | 2686744.9573 | 1255554.328 | 2686764.4536 | 1255532.5283
42 | 2686753.2613 | 1255566.287 | 2686762.0818 | 1255576.3847 | 2686767.0993 | 1255579.9053 | 2686771.2216 | 1255581.7115 | 2686777.7368 | 1255583.4083 | 2686784.6026 | 1255583.8315 | 2686789.6034 | 1255583.0126
43 | 2686737.136 | 1255562.9979 | 2686744.3703 | 1255567.6185 | 2686749.7407 | 1255573.8891
44 | 2686737.136 | 1255562.9979 | 2686716.7811 | 1255585.3789
45 | 2686730.3097 | 1255386.4179 | 2686726.6587 | 1255387.834
46 | 2686730.3097 | 1255386.4179 | 2686734.336 | 1255384.9654
47 | 2686726.6587 | 1255387.834 | 2686717.9337 | 1255391.218
48 | 2686750.7032 | 1255379.4428 | 2686742.2465 | 1255382.1116 | 2686734.336 | 1255384.9654
49 | 2686768.2739 | 1255590.8532 | 2686762.9686 | 1255587.9287 | 2686758.2389 | 1255583.8118 | 2686749.7407 | 1255573.8891
50 | 2686790.0607 | 1255496.0996 | 2686803.7519 | 1255519.2514
51 | 2686672.3364 | 1255519.3713 | 2686681.0964 | 1255508.4133 | 2686688.9651 | 1255498.5653
52 | 2686672.3364 | 1255519.3713 | 2686685.5165 | 1255527.9647
53 | 2686688.9651 | 1255498.5653 | 2686714.0825 | 1255507.9847 | 2686722.4692 | 1255493.092
54 | 2686701.8637 | 1255534.137 | 2686701.8637 | 1255534.137 | 2686694.3191 | 1255533.704 | 2686685.5165 | 1255527.9647
55 | 2686727.8713 | 1255442.1361 | 2686729.2587 | 1255438.5759 | 2686729.8297 | 1255436.6717
56 | 2686729.8297 | 1255436.6717 | 2686738.2151 | 1255439.9637 | 2686749.9711 | 1255443.3496 | 2686751.8086 | 1255443.5655 | 2686753.3949 | 1255442.3879 | 2686753.8777 | 1255440.8382 | 2686755.5664 | 1255432.6789
57 | 2686727.8713 | 1255442.1361 | 2686745.6512 | 1255451.9262 | 2686740.4539 | 1255461.1553
58 | 2686821.8997 | 1255377.9645 | 2686820.7939 | 1255381.3509 | 2686818.4484 | 1255388.5109 | 2686814.9288 | 1255387.2583 | 2686814.8568 | 1255388.5694 | 2686814.4349 | 1255390.0755 | 2686805.8881 | 1255414.758
59 | 2686821.8997 | 1255377.9645 | 2686801.3711 | 1255375.5617 | 2686788.7802 | 1255374.5765 | 2686786.5804 | 1255374.7072
60 | 2686805.8881 | 1255414.758 | 2686790.2158 | 1255408.3679
61 | 2686805.8881 | 1255414.758 | 2686800.5604 | 1255430.1313
62 | 2686786.5804 | 1255374.7072 | 2686782.0353 | 1255374.9774
63 | 2686700.7539 | 1255471.5064 | 2686687.6114 | 1255488.0319
64 | 2686624.4534 | 1255435.1779 | 2686618.0716 | 1255438.1784
65 | 2686500.7633 | 1255280.8244 | 2686513.294 | 1255294.1954 | 2686531.4208 | 1255313.8531 | 2686556.8421 | 1255331.9607 | 2686563.6378 | 1255351.1191 | 2686563.118 | 1255396.9689 | 2686562.6739 | 1255401.5437 | 2686560.595 | 1255414.0627
66 | 2686473.9854 | 1255261.0515 | 2686470.8716 | 1255270.7357 | 2686480.3811 | 1255276.112 | 2686493.8525 | 1255278.8108 | 2686500.7633 | 1255280.8244
67 | 2686437.6455 | 1255241.0279 | 2686473.9854 | 1255261.0515
68 | 2686473.9854 | 1255261.0515 | 2686480.1361 | 1255239.1912 | 2686486.6788 | 1255216.8573
69 | 2686751.5615 | 1255273.4867 | 2686768.5812 | 1255274.0589 | 2686795.1115 | 1255277.9878
70 | 2686717.9337 | 1255391.218 | 2686712.132 | 1255393.4683 | 2686692.4016 | 1255402.8905
71 | 2686750.7032 | 1255379.4428 | 2686754.0313 | 1255378.3925 | 2686754.0313 | 1255378.3925
72 | 2686768.971 | 1255591.0226 | 2686768.2739 | 1255590.8532 | 2686768.2739 | 1255590.8532
73 | 2686731.4812 | 1255477.0888 | 2686722.4692 | 1255493.092
74 | 2686701.8637 | 1255534.137 | 2686708.6832 | 1255538.24 | 2686708.7532 | 1255538.4158
75 | 2686738.9786 | 1255463.7752 | 2686740.4539 | 1255461.1553
76 | 2686754.0313 | 1255378.3925 | 2686764.8681 | 1255376.561 | 2686774.6765 | 1255375.4149 | 2686782.0353 | 1255374.9774
77 | 2686719.3438 | 1255441.9009 | 2686716.0493 | 1255448.9237 | 2686712.638 | 1255455.2119 | 2686707.9222 | 1255462.4929 | 2686700.7539 | 1255471.5064
78 | 2686437.6455 | 1255241.0279 | 2686434.1532 | 1255239.4424
79 | 2686624.4534 | 1255435.1779 | 2686632.2393 | 1255431.5172 | 2686634.6661 | 1255430.4049
80 | 2686726.2675 | 1255419.0341 | 2686723.7932 | 1255430.1004 | 2686719.9504 | 1255440.6078 | 2686719.3438 | 1255441.9009
81 | 2686649.6849 | 1255423.2899 | 2686637.6466 | 1255429.0388 | 2686634.6661 | 1255430.4049
82 | 2686649.6849 | 1255423.2899 | 2686656.1451 | 1255420.2048
83 | 2686667.4874 | 1255414.7883 | 2686656.1451 | 1255420.2048
84 | 2686667.4874 | 1255414.7883 | 2686683.7855 | 1255407.0052
85 | 2686683.7855 | 1255407.0052 | 2686692.4016 | 1255402.8905
86 | 2686738.9786 | 1255463.7752 | 2686731.4812 | 1255477.0888

## bus_geodata
| x | y | coords
0 | 2686782.4899 | 1255666.175
1 | 2686703.9964 | 1255702.1195
2 | 2686696.8467 | 1255607.2975
3 | 2686636.4741 | 1255583.329
4 | 2686671.7412 | 1255507.9872
5 | 2686670.795 | 1255596.2855
6 | 2686554.0444 | 1255467.546
7 | 2686586.3868 | 1255453.0755
8 | 2686558.5343 | 1255426.4726
9 | 2686677.0784 | 1255601.4481
10 | 2686701.0927 | 1255602.6289
11 | 2686767.7498 | 1255403.8241
12 | 2686773.801 | 1255402.7119
13 | 2686760.2446 | 1255415.1006
14 | 2686784.1653 | 1255478.3663
15 | 2686782.1108 | 1255484.2885
16 | 2686794.5912 | 1255447.3559
17 | 2686778.7306 | 1255494.032
18 | 2686787.7073 | 1255499.6901
19 | 2686770.0646 | 1255508.974
20 | 2686612.9703 | 1255445.6351
21 | 2686615.2375 | 1255465.9616
22 | 2686646.2674 | 1255430.2311
23 | 2686847.2515 | 1255313.3421
24 | 2686833.7966 | 1255281.7762
25 | 2686831.2203 | 1255354.2061
26 | 2686618.724 | 1255497.3033
27 | 2686617.7157 | 1255488.239
28 | 2686619.3008 | 1255502.9612
29 | 2686744.9573 | 1255554.328
30 | 2686753.2613 | 1255566.287
31 | 2686737.136 | 1255562.9979
32 | 2686764.4536 | 1255532.5283
33 | 2686730.3097 | 1255386.4179
34 | 2686726.6587 | 1255387.834
35 | 2686734.336 | 1255384.9654
36 | 2686749.7407 | 1255573.8891
37 | 2686716.7811 | 1255585.3789
38 | 2686790.0607 | 1255496.0996
39 | 2686672.3364 | 1255519.3713
40 | 2686688.9651 | 1255498.5653
41 | 2686685.5165 | 1255527.9647
42 | 2686729.8297 | 1255436.6717
43 | 2686727.8713 | 1255442.1361
44 | 2686755.5664 | 1255432.6789
45 | 2686821.8997 | 1255377.9645
46 | 2686805.8881 | 1255414.758
47 | 2686786.5804 | 1255374.7072
48 | 2686687.6114 | 1255488.0319
49 | 2686620.2544 | 1255512.315
50 | 2686803.7519 | 1255519.2514
51 | 2686790.2158 | 1255408.3679
52 | 2686800.5604 | 1255430.1313
53 | 2686618.0716 | 1255438.1784
54 | 2686560.595 | 1255414.0627
55 | 2686759.2234 | 1255523.6926
56 | 2686592.7182 | 1255471.9515
57 | 2686665.4877 | 1255421.3394
58 | 2686500.7633 | 1255280.8244
59 | 2686473.9854 | 1255261.0515
60 | 2686795.1115 | 1255277.9878
61 | 2686789.6034 | 1255583.0126
62 | 2686717.9337 | 1255391.218
63 | 2686750.7032 | 1255379.4428
64 | 2686768.2739 | 1255590.8532
65 | 2686722.4692 | 1255493.092
66 | 2686701.8637 | 1255534.137
67 | 2686740.4539 | 1255461.1553
68 | 2686782.0353 | 1255374.9774
69 | 2686700.7539 | 1255471.5064
70 | 2686768.971 | 1255591.0226
71 | 2686708.7532 | 1255538.4158
72 | 2686486.6788 | 1255216.8573
73 | 2686437.6455 | 1255241.0279
74 | 2686434.1532 | 1255239.4424
75 | 2686751.5615 | 1255273.4867
76 | 2686624.4534 | 1255435.1779
77 | 2686719.3438 | 1255441.9009
78 | 2686634.6661 | 1255430.4049
79 | 2686649.6849 | 1255423.2899
80 | 2686656.1451 | 1255420.2048
81 | 2686667.4874 | 1255414.7883
82 | 2686683.7855 | 1255407.0052
83 | 2686754.0313 | 1255378.3925
84 | 2686692.4016 | 1255402.8905
85 | 2686738.9786 | 1255463.7752
86 | 2686731.4812 | 1255477.0888
87 | 2686726.2675 | 1255419.0341
88 | 2686671.7412 | 1255507.9872

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1