## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6607-9_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6607-9_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_6607-9_0_2_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_6607-9_0_2_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_6607-9_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6607-9_0_2_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_6607-9_0_2_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_6607-9_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_6607-9_0_2_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_6607-9_0_2_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_6607-9_0_2_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_6607-9_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_6607-9_0_2_node_32 | 0.4 | n |  | TRUE
13 | bus_LV_6607-9_0_2_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_6607-9_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_6607-9_0_2_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_6607-9_0_2_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_6607-9_0_2_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_6607-9_0_2_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_6607-9_0_2_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_6607-9_0_2_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_6607-9_0_2_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_6607-9_0_2_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_6607-9_0_2_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_6607-9_0_2_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_6607-9_0_2_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_6607-9_0_2_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_6607-9_0_2_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_6607-9_0_2_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_6607-9_0_2_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_6607-9_0_2_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_6607-9_0_2_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_6607-9_0_2_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_6607-9_0_2_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_6607-9_0_2_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_6607-9_0_2_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_6607-9_0_2_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_6607-9_0_2_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_6607-9_0_2_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_6607-9_0_2_node_38 | 0.4 | n |  | TRUE
40 | bus_MV_458_0_node_123 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6607-9_0_2_load_0 | 0 | 0.037037 | 0.0092823 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6607-9_0_2_load_40 | 5 | 0.020365 | 0.0051039 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6607-9_0_2_load_27 | 10 | 0.00016383 | 4.1059e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6607-9_0_2_load_32 | 12 | 0.0045473 | 0.0011396 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6607-9_0_2_load_30 | 15 | 0.018659 | 0.0046763 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6607-9_0_2_load_25 | 17 | 0.00078515 | 0.00019678 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6607-9_0_2_load_23 | 18 | 0.0014784 | 0.00037053 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6607-9_0_2_load_24 | 19 | 0.00097734 | 0.00024494 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6607-9_0_2_load_20 | 20 | 0.028436 | 0.0071267 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6607-9_0_2_load_29 | 21 | 0.034224 | 0.0085775 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6607-9_0_2_load_39 | 22 | 0.051549 | 0.01292 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6607-9_0_2_load_33 | 23 | 0.00029658 | 7.4331e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6607-9_0_2_load_28 | 26 | 0.072845 | 0.018257 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6607-9_0_2_load_37 | 29 | 0.0089687 | 0.0022478 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6607-9_0_2_load_36 | 31 | 0.0020764 | 0.0005204 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6607-9_0_2_load_31 | 33 | 0.0066573 | 0.0016685 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6607-9_0_2_load_26 | 34 | 5.9076e-05 | 1.4806e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6607-9_0_2_load_21 | 35 | 0.027398 | 0.0068666 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6607-9_0_2_load_22 | 37 | 0.0057776 | 0.001448 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6607-9_0_2_load_38 | 39 | 0.0034428 | 0.00086286 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6607-9_0_2_line_0 |  | 0 | 1 | 0.01818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6607-9_0_2_line_1 |  | 1 | 2 | 0.010095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6607-9_0_2_line_2 |  | 2 | 3 | 0.07945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6607-9_0_2_line_3 |  | 3 | 22 | 0.016682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_6607-9_0_2_line_4 |  | 3 | 4 | 0.004188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_6607-9_0_2_line_5 |  | 3 | 9 | 0.079877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6607-9_0_2_line_6 |  | 4 | 5 | 0.016636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6607-9_0_2_line_7 |  | 4 | 6 | 0.074344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6607-9_0_2_line_8 |  | 6 | 21 | 0.013744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6607-9_0_2_line_9 |  | 6 | 11 | 0.021647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6607-9_0_2_line_10 |  | 7 | 8 | 0.011004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6607-9_0_2_line_11 |  | 7 | 9 | 0.11585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6607-9_0_2_line_12 |  | 7 | 10 | 0.078591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6607-9_0_2_line_13 |  | 8 | 23 | 0.13157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6607-9_0_2_line_14 |  | 8 | 13 | 0.037939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6607-9_0_2_line_15 |  | 9 | 19 | 0.0095881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6607-9_0_2_line_16 |  | 10 | 34 | 0.030441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6607-9_0_2_line_17 |  | 11 | 12 | 0.04818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6607-9_0_2_line_18 |  | 12 | 28 | 0.057714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6607-9_0_2_line_19 |  | 13 | 14 | 0.052443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6607-9_0_2_line_20 |  | 13 | 15 | 0.11387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6607-9_0_2_line_21 |  | 14 | 20 | 0.038936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6607-9_0_2_line_22 |  | 15 | 32 | 0.026438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6607-9_0_2_line_23 |  | 16 | 17 | 0.022699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6607-9_0_2_line_24 |  | 16 | 18 | 0.16679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6607-9_0_2_line_25 |  | 18 | 19 | 0.0054287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6607-9_0_2_line_26 |  | 20 | 35 | 0.036365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6607-9_0_2_line_27 |  | 23 | 36 | 0.30164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6607-9_0_2_line_28 |  | 24 | 25 | 0.048371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6607-9_0_2_line_29 |  | 24 | 26 | 0.085989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6607-9_0_2_line_30 |  | 25 | 29 | 0.041192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6607-9_0_2_line_31 |  | 25 | 30 | 0.10619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6607-9_0_2_line_32 |  | 26 | 27 | 0.075828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6607-9_0_2_line_33 |  | 27 | 28 | 0.008246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6607-9_0_2_line_34 |  | 30 | 31 | 0.012939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6607-9_0_2_line_35 |  | 32 | 33 | 0.038376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6607-9_0_2_line_36 |  | 35 | 37 | 0.030497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6607-9_0_2_line_37 |  | 36 | 38 | 0.13978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6607-9_0_2_line_38 |  | 38 | 39 | 0.36184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6607-9_0_2_trafo_39 | 0.63 MVA 20/0.4 kV | 40 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2494672.4816 | 1115043.958 | 2494680.3209 | 1115027.5555
1 | 2494663.4882 | 1115039.3226 | 2494672.4816 | 1115043.958
2 | 2494631.0684 | 1114985.8192 | 2494620.7032 | 1115013.2839 | 2494642.6636 | 1115027.1995 | 2494663.4882 | 1115039.3226
3 | 2494631.0684 | 1114985.8192 | 2494615.7147 | 1114979.1934
4 | 2494631.0684 | 1114985.8192 | 2494634.9353 | 1114987.4529
5 | 2494599.832 | 1115059.2213 | 2494604.355 | 1115050.637 | 2494606.0175 | 1115047.2058 | 2494607.493 | 1115044.1226 | 2494608.9237 | 1115041.1291 | 2494611.0502 | 1115036.8449 | 2494613.1856 | 1115032.1825 | 2494614.0502 | 1115030.3885 | 2494617.911 | 1115021.4711 | 2494620.7032 | 1115013.2839 | 2494631.0684 | 1114985.8192
6 | 2494634.9353 | 1114987.4529 | 2494633.3952 | 1114990.8152 | 2494644.6745 | 1114997.2119
7 | 2494634.9353 | 1114987.4529 | 2494639.453 | 1114977.668 | 2494648.6926 | 1114971.1586 | 2494664.1117 | 1114937.1907 | 2494670.2849 | 1114923.5634
8 | 2494670.2849 | 1114923.5634 | 2494681.7702 | 1114931.1128
9 | 2494667.8117 | 1114904.8389 | 2494674.4446 | 1114914.9521 | 2494670.2849 | 1114923.5634
10 | 2494495.5309 | 1115009.2841 | 2494485.9889 | 1115003.758
11 | 2494495.5309 | 1115009.2841 | 2494503.5752 | 1115011.3007 | 2494511.4246 | 1115014.5438 | 2494529.663 | 1115023.6095 | 2494554.7416 | 1115036.0695 | 2494569.106 | 1115043.991 | 2494583.0033 | 1115050.82 | 2494589.166 | 1115053.8925 | 2494599.832 | 1115059.2213
12 | 2494495.5309 | 1115009.2841 | 2494492.541 | 1115010.1145 | 2494489.3281 | 1115011.438 | 2494482.9478 | 1115016.2634 | 2494458.1783 | 1115038.3539 | 2494434.7559 | 1115058.3918
13 | 2494485.9889 | 1115003.758 | 2494483.2493 | 1115006.5408 | 2494477.6335 | 1115011.7977 | 2494468.9964 | 1115019.631 | 2494452.0458 | 1115034.3583 | 2494421.5118 | 1115061.5749 | 2494405.1613 | 1115076.1584 | 2494402.6437 | 1115078.3815 | 2494387.9766 | 1115091.5175
14 | 2494485.9889 | 1115003.758 | 2494493.4984 | 1114996.8115 | 2494497.7011 | 1114992.8913 | 2494503.6482 | 1114987.5842 | 2494508.3257 | 1114983.4334 | 2494514.6269 | 1114978.9429
15 | 2494599.832 | 1115059.2213 | 2494608.4099 | 1115063.5052
16 | 2494434.7559 | 1115058.3918 | 2494425.9665 | 1115065.9111 | 2494411.8797 | 1115078.4721
17 | 2494667.8117 | 1114904.8389 | 2494684.6263 | 1114899.1093 | 2494704.9883 | 1114893.9517 | 2494714.2094 | 1114892.0692
18 | 2494771.1895 | 1114883.0379 | 2494768.2693 | 1114883.4445 | 2494760.3025 | 1114884.5504 | 2494745.5665 | 1114886.3522 | 2494723.028 | 1114890.2689 | 2494714.2094 | 1114892.0692
19 | 2494561.4237 | 1114955.0678 | 2494546.016 | 1114962.1852 | 2494541.0818 | 1114964.4615 | 2494532.1066 | 1114969.2988 | 2494521.894 | 1114974.9248 | 2494514.6269 | 1114978.9429
20 | 2494514.6269 | 1114978.9429 | 2494505.4422 | 1114974.4223 | 2494501.0633 | 1114973.9983 | 2494478.8484 | 1114962.7895 | 2494412.469 | 1114929.295
21 | 2494561.4237 | 1114955.0678 | 2494525.2559 | 1114940.649
22 | 2494388.8659 | 1114917.3852 | 2494412.469 | 1114929.295
23 | 2494763.7552 | 1115137.6193 | 2494755.0084 | 1115146.6995 | 2494752.0032 | 1115150.6431 | 2494749.232 | 1115154.9636
24 | 2494763.7552 | 1115137.6193 | 2494750.3971 | 1115132.4594 | 2494733.2857 | 1115125.5414 | 2494706.3014 | 1115112.7025 | 2494621.7716 | 1115070.1796 | 2494613.4274 | 1115066.0111 | 2494613.2666 | 1115065.9308
25 | 2494613.2666 | 1115065.9308 | 2494608.4099 | 1115063.5052
26 | 2494525.2559 | 1114940.649 | 2494491.4763 | 1114927.1824
27 | 2494161.6269 | 1115290.861 | 2494188.4568 | 1115268.7999 | 2494223.9666 | 1115237.8482 | 2494324.2588 | 1115148.5835 | 2494387.9766 | 1115091.5175
28 | 2494612.8209 | 1114836.1408 | 2494613.6521 | 1114832.8687 | 2494582.4437 | 1114825.9188 | 2494569.422 | 1114825.9345
29 | 2494612.8209 | 1114836.1408 | 2494695.7823 | 1114858.7572
30 | 2494561.6865 | 1114866.0171 | 2494568.8075 | 1114843.4119 | 2494569.422 | 1114825.9345
31 | 2494494.5266 | 1114848.9653 | 2494518.4018 | 1114855.7091 | 2494524.0011 | 1114833.5417 | 2494527.8159 | 1114818.4434 | 2494539.4867 | 1114823.7879 | 2494554.0385 | 1114826.0358 | 2494569.422 | 1114825.9345
32 | 2494767.7228 | 1114875.5601 | 2494760.8238 | 1114878.115 | 2494759.6469 | 1114876.1675 | 2494695.7823 | 1114858.7572
33 | 2494771.1895 | 1114883.0379 | 2494768.9042 | 1114877.7632 | 2494767.7228 | 1114875.5601
34 | 2494494.5266 | 1114848.9653 | 2494482.0454 | 1114845.425
35 | 2494403.3759 | 1114881.8536 | 2494390.3332 | 1114914.2798 | 2494388.8659 | 1114917.3852
36 | 2494491.4763 | 1114927.1824 | 2494463.1472 | 1114915.8886
37 | 2494236.5955 | 1115408.8819 | 2494232.1783 | 1115403.1554 | 2494165.635 | 1115296.5946 | 2494161.6269 | 1115290.861
38 | 2494513.9776 | 1115178.2155 | 2494502.9983 | 1115191.671 | 2494457.3595 | 1115236.2063 | 2494324.5726 | 1115354.8661 | 2494311.1125 | 1115363.3177 | 2494236.5955 | 1115408.8819

## bus_geodata
| x | y | coords
0 | 2494680.3209 | 1115027.5555
1 | 2494672.4816 | 1115043.958
2 | 2494663.4882 | 1115039.3226
3 | 2494631.0684 | 1114985.8192
4 | 2494634.9353 | 1114987.4529
5 | 2494644.6745 | 1114997.2119
6 | 2494670.2849 | 1114923.5634
7 | 2494495.5309 | 1115009.2841
8 | 2494485.9889 | 1115003.758
9 | 2494599.832 | 1115059.2213
10 | 2494434.7559 | 1115058.3918
11 | 2494667.8117 | 1114904.8389
12 | 2494714.2094 | 1114892.0692
13 | 2494514.6269 | 1114978.9429
14 | 2494561.4237 | 1114955.0678
15 | 2494412.469 | 1114929.295
16 | 2494763.7552 | 1115137.6193
17 | 2494749.232 | 1115154.9636
18 | 2494613.2666 | 1115065.9308
19 | 2494608.4099 | 1115063.5052
20 | 2494525.2559 | 1114940.649
21 | 2494681.7702 | 1114931.1128
22 | 2494615.7147 | 1114979.1934
23 | 2494387.9766 | 1115091.5175
24 | 2494612.8209 | 1114836.1408
25 | 2494569.422 | 1114825.9345
26 | 2494695.7823 | 1114858.7572
27 | 2494767.7228 | 1114875.5601
28 | 2494771.1895 | 1114883.0379
29 | 2494561.6865 | 1114866.0171
30 | 2494494.5266 | 1114848.9653
31 | 2494482.0454 | 1114845.425
32 | 2494388.8659 | 1114917.3852
33 | 2494403.3759 | 1114881.8536
34 | 2494411.8797 | 1115078.4721
35 | 2494491.4763 | 1114927.1824
36 | 2494161.6269 | 1115290.861
37 | 2494463.1472 | 1114915.8886
38 | 2494236.5955 | 1115408.8819
39 | 2494513.9776 | 1115178.2155
40 | 2494631.0684 | 1114985.8192

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1