## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6621-284_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6621-284_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6621-284_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6621-284_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6621-284_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6621-284_0_6_node_47 | 0.4 | n |  | TRUE
6 | bus_LV_6621-284_0_6_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_6621-284_0_6_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_6621-284_0_6_node_51 | 0.4 | n |  | TRUE
9 | bus_LV_6621-284_0_6_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_6621-284_0_6_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_6621-284_0_6_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_6621-284_0_6_node_54 | 0.4 | n |  | TRUE
13 | bus_LV_6621-284_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_6621-284_0_6_node_53 | 0.4 | n |  | TRUE
15 | bus_LV_6621-284_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_6621-284_0_6_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_6621-284_0_6_node_57 | 0.4 | n |  | TRUE
18 | bus_LV_6621-284_0_6_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_6621-284_0_6_node_55 | 0.4 | n |  | TRUE
20 | bus_LV_6621-284_0_6_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_6621-284_0_6_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_6621-284_0_6_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_6621-284_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_6621-284_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_6621-284_0_6_node_41 | 0.4 | n |  | TRUE
26 | bus_LV_6621-284_0_6_node_50 | 0.4 | n |  | TRUE
27 | bus_LV_6621-284_0_6_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_6621-284_0_6_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_6621-284_0_6_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_6621-284_0_6_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_6621-284_0_6_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_6621-284_0_6_node_46 | 0.4 | n |  | TRUE
33 | bus_LV_6621-284_0_6_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_6621-284_0_6_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_6621-284_0_6_node_52 | 0.4 | n |  | TRUE
36 | bus_LV_6621-284_0_6_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_6621-284_0_6_node_56 | 0.4 | n |  | TRUE
38 | bus_LV_6621-284_0_6_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_6621-284_0_6_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_6621-284_0_6_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_6621-284_0_6_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_6621-284_0_6_node_48 | 0.4 | n |  | TRUE
43 | bus_LV_6621-284_0_6_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_6621-284_0_6_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_6621-284_0_6_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_6621-284_0_6_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_6621-284_0_6_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_6621-284_0_6_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_6621-284_0_6_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_6621-284_0_6_node_23 | 0.4 | n |  | TRUE
51 | bus_LV_6621-284_0_6_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_6621-284_0_6_node_29 | 0.4 | n |  | TRUE
53 | bus_MV_646_0_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6621-284_0_6_load_0 | 0 | 0.01113 | 0.0027894 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6621-284_0_6_load_1 | 1 | 0.011292 | 0.0028299 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6621-284_0_6_load_3 | 3 | 0.019121 | 0.0047922 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6621-284_0_6_load_30 | 7 | 0.018 | 0.0045113 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6621-284_0_6_load_51 | 8 | 0.012651 | 0.0031706 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6621-284_0_6_load_28 | 10 | 0.023675 | 0.0059335 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6621-284_0_6_load_54 | 12 | 0.016968 | 0.0042526 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6621-284_0_6_load_53 | 14 | 0.014526 | 0.0036405 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6621-284_0_6_load_57 | 17 | 0.013715 | 0.0034374 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6621-284_0_6_load_32 | 18 | 0.017515 | 0.0043896 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6621-284_0_6_load_55 | 19 | 0.012241 | 0.0030679 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6621-284_0_6_load_25 | 21 | 0.012006 | 0.003009 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6621-284_0_6_load_42 | 22 | 0.0097276 | 0.002438 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6621-284_0_6_load_41 | 25 | 0.017755 | 0.0044499 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6621-284_0_6_load_50 | 26 | 0.014039 | 0.0035185 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6621-284_0_6_load_58 | 27 | 0.020765 | 0.0052043 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6621-284_0_6_load_33 | 30 | 0.016915 | 0.0042393 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6621-284_0_6_load_44 | 33 | 0.045561 | 0.011419 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6621-284_0_6_load_31 | 34 | 0.011854 | 0.0029709 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6621-284_0_6_load_52 | 35 | 0.021858 | 0.0054781 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6621-284_0_6_load_26 | 36 | 0.019473 | 0.0048805 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6621-284_0_6_load_56 | 37 | 0.011827 | 0.0029642 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6621-284_0_6_load_43 | 39 | 0.007526 | 0.0018862 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6621-284_0_6_load_45 | 40 | 0.018766 | 0.0047033 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6621-284_0_6_load_40 | 41 | 0.011647 | 0.002919 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6621-284_0_6_load_48 | 42 | 0.022733 | 0.0056974 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6621-284_0_6_load_37 | 43 | 0.012186 | 0.003054 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6621-284_0_6_load_38 | 44 | 0.015136 | 0.0037934 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6621-284_0_6_load_39 | 45 | 0.017545 | 0.0043971 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6621-284_0_6_load_49 | 46 | 0.012864 | 0.003224 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6621-284_0_6_load_35 | 47 | 0.010775 | 0.0027005 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6621-284_0_6_load_34 | 48 | 0.012114 | 0.003036 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6621-284_0_6_load_36 | 49 | 0.014042 | 0.0035193 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6621-284_0_6_load_23 | 50 | 0.030298 | 0.0075934 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6621-284_0_6_load_27 | 51 | 0.0251 | 0.0062906 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6621-284_0_6_load_29 | 52 | 0.021226 | 0.0053197 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6621-284_0_6_line_0 |  | 0 | 1 | 0.016181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_6621-284_0_6_line_1 |  | 0 | 2 | 0.029924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_6621-284_0_6_line_2 |  | 1 | 3 | 0.019699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_6621-284_0_6_line_3 |  | 2 | 4 | 0.008773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_6621-284_0_6_line_4 |  | 3 | 5 | 0.017556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_6621-284_0_6_line_5 |  | 4 | 6 | 0.027552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6621-284_0_6_line_6 |  | 4 | 7 | 0.01178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_6621-284_0_6_line_7 |  | 5 | 9 | 0.00566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_6621-284_0_6_line_8 |  | 5 | 28 | 0.005327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6621-284_0_6_line_9 |  | 6 | 8 | 0.018042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6621-284_0_6_line_10 |  | 7 | 34 | 0.019201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_6621-284_0_6_line_11 |  | 8 | 35 | 0.021787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6621-284_0_6_line_12 |  | 9 | 10 | 0.008225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_6621-284_0_6_line_13 |  | 10 | 36 | 0.02431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6621-284_0_6_line_14 |  | 10 | 24 | 0.030746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_6621-284_0_6_line_15 |  | 11 | 12 | 0.0095278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6621-284_0_6_line_16 |  | 11 | 13 | 0.010625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6621-284_0_6_line_17 |  | 11 | 14 | 0.028031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6621-284_0_6_line_18 |  | 12 | 37 | 0.018859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6621-284_0_6_line_19 |  | 13 | 18 | 0.010938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6621-284_0_6_line_20 |  | 13 | 19 | 0.027886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6621-284_0_6_line_21 |  | 15 | 16 | 0.002912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6621-284_0_6_line_22 |  | 15 | 17 | 0.010129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6621-284_0_6_line_23 |  | 16 | 20 | 0.01697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6621-284_0_6_line_24 |  | 16 | 21 | 0.024779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6621-284_0_6_line_25 |  | 17 | 37 | 0.018044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6621-284_0_6_line_26 |  | 18 | 34 | 0.019405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_6621-284_0_6_line_27 |  | 20 | 22 | 0.0060408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6621-284_0_6_line_28 |  | 21 | 38 | 0.010676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6621-284_0_6_line_29 |  | 22 | 39 | 0.019453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6621-284_0_6_line_30 |  | 23 | 24 | 0.0097153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6621-284_0_6_line_31 |  | 23 | 25 | 0.0092084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6621-284_0_6_line_32 |  | 23 | 26 | 0.02251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6621-284_0_6_line_33 |  | 24 | 27 | 0.010495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6621-284_0_6_line_34 |  | 25 | 45 | 0.015571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6621-284_0_6_line_35 |  | 26 | 46 | 0.010914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6621-284_0_6_line_36 |  | 27 | 49 | 0.017411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6621-284_0_6_line_37 |  | 28 | 29 | 0.023203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6621-284_0_6_line_38 |  | 29 | 30 | 0.012403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6621-284_0_6_line_39 |  | 30 | 48 | 0.016693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6621-284_0_6_line_40 |  | 31 | 32 | 0.008493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6621-284_0_6_line_41 |  | 31 | 33 | 0.01757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6621-284_0_6_line_42 |  | 32 | 35 | 0.01277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6621-284_0_6_line_43 |  | 33 | 40 | 0.046904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6621-284_0_6_line_44 |  | 38 | 50 | 0.013894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6621-284_0_6_line_45 |  | 41 | 42 | 0.0044107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6621-284_0_6_line_46 |  | 42 | 46 | 0.0051886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6621-284_0_6_line_47 |  | 43 | 44 | 0.028796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6621-284_0_6_line_48 |  | 44 | 45 | 0.014634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6621-284_0_6_line_49 |  | 47 | 48 | 0.016112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6621-284_0_6_line_50 |  | 49 | 52 | 0.033212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6621-284_0_6_line_51 |  | 51 | 52 | 0.021319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6621-284_0_6_trafo_1 | 0.63 MVA 20/0.4 kV | 53 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2499624.0206 | 1117101.7967 | 2499640.1684 | 1117102.826
1 | 2499594.1576 | 1117099.8932 | 2499624.0206 | 1117101.7967
2 | 2499659.8275 | 1117104.079 | 2499640.1684 | 1117102.826
3 | 2499591.1257 | 1117091.6606 | 2499592.8803 | 1117096.4345 | 2499594.1576 | 1117099.8932
4 | 2499677.2715 | 1117105.6737 | 2499670.0175 | 1117105.405 | 2499664.8745 | 1117104.4007 | 2499659.8275 | 1117104.079
5 | 2499570.0501 | 1117109.3993 | 2499577.7132 | 1117103.1571 | 2499582.7864 | 1117099.0258 | 2499591.1257 | 1117091.6606
6 | 2499591.1257 | 1117091.6606 | 2499600.1851 | 1117084.1314
7 | 2499678.5365 | 1117111.1896 | 2499677.2715 | 1117105.6737
8 | 2499677.9559 | 1117100.3924 | 2499677.2715 | 1117105.6737
9 | 2499570.0501 | 1117109.3993 | 2499581.7804 | 1117108.6486 | 2499588.0674 | 1117108.7188
10 | 2499614.952 | 1117071.8589 | 2499600.1851 | 1117084.1314
11 | 2499588.0674 | 1117108.7188 | 2499590.9849 | 1117108.7514 | 2499596.2189 | 1117109.654 | 2499605.9455 | 1117110.9823 | 2499609.4672 | 1117112.2463
12 | 2499678.5365 | 1117111.1896 | 2499680.4142 | 1117119.1968
13 | 2499680.4142 | 1117119.1968 | 2499677.5932 | 1117116.6864 | 2499657.0978 | 1117115.4283
14 | 2499687.5235 | 1117146.118 | 2499689.7439 | 1117145.4697 | 2499683.1543 | 1117121.4861 | 2499680.4142 | 1117119.1968
15 | 2499631.7944 | 1117044.056 | 2499625.8854 | 1117036.5819
16 | 2499631.7944 | 1117044.056 | 2499634.4126 | 1117047.3702 | 2499638.288 | 1117052.4647
17 | 2499631.7944 | 1117044.056 | 2499610.1596 | 1117061.8787
18 | 2499625.8854 | 1117036.5819 | 2499614.1892 | 1117021.7879
19 | 2499638.288 | 1117052.4647 | 2499629.8759 | 1117059.4558
20 | 2499638.288 | 1117052.4647 | 2499655.6185 | 1117074.3115
21 | 2499594.0818 | 1117000.9436 | 2499596.7168 | 1116999.6879
22 | 2499596.7168 | 1116999.6879 | 2499602.9984 | 1117007.6332
23 | 2499583.2339 | 1116987.8932 | 2499588.0552 | 1116993.6946 | 2499594.0818 | 1117000.9436
24 | 2499594.0818 | 1117000.9436 | 2499575.1106 | 1117016.8845
25 | 2499614.1892 | 1117021.7879 | 2499602.9984 | 1117007.6332
26 | 2499614.952 | 1117071.8589 | 2499629.8759 | 1117059.4558
27 | 2499583.2339 | 1116987.8932 | 2499578.6242 | 1116991.7973
28 | 2499566.9368 | 1117023.7528 | 2499575.1106 | 1117016.8845
29 | 2499563.7801 | 1117004.3697 | 2499578.6242 | 1116991.7973
30 | 2499687.5235 | 1117146.118 | 2499688.648 | 1117150.1463 | 2499689.9801 | 1117155.5165
31 | 2499689.9801 | 1117155.5165 | 2499681.174 | 1117158.2085
32 | 2499689.9801 | 1117155.5165 | 2499692.0541 | 1117154.8817 | 2499697.0181 | 1117174.608
33 | 2499687.5235 | 1117146.118 | 2499677.449 | 1117149.0595
34 | 2499666.283 | 1117162.7605 | 2499681.174 | 1117158.2085
35 | 2499697.0181 | 1117174.608 | 2499699.6815 | 1117185.1921
36 | 2499660.7363 | 1117153.9392 | 2499677.449 | 1117149.0595
37 | 2499677.9559 | 1117100.3924 | 2499681.6956 | 1117099.6411 | 2499686.3458 | 1117098.8635 | 2499685.5019 | 1117094.0633 | 2499686.8133 | 1117090.7395 | 2499689.4138 | 1117085.0817
38 | 2499689.4138 | 1117085.0817 | 2499684.9649 | 1117084.9665 | 2499680.0437 | 1117078.719
39 | 2499669.7145 | 1117065.6061 | 2499680.0437 | 1117078.719
40 | 2499620.0015 | 1117119.1765 | 2499622.4142 | 1117127.3194
41 | 2499622.4142 | 1117127.3194 | 2499627.3959 | 1117144.1678
42 | 2499620.0015 | 1117119.1765 | 2499613.1996 | 1117113.5858 | 2499609.4672 | 1117112.2463
43 | 2499627.3959 | 1117144.1678 | 2499632.7287 | 1117162.2034 | 2499605.6885 | 1117169.8365
44 | 2499566.9368 | 1117023.7528 | 2499556.2693 | 1117032.6551
45 | 2499702.0241 | 1117194.5012 | 2499700.9477 | 1117190.2239
46 | 2499699.6815 | 1117185.1921 | 2499700.9477 | 1117190.2239
47 | 2499649.0723 | 1117188.3809 | 2499643.3693 | 1117169.765 | 2499652.2881 | 1117167.0386
48 | 2499666.283 | 1117162.7605 | 2499652.2881 | 1117167.0386
49 | 2499669.7145 | 1117065.6061 | 2499659.7447 | 1117052.9494
50 | 2499660.7363 | 1117153.9392 | 2499640.9328 | 1117159.7214 | 2499637.4079 | 1117147.6435
51 | 2499637.4079 | 1117147.6435 | 2499631.4352 | 1117127.1786

## bus_geodata
| x | y | coords
0 | 2499624.0206 | 1117101.7967
1 | 2499640.1684 | 1117102.826
2 | 2499594.1576 | 1117099.8932
3 | 2499659.8275 | 1117104.079
4 | 2499591.1257 | 1117091.6606
5 | 2499677.2715 | 1117105.6737
6 | 2499570.0501 | 1117109.3993
7 | 2499600.1851 | 1117084.1314
8 | 2499588.0674 | 1117108.7188
9 | 2499678.5365 | 1117111.1896
10 | 2499680.4142 | 1117119.1968
11 | 2499631.7944 | 1117044.056
12 | 2499625.8854 | 1117036.5819
13 | 2499638.288 | 1117052.4647
14 | 2499610.1596 | 1117061.8787
15 | 2499596.7168 | 1116999.6879
16 | 2499594.0818 | 1117000.9436
17 | 2499602.9984 | 1117007.6332
18 | 2499629.8759 | 1117059.4558
19 | 2499655.6185 | 1117074.3115
20 | 2499583.2339 | 1116987.8932
21 | 2499575.1106 | 1117016.8845
22 | 2499578.6242 | 1116991.7973
23 | 2499689.9801 | 1117155.5165
24 | 2499687.5235 | 1117146.118
25 | 2499681.174 | 1117158.2085
26 | 2499697.0181 | 1117174.608
27 | 2499677.449 | 1117149.0595
28 | 2499677.9559 | 1117100.3924
29 | 2499689.4138 | 1117085.0817
30 | 2499680.0437 | 1117078.719
31 | 2499622.4142 | 1117127.3194
32 | 2499620.0015 | 1117119.1765
33 | 2499627.3959 | 1117144.1678
34 | 2499614.952 | 1117071.8589
35 | 2499609.4672 | 1117112.2463
36 | 2499657.0978 | 1117115.4283
37 | 2499614.1892 | 1117021.7879
38 | 2499566.9368 | 1117023.7528
39 | 2499563.7801 | 1117004.3697
40 | 2499605.6885 | 1117169.8365
41 | 2499702.0241 | 1117194.5012
42 | 2499700.9477 | 1117190.2239
43 | 2499649.0723 | 1117188.3809
44 | 2499652.2881 | 1117167.0386
45 | 2499666.283 | 1117162.7605
46 | 2499699.6815 | 1117185.1921
47 | 2499659.7447 | 1117052.9494
48 | 2499669.7145 | 1117065.6061
49 | 2499660.7363 | 1117153.9392
50 | 2499556.2693 | 1117032.6551
51 | 2499631.4352 | 1117127.1786
52 | 2499637.4079 | 1117147.6435
53 | 2499677.2715 | 1117105.6737

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1