## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6621-304_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6621-304_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6621-304_0_6_node_13 | 0.4 | n |  | TRUE
3 | bus_LV_6621-304_0_6_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_6621-304_0_6_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_6621-304_0_6_node_37 | 0.4 | n |  | TRUE
6 | bus_LV_6621-304_0_6_node_91 | 0.4 | n |  | TRUE
7 | bus_LV_6621-304_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_6621-304_0_6_node_96 | 0.4 | n |  | TRUE
9 | bus_LV_6621-304_0_6_node_97 | 0.4 | n |  | TRUE
10 | bus_LV_6621-304_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_6621-304_0_6_node_84 | 0.4 | n |  | TRUE
12 | bus_LV_6621-304_0_6_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_6621-304_0_6_node_83 | 0.4 | n |  | TRUE
14 | bus_LV_6621-304_0_6_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_6621-304_0_6_node_100 | 0.4 | n |  | TRUE
16 | bus_LV_6621-304_0_6_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_6621-304_0_6_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_6621-304_0_6_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_6621-304_0_6_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_6621-304_0_6_node_107 | 0.4 | n |  | TRUE
21 | bus_LV_6621-304_0_6_node_66 | 0.4 | n |  | TRUE
22 | bus_LV_6621-304_0_6_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_6621-304_0_6_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_6621-304_0_6_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_6621-304_0_6_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_6621-304_0_6_node_48 | 0.4 | n |  | TRUE
27 | bus_LV_6621-304_0_6_node_49 | 0.4 | n |  | TRUE
28 | bus_LV_6621-304_0_6_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_6621-304_0_6_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_6621-304_0_6_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_6621-304_0_6_node_64 | 0.4 | n |  | TRUE
32 | bus_LV_6621-304_0_6_node_51 | 0.4 | n |  | TRUE
33 | bus_LV_6621-304_0_6_node_72 | 0.4 | n |  | TRUE
34 | bus_LV_6621-304_0_6_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_6621-304_0_6_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_6621-304_0_6_node_98 | 0.4 | n |  | TRUE
37 | bus_LV_6621-304_0_6_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_6621-304_0_6_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_6621-304_0_6_node_81 | 0.4 | n |  | TRUE
40 | bus_LV_6621-304_0_6_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_6621-304_0_6_node_65 | 0.4 | n |  | TRUE
42 | bus_LV_6621-304_0_6_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_6621-304_0_6_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_6621-304_0_6_node_63 | 0.4 | n |  | TRUE
45 | bus_LV_6621-304_0_6_node_60 | 0.4 | n |  | TRUE
46 | bus_LV_6621-304_0_6_node_77 | 0.4 | n |  | TRUE
47 | bus_LV_6621-304_0_6_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_6621-304_0_6_node_75 | 0.4 | n |  | TRUE
49 | bus_LV_6621-304_0_6_node_82 | 0.4 | n |  | TRUE
50 | bus_LV_6621-304_0_6_node_78 | 0.4 | n |  | TRUE
51 | bus_LV_6621-304_0_6_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_6621-304_0_6_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_6621-304_0_6_node_69 | 0.4 | n |  | TRUE
54 | bus_LV_6621-304_0_6_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_6621-304_0_6_node_92 | 0.4 | n |  | TRUE
56 | bus_LV_6621-304_0_6_node_90 | 0.4 | n |  | TRUE
57 | bus_LV_6621-304_0_6_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_6621-304_0_6_node_95 | 0.4 | n |  | TRUE
59 | bus_LV_6621-304_0_6_node_110 | 0.4 | n |  | TRUE
60 | bus_LV_6621-304_0_6_node_109 | 0.4 | n |  | TRUE
61 | bus_LV_6621-304_0_6_node_106 | 0.4 | n |  | TRUE
62 | bus_LV_6621-304_0_6_node_105 | 0.4 | n |  | TRUE
63 | bus_LV_6621-304_0_6_node_108 | 0.4 | n |  | TRUE
64 | bus_LV_6621-304_0_6_node_58 | 0.4 | n |  | TRUE
65 | bus_LV_6621-304_0_6_node_101 | 0.4 | n |  | TRUE
66 | bus_LV_6621-304_0_6_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_6621-304_0_6_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_6621-304_0_6_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_6621-304_0_6_node_73 | 0.4 | n |  | TRUE
70 | bus_LV_6621-304_0_6_node_74 | 0.4 | n |  | TRUE
71 | bus_LV_6621-304_0_6_node_70 | 0.4 | n |  | TRUE
72 | bus_LV_6621-304_0_6_node_59 | 0.4 | n |  | TRUE
73 | bus_LV_6621-304_0_6_node_111 | 0.4 | n |  | TRUE
74 | bus_LV_6621-304_0_6_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_6621-304_0_6_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_6621-304_0_6_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_6621-304_0_6_node_50 | 0.4 | n |  | TRUE
78 | bus_LV_6621-304_0_6_node_46 | 0.4 | n |  | TRUE
79 | bus_LV_6621-304_0_6_node_47 | 0.4 | n |  | TRUE
80 | bus_LV_6621-304_0_6_node_44 | 0.4 | n |  | TRUE
81 | bus_LV_6621-304_0_6_node_43 | 0.4 | n |  | TRUE
82 | bus_LV_6621-304_0_6_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_6621-304_0_6_node_99 | 0.4 | n |  | TRUE
84 | bus_LV_6621-304_0_6_node_104 | 0.4 | n |  | TRUE
85 | bus_LV_6621-304_0_6_node_61 | 0.4 | n |  | TRUE
86 | bus_LV_6621-304_0_6_node_79 | 0.4 | n |  | TRUE
87 | bus_LV_6621-304_0_6_node_39 | 0.4 | n |  | TRUE
88 | bus_LV_6621-304_0_6_node_40 | 0.4 | n |  | TRUE
89 | bus_LV_6621-304_0_6_node_41 | 0.4 | n |  | TRUE
90 | bus_LV_6621-304_0_6_node_42 | 0.4 | n |  | TRUE
91 | bus_LV_6621-304_0_6_node_102 | 0.4 | n |  | TRUE
92 | bus_LV_6621-304_0_6_node_103 | 0.4 | n |  | TRUE
93 | bus_LV_6621-304_0_6_node_80 | 0.4 | n |  | TRUE
94 | bus_LV_6621-304_0_6_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_6621-304_0_6_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_6621-304_0_6_node_88 | 0.4 | n |  | TRUE
97 | bus_LV_6621-304_0_6_node_93 | 0.4 | n |  | TRUE
98 | bus_LV_6621-304_0_6_node_94 | 0.4 | n |  | TRUE
99 | bus_MV_651_0_node_47 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6621-304_0_6_load_0 | 0 | 0.02189 | 0.0054862 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6621-304_0_6_load_37 | 5 | 0.040243 | 0.010086 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6621-304_0_6_load_91 | 6 | 0.007391 | 0.0018524 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6621-304_0_6_load_96 | 8 | 0.014117 | 0.003538 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6621-304_0_6_load_97 | 9 | 0.023014 | 0.0057678 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6621-304_0_6_load_84 | 11 | 0.015696 | 0.0039339 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6621-304_0_6_load_83 | 13 | 0.017721 | 0.0044413 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6621-304_0_6_load_100 | 15 | 0.0097614 | 0.0024464 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6621-304_0_6_load_107 | 20 | 0.0077325 | 0.0019379 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6621-304_0_6_load_48 | 26 | 0.00095808 | 0.00024012 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6621-304_0_6_load_49 | 27 | 0.0037872 | 0.00094917 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6621-304_0_6_load_45 | 28 | 0.00092008 | 0.00023059 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6621-304_0_6_load_64 | 31 | 0.0069855 | 0.0017507 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6621-304_0_6_load_51 | 32 | 0.0021667 | 0.00054302 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6621-304_0_6_load_72 | 33 | 0.0060522 | 0.0015168 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6621-304_0_6_load_98 | 36 | 0.0017742 | 0.00044465 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6621-304_0_6_load_81 | 39 | 0.0049437 | 0.001239 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6621-304_0_6_load_65 | 41 | 0.005326 | 0.0013348 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6621-304_0_6_load_63 | 44 | 0.0059797 | 0.0014987 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6621-304_0_6_load_60 | 45 | 0.0041973 | 0.0010519 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6621-304_0_6_load_77 | 46 | 0.0034002 | 0.00085217 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6621-304_0_6_load_75 | 48 | 0.017129 | 0.004293 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6621-304_0_6_load_82 | 49 | 0.0034032 | 0.00085293 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6621-304_0_6_load_78 | 50 | 0.0012016 | 0.00030116 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6621-304_0_6_load_69 | 53 | 0.0041946 | 0.0010513 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6621-304_0_6_load_92 | 55 | 0.011176 | 0.002801 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6621-304_0_6_load_90 | 56 | 0.010956 | 0.0027459 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6621-304_0_6_load_52 | 57 | 0.0021548 | 0.00054005 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6621-304_0_6_load_95 | 58 | 0.01404 | 0.0035187 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6621-304_0_6_load_110 | 59 | 0.0088837 | 0.0022265 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6621-304_0_6_load_109 | 60 | 0.014491 | 0.0036317 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6621-304_0_6_load_106 | 61 | 0.0054412 | 0.0013637 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6621-304_0_6_load_105 | 62 | 0.0056097 | 0.0014059 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6621-304_0_6_load_108 | 63 | 0.0089651 | 0.0022469 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6621-304_0_6_load_58 | 64 | 0.013416 | 0.0033624 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6621-304_0_6_load_101 | 65 | 0.0073767 | 0.0018488 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6621-304_0_6_load_56 | 66 | 0.012304 | 0.0030835 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6621-304_0_6_load_53 | 67 | 0.012466 | 0.0031243 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6621-304_0_6_load_73 | 69 | 0.0062265 | 0.0015605 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6621-304_0_6_load_74 | 70 | 0.0069519 | 0.0017423 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6621-304_0_6_load_70 | 71 | 0.0098496 | 0.0024686 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6621-304_0_6_load_111 | 73 | 0.0087553 | 0.0021943 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6621-304_0_6_load_67 | 76 | 0.0060464 | 0.0015154 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6621-304_0_6_load_50 | 77 | 0.0050696 | 0.0012706 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6621-304_0_6_load_46 | 78 | 0.00093607 | 0.0002346 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6621-304_0_6_load_47 | 79 | 0.0020512 | 0.00051408 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6621-304_0_6_load_44 | 80 | 0.002132 | 0.00053432 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6621-304_0_6_load_43 | 81 | 0.00092577 | 0.00023202 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6621-304_0_6_load_71 | 82 | 0.0061364 | 0.0015379 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6621-304_0_6_load_99 | 83 | 0.0051889 | 0.0013005 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6621-304_0_6_load_104 | 84 | 0.005352 | 0.0013413 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6621-304_0_6_load_61 | 85 | 0.0032086 | 0.00080415 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6621-304_0_6_load_79 | 86 | 0.0096823 | 0.0024266 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6621-304_0_6_load_39 | 87 | 0.0015455 | 0.00038734 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6621-304_0_6_load_40 | 88 | 0.0010546 | 0.00026431 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6621-304_0_6_load_41 | 89 | 0.00091776 | 0.00023001 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6621-304_0_6_load_42 | 90 | 0.0017677 | 0.00044303 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6621-304_0_6_load_102 | 91 | 0.0098837 | 0.0024771 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6621-304_0_6_load_103 | 92 | 0.0098551 | 0.0024699 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6621-304_0_6_load_80 | 93 | 0.0095546 | 0.0023946 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6621-304_0_6_load_85 | 94 | 0.0007924 | 0.0001986 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6621-304_0_6_load_93 | 97 | 0.014229 | 0.0035662 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6621-304_0_6_load_94 | 98 | 0.013864 | 0.0034746 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 91 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6621-304_0_6_line_0 |  | 0 | 1 | 0.035129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6621-304_0_6_line_1 |  | 1 | 2 | 0.11789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6621-304_0_6_line_2 |  | 2 | 13 | 0.04872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6621-304_0_6_line_3 |  | 2 | 14 | 0.041883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6621-304_0_6_line_4 |  | 3 | 4 | 0.012117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6621-304_0_6_line_5 |  | 3 | 5 | 0.012306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6621-304_0_6_line_6 |  | 4 | 6 | 0.0046355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6621-304_0_6_line_7 |  | 6 | 56 | 0.014482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6621-304_0_6_line_8 |  | 7 | 8 | 0.0099831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6621-304_0_6_line_9 |  | 7 | 9 | 0.0090326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6621-304_0_6_line_10 |  | 8 | 58 | 0.014323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6621-304_0_6_line_11 |  | 9 | 54 | 0.020243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6621-304_0_6_line_12 |  | 10 | 11 | 0.034352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_6621-304_0_6_line_13 |  | 10 | 12 | 0.0093851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_6621-304_0_6_line_14 |  | 10 | 13 | 0.067841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6621-304_0_6_line_15 |  | 11 | 16 | 0.035962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_6621-304_0_6_line_16 |  | 12 | 21 | 0.033642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_6621-304_0_6_line_17 |  | 14 | 15 | 0.041031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6621-304_0_6_line_18 |  | 15 | 65 | 0.017872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6621-304_0_6_line_19 |  | 16 | 17 | 0.083172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_6621-304_0_6_line_20 |  | 17 | 54 | 0.013096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6621-304_0_6_line_21 |  | 17 | 55 | 0.01243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6621-304_0_6_line_22 |  | 18 | 19 | 0.027885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6621-304_0_6_line_23 |  | 18 | 20 | 0.032479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6621-304_0_6_line_24 |  | 19 | 66 | 0.010242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6621-304_0_6_line_25 |  | 19 | 67 | 0.015663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6621-304_0_6_line_26 |  | 21 | 76 | 0.030977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_6621-304_0_6_line_27 |  | 21 | 66 | 0.017032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6621-304_0_6_line_28 |  | 22 | 23 | 0.081022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6621-304_0_6_line_29 |  | 22 | 24 | 0.011882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6621-304_0_6_line_30 |  | 23 | 32 | 0.00316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6621-304_0_6_line_31 |  | 24 | 45 | 0.010871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6621-304_0_6_line_32 |  | 25 | 26 | 0.019377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6621-304_0_6_line_33 |  | 25 | 27 | 0.030751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6621-304_0_6_line_34 |  | 25 | 28 | 0.024569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6621-304_0_6_line_35 |  | 26 | 77 | 0.011494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6621-304_0_6_line_36 |  | 27 | 34 | 0.025724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6621-304_0_6_line_37 |  | 28 | 78 | 0.025511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6621-304_0_6_line_38 |  | 29 | 30 | 0.095368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_6621-304_0_6_line_39 |  | 29 | 31 | 0.0098502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6621-304_0_6_line_40 |  | 30 | 33 | 0.017798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_6621-304_0_6_line_41 |  | 31 | 44 | 0.040332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6621-304_0_6_line_42 |  | 32 | 79 | 0.02506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6621-304_0_6_line_43 |  | 32 | 57 | 0.0082552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6621-304_0_6_line_44 |  | 33 | 82 | 6.2206e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_6621-304_0_6_line_45 |  | 34 | 35 | 0.018537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6621-304_0_6_line_46 |  | 35 | 36 | 0.029812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6621-304_0_6_line_47 |  | 36 | 83 | 0.020912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6621-304_0_6_line_48 |  | 37 | 38 | 0.052609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6621-304_0_6_line_49 |  | 37 | 39 | 0.011802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6621-304_0_6_line_50 |  | 38 | 49 | 0.017368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6621-304_0_6_line_51 |  | 39 | 47 | 0.012752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6621-304_0_6_line_52 |  | 40 | 41 | 0.014736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6621-304_0_6_line_53 |  | 40 | 42 | 0.034428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6621-304_0_6_line_54 |  | 40 | 43 | 0.039749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6621-304_0_6_line_55 |  | 40 | 44 | 0.0070719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6621-304_0_6_line_56 |  | 41 | 84 | 0.0064536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6621-304_0_6_line_57 |  | 42 | 47 | 0.041268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6621-304_0_6_line_58 |  | 42 | 48 | 0.080712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6621-304_0_6_line_59 |  | 43 | 46 | 0.017744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6621-304_0_6_line_60 |  | 45 | 85 | 0.015271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6621-304_0_6_line_61 |  | 46 | 52 | 0.016154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6621-304_0_6_line_62 |  | 47 | 50 | 0.029567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6621-304_0_6_line_63 |  | 50 | 86 | 0.0064267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6621-304_0_6_line_64 |  | 51 | 52 | 0.051486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6621-304_0_6_line_65 |  | 51 | 53 | 0.011104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6621-304_0_6_line_66 |  | 52 | 85 | 0.020972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6621-304_0_6_line_67 |  | 55 | 56 | 0.014695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6621-304_0_6_line_68 |  | 58 | 97 | 0.01444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6621-304_0_6_line_69 |  | 59 | 60 | 0.0039111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6621-304_0_6_line_70 |  | 60 | 75 | 0.011581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6621-304_0_6_line_71 |  | 61 | 62 | 0.0065269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6621-304_0_6_line_72 |  | 62 | 84 | 0.0064982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6621-304_0_6_line_73 |  | 63 | 64 | 0.0036168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6621-304_0_6_line_74 |  | 64 | 74 | 0.012104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6621-304_0_6_line_75 |  | 67 | 74 | 0.02104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6621-304_0_6_line_76 |  | 68 | 69 | 0.017093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6621-304_0_6_line_77 |  | 68 | 70 | 0.032859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_6621-304_0_6_line_78 |  | 68 | 71 | 0.026727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_6621-304_0_6_line_79 |  | 70 | 91 | 0.017983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_6621-304_0_6_line_80 |  | 71 | 82 | 0.0038643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_6621-304_0_6_line_81 |  | 72 | 73 | 0.0055973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6621-304_0_6_line_82 |  | 72 | 74 | 0.01008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6621-304_0_6_line_83 |  | 73 | 75 | 0.024841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_6621-304_0_6_line_84 |  | 76 | 92 | 0.018275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_6621-304_0_6_line_85 |  | 77 | 90 | 0.014859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6621-304_0_6_line_86 |  | 78 | 79 | 0.0085228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6621-304_0_6_line_87 |  | 80 | 81 | 0.0083529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_6621-304_0_6_line_88 |  | 81 | 89 | 0.024791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_6621-304_0_6_line_89 |  | 83 | 96 | 0.025323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_6621-304_0_6_line_90 |  | 86 | 93 | 0.027478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_6621-304_0_6_line_91 |  | 87 | 88 | 0.0069892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_6621-304_0_6_line_92 |  | 87 | 89 | 0.011132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_6621-304_0_6_line_93 |  | 88 | 90 | 0.0089168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_6621-304_0_6_line_94 |  | 91 | 92 | 0.004703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_6621-304_0_6_line_95 |  | 94 | 95 | 0.033419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_6621-304_0_6_line_96 |  | 95 | 96 | 0.053405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_6621-304_0_6_line_97 |  | 97 | 98 | 0.014424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6621-304_0_6_trafo_102 | 0.63 MVA 20/0.4 kV | 99 | 91 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2497860.5075 | 1118008.0392 | 2497827.5722 | 1117995.8189
1 | 2497780.2233 | 1117997.3773 | 2497785.335 | 1117980.1134 | 2497783.0743 | 1117979.2621 | 2497786.4001 | 1117970.5115 | 2497801.9269 | 1117976.6309 | 2497813.3079 | 1117980.441 | 2497857.9306 | 1117996.2419 | 2497860.5075 | 1118008.0392
2 | 2497780.2233 | 1117997.3773 | 2497805.5195 | 1118039.0155
3 | 2497755.4206 | 1117975.4492 | 2497766.5925 | 1117975.5605 | 2497776.6662 | 1117979.2037 | 2497775.1808 | 1117980.8409 | 2497774.6001 | 1117983.0188 | 2497774.8513 | 1117985.5495 | 2497780.2233 | 1117997.3773
4 | 2497936.5799 | 1118075.1421 | 2497942.8456 | 1118085.5207
5 | 2497936.5799 | 1118075.1421 | 2497935.4376 | 1118073.3269 | 2497926.743 | 1118078.5857
6 | 2497942.8456 | 1118085.5207 | 2497938.8769 | 1118087.916
7 | 2497926.4784 | 1118095.3989 | 2497938.8769 | 1118087.916
8 | 2497877.8051 | 1118076.5015 | 2497872.695 | 1118067.9253
9 | 2497877.8051 | 1118076.5015 | 2497882.4307 | 1118084.2598
10 | 2497865.3636 | 1118055.6211 | 2497872.695 | 1118067.9253
11 | 2497896.0081 | 1118098.497 | 2497887.9182 | 1118093.4637 | 2497882.4307 | 1118084.2598
12 | 2497840.7437 | 1118096.9957 | 2497858.5836 | 1118126.3518
13 | 2497832.4184 | 1118101.3279 | 2497837.7135 | 1118098.5701 | 2497840.7437 | 1118096.9957
14 | 2497840.7437 | 1118096.9957 | 2497805.5195 | 1118039.0155
15 | 2497877.2595 | 1118157.0838 | 2497858.5836 | 1118126.3518
16 | 2497802.2004 | 1118116.1143 | 2497805.1019 | 1118114.6866 | 2497812.2446 | 1118111.1749 | 2497832.4184 | 1118101.3279
17 | 2497755.4206 | 1117975.4492 | 2497776.8306 | 1118010.4511
18 | 2497776.8306 | 1118010.4511 | 2497786.1562 | 1118025.6969
19 | 2497877.2595 | 1118157.0838 | 2497878.8318 | 1118159.6811 | 2497881.0812 | 1118161.233 | 2497883.6725 | 1118161.5561 | 2497886.6937 | 1118160.3599 | 2497902.1601 | 1118154.2506 | 2497909.7744 | 1118151.2424 | 2497916.3323 | 1118129.0955 | 2497903.2555 | 1118109.4149
20 | 2497903.2555 | 1118109.4149 | 2497896.0081 | 1118098.497
21 | 2497903.2555 | 1118109.4149 | 2497913.8974 | 1118102.9921
22 | 2497752.2909 | 1118139.5725 | 2497773.7689 | 1118129.7144 | 2497777.7176 | 1118128.1355
23 | 2497752.2909 | 1118139.5725 | 2497766.2705 | 1118168.8889
24 | 2497777.7176 | 1118128.1355 | 2497786.9116 | 1118123.6212
25 | 2497777.7176 | 1118128.1355 | 2497784.3073 | 1118142.3449
26 | 2497802.2004 | 1118116.1143 | 2497789.3341 | 1118087.9361
27 | 2497802.2004 | 1118116.1143 | 2497786.9116 | 1118123.6212
28 | 2497568.2099 | 1117935.3907 | 2497601.4809 | 1117937.6734 | 2497604.4733 | 1117937.9674 | 2497607.1702 | 1117939.0446 | 2497609.8624 | 1117940.7557 | 2497611.7159 | 1117943.0814 | 2497616.6176 | 1117941.7087 | 2497618.1558 | 1117930.4311 | 2497623.7796 | 1117926.5668 | 2497623.6761 | 1117922.7328 | 2497625.3229 | 1117917.8685 | 2497626.3966 | 1117914.715
29 | 2497568.2099 | 1117935.3907 | 2497567.2982 | 1117942.1771 | 2497562.2876 | 1117941.6839
30 | 2497626.3966 | 1117914.715 | 2497627.5199 | 1117911.7608
31 | 2497562.2876 | 1117941.6839 | 2497558.7597 | 1117943.9562 | 2497558.3537 | 1117950.6189
32 | 2497544.1669 | 1117904.6006 | 2497545.4962 | 1117885.2697
33 | 2497544.1669 | 1117904.6006 | 2497513.5348 | 1117901.8953
34 | 2497544.1669 | 1117904.6006 | 2497568.6554 | 1117906.5918
35 | 2497545.4962 | 1117885.2697 | 2497546.2847 | 1117873.8028
36 | 2497489.6957 | 1117894.4502 | 2497492.4817 | 1117897.1381 | 2497496.7176 | 1117899.2899 | 2497501.7078 | 1117900.8508 | 2497513.5348 | 1117901.8953
37 | 2497568.6554 | 1117906.5918 | 2497594.0829 | 1117908.6593
38 | 2497651.7227 | 1118000.8076 | 2497674.1517 | 1117991.9337 | 2497677.1958 | 1117990.7259 | 2497679.55 | 1117989.7966 | 2497701.565 | 1117981.0854 | 2497720.3214 | 1118018.403
39 | 2497651.7227 | 1118000.8076 | 2497642.5632 | 1118004.4311
40 | 2497720.3214 | 1118018.403 | 2497721.4097 | 1118020.6749 | 2497724.6995 | 1118019.3852 | 2497728.4713 | 1118027.8823 | 2497729.5139 | 1118030.098
41 | 2497605.0589 | 1118019.2679 | 2497642.5632 | 1118004.4311
42 | 2497627.5199 | 1117911.7608 | 2497612.1768 | 1117910.1305 | 2497602.5776 | 1117909.35
43 | 2497627.5199 | 1117911.7608 | 2497635.7286 | 1117912.6366
44 | 2497729.5139 | 1118030.098 | 2497729.5404 | 1118030.1542
45 | 2497489.6957 | 1117894.4502 | 2497487.8977 | 1117892.2126 | 2497486.0282 | 1117888.9422 | 2497484.5309 | 1117883.0417 | 2497483.8078 | 1117877.2725
46 | 2497483.8078 | 1117877.2725 | 2497486.2677 | 1117855.7172 | 2497487.1962 | 1117847.6537
47 | 2497487.1962 | 1117847.6537 | 2497489.5884 | 1117826.8785
48 | 2497525.1012 | 1118040.4094 | 2497519.2247 | 1118042.11 | 2497519.8291 | 1118045.4352 | 2497521.1928 | 1118048.9254 | 2497523.1274 | 1118051.939 | 2497525.1147 | 1118053.9622 | 2497528.9021 | 1118051.5187 | 2497537.3323 | 1118047.9181 | 2497555.1716 | 1118040.6225
49 | 2497555.1716 | 1118040.6225 | 2497556.3458 | 1118043.8602 | 2497559.4782 | 1118051.609
50 | 2497525.1012 | 1118040.4094 | 2497520.0827 | 1118023.7819
51 | 2497561.75 | 1118063.948 | 2497561.5909 | 1118056.8351 | 2497559.4782 | 1118051.609
52 | 2497599.2804 | 1118022.8756 | 2497598.8751 | 1118026.2957 | 2497603.7257 | 1118036.493
53 | 2497599.2804 | 1118022.8756 | 2497593.3707 | 1118025.355 | 2497603.5371 | 1118047.6859 | 2497600.3014 | 1118048.9748
54 | 2497570.2548 | 1118019.1869 | 2497570.9861 | 1118022.71 | 2497577.0179 | 1118020.6066 | 2497581.7681 | 1118018.9473 | 2497583.8334 | 1118018.2897 | 2497585.5354 | 1118022.6081 | 2497591.0857 | 1118020.3349 | 2497593.3707 | 1118025.355 | 2497599.2804 | 1118022.8756
55 | 2497599.2804 | 1118022.8756 | 2497600.5464 | 1118021.053 | 2497605.0589 | 1118019.2679
56 | 2497603.7257 | 1118036.493 | 2497606.4979 | 1118042.3209
57 | 2497561.75 | 1118063.948 | 2497564.2016 | 1118063.3061 | 2497600.3014 | 1118048.9748
58 | 2497600.3014 | 1118048.9748 | 2497607.3934 | 1118063.8975 | 2497635.1423 | 1118121.7795
59 | 2497570.2548 | 1118019.1869 | 2497565.3982 | 1118005.9051 | 2497564.5226 | 1118002.4108
60 | 2497558.6348 | 1117965.8853 | 2497558.3128 | 1117951.2906 | 2497558.3537 | 1117950.6189
61 | 2497560.5962 | 1117986.741 | 2497564.5226 | 1118002.4108
62 | 2497561.75 | 1118063.948 | 2497561.8432 | 1118068.0824 | 2497571.7524 | 1118091.5038
63 | 2497571.7524 | 1118091.5038 | 2497574.2565 | 1118097.4226
64 | 2497519.5511 | 1117959.3521 | 2497533.9699 | 1117977.9641 | 2497560.5962 | 1117986.741
65 | 2497519.5511 | 1117959.3521 | 2497520.7799 | 1117948.3164
66 | 2497560.5962 | 1117986.741 | 2497558.7782 | 1117972.3849 | 2497558.6348 | 1117965.8853
67 | 2497926.4784 | 1118095.3989 | 2497913.8974 | 1118102.9921
68 | 2497857.9724 | 1118043.2165 | 2497865.3636 | 1118055.6211
69 | 2497833.3543 | 1118155.1869 | 2497835.0563 | 1118158.7083
70 | 2497828.343 | 1118144.7464 | 2497831.5278 | 1118151.4079 | 2497833.3543 | 1118155.1869
71 | 2497609.2892 | 1118048.189 | 2497612.0929 | 1118054.0831
72 | 2497609.2892 | 1118048.189 | 2497606.4979 | 1118042.3209
73 | 2497798.4974 | 1118175.9836 | 2497796.9612 | 1118172.7093
74 | 2497792.841 | 1118161.5567 | 2497792.7314 | 1118163.7488 | 2497796.0536 | 1118170.7749 | 2497796.9612 | 1118172.7093
75 | 2497792.841 | 1118161.5567 | 2497792.0016 | 1118158.9359 | 2497784.3073 | 1118142.3449
76 | 2497744.0716 | 1118057.0593 | 2497735.7764 | 1118060.4349 | 2497728.4055 | 1118063.8821
77 | 2497744.0716 | 1118057.0593 | 2497767.9504 | 1118045.8264 | 2497770.6305 | 1118051.715
78 | 2497744.0716 | 1118057.0593 | 2497733.4158 | 1118038.1608 | 2497731.9384 | 1118035.2506 | 2497731.1857 | 1118033.6507
79 | 2497770.6305 | 1118051.715 | 2497776.3765 | 1118064.3401 | 2497778.1488 | 1118068.0499
80 | 2497731.1857 | 1118033.6507 | 2497729.5404 | 1118030.1542
81 | 2497801.7345 | 1118157.048 | 2497805.9616 | 1118154.5862 | 2497806.5163 | 1118154.1501
82 | 2497801.7345 | 1118157.048 | 2497794.0447 | 1118161.5252 | 2497792.841 | 1118161.5567
83 | 2497828.343 | 1118144.7464 | 2497821.145 | 1118144.5234 | 2497815.8192 | 1118146.837 | 2497806.5163 | 1118154.1501
84 | 2497780.1762 | 1118072.2934 | 2497781.9302 | 1118075.9647 | 2497786.1604 | 1118080.9853 | 2497789.3341 | 1118087.9361
85 | 2497547.5396 | 1117859.0036 | 2497547.5396 | 1117859.0036 | 2497547.0778 | 1117862.269 | 2497546.2847 | 1117873.8028
86 | 2497594.0829 | 1117908.6593 | 2497602.5776 | 1117909.35
87 | 2497597.3006 | 1117857.0724 | 2497605.6337 | 1117857.648
88 | 2497572.5704 | 1117855.3329 | 2497584.7469 | 1117856.2052 | 2497597.3006 | 1117857.0724
89 | 2497492.4852 | 1117801.7221 | 2497489.5884 | 1117826.8785
90 | 2497585.6217 | 1118122.4249 | 2497580.6276 | 1118112.4813 | 2497574.2565 | 1118097.4226
91 | 2497561.4671 | 1117854.5376 | 2497554.4958 | 1117854.0382
92 | 2497572.5704 | 1117855.3329 | 2497561.4671 | 1117854.5376
93 | 2497547.5396 | 1117859.0036 | 2497549.2041 | 1117856.5516 | 2497551.1931 | 1117855.0281 | 2497554.4958 | 1117854.0382 | 2497554.4958 | 1117854.0382
94 | 2497778.1488 | 1118068.0499 | 2497780.1762 | 1118072.2934
95 | 2497535.565 | 1117786.4827 | 2497565.266 | 1117801.8015
96 | 2497492.4852 | 1117801.7221 | 2497497.0576 | 1117800.4994 | 2497500.5914 | 1117799.9392 | 2497508.7859 | 1117803.8139 | 2497518.3309 | 1117804.9307 | 2497526.0818 | 1117801.7641 | 2497529.5165 | 1117795.8133 | 2497531.7144 | 1117790.6728 | 2497535.565 | 1117786.4827
97 | 2497857.9724 | 1118043.2165 | 2497850.5894 | 1118030.8257

## bus_geodata
| x | y | coords
0 | 2497827.5722 | 1117995.8189
1 | 2497860.5075 | 1118008.0392
2 | 2497780.2233 | 1117997.3773
3 | 2497936.5799 | 1118075.1421
4 | 2497942.8456 | 1118085.5207
5 | 2497926.743 | 1118078.5857
6 | 2497938.8769 | 1118087.916
7 | 2497877.8051 | 1118076.5015
8 | 2497872.695 | 1118067.9253
9 | 2497882.4307 | 1118084.2598
10 | 2497840.7437 | 1118096.9957
11 | 2497858.5836 | 1118126.3518
12 | 2497832.4184 | 1118101.3279
13 | 2497805.5195 | 1118039.0155
14 | 2497755.4206 | 1117975.4492
15 | 2497776.8306 | 1118010.4511
16 | 2497877.2595 | 1118157.0838
17 | 2497903.2555 | 1118109.4149
18 | 2497752.2909 | 1118139.5725
19 | 2497777.7176 | 1118128.1355
20 | 2497766.2705 | 1118168.8889
21 | 2497802.2004 | 1118116.1143
22 | 2497568.2099 | 1117935.3907
23 | 2497626.3966 | 1117914.715
24 | 2497562.2876 | 1117941.6839
25 | 2497544.1669 | 1117904.6006
26 | 2497545.4962 | 1117885.2697
27 | 2497513.5348 | 1117901.8953
28 | 2497568.6554 | 1117906.5918
29 | 2497651.7227 | 1118000.8076
30 | 2497720.3214 | 1118018.403
31 | 2497642.5632 | 1118004.4311
32 | 2497627.5199 | 1117911.7608
33 | 2497729.5139 | 1118030.098
34 | 2497489.6957 | 1117894.4502
35 | 2497483.8078 | 1117877.2725
36 | 2497487.1962 | 1117847.6537
37 | 2497555.1716 | 1118040.6225
38 | 2497525.1012 | 1118040.4094
39 | 2497559.4782 | 1118051.609
40 | 2497599.2804 | 1118022.8756
41 | 2497603.7257 | 1118036.493
42 | 2497600.3014 | 1118048.9748
43 | 2497570.2548 | 1118019.1869
44 | 2497605.0589 | 1118019.2679
45 | 2497558.3537 | 1117950.6189
46 | 2497564.5226 | 1118002.4108
47 | 2497561.75 | 1118063.948
48 | 2497635.1423 | 1118121.7795
49 | 2497520.0827 | 1118023.7819
50 | 2497571.7524 | 1118091.5038
51 | 2497519.5511 | 1117959.3522
52 | 2497560.5962 | 1117986.741
53 | 2497520.7799 | 1117948.3164
54 | 2497896.0081 | 1118098.497
55 | 2497913.8974 | 1118102.9921
56 | 2497926.4784 | 1118095.3989
57 | 2497635.7286 | 1117912.6366
58 | 2497865.3636 | 1118055.6211
59 | 2497835.0563 | 1118158.7083
60 | 2497833.3543 | 1118155.1869
61 | 2497612.0929 | 1118054.0831
62 | 2497609.2892 | 1118048.189
63 | 2497798.4974 | 1118175.9836
64 | 2497796.9612 | 1118172.7093
65 | 2497786.1562 | 1118025.6969
66 | 2497786.9116 | 1118123.6212
67 | 2497784.3073 | 1118142.3449
68 | 2497744.0716 | 1118057.0593
69 | 2497728.4055 | 1118063.8821
70 | 2497770.6305 | 1118051.715
71 | 2497731.1857 | 1118033.6507
72 | 2497801.7345 | 1118157.048
73 | 2497806.5163 | 1118154.1501
74 | 2497792.841 | 1118161.5567
75 | 2497828.343 | 1118144.7464
76 | 2497789.3341 | 1118087.9361
77 | 2497546.2847 | 1117873.8028
78 | 2497594.0829 | 1117908.6593
79 | 2497602.5776 | 1117909.35
80 | 2497605.6337 | 1117857.648
81 | 2497597.3006 | 1117857.0724
82 | 2497729.5404 | 1118030.1542
83 | 2497489.5884 | 1117826.8785
84 | 2497606.4979 | 1118042.3209
85 | 2497558.6348 | 1117965.8853
86 | 2497574.2565 | 1118097.4226
87 | 2497561.4671 | 1117854.5376
88 | 2497554.4958 | 1117854.0382
89 | 2497572.5704 | 1117855.3329
90 | 2497547.5396 | 1117859.0036
91 | 2497778.1488 | 1118068.0499
92 | 2497780.1762 | 1118072.2934
93 | 2497585.6217 | 1118122.4249
94 | 2497565.266 | 1117801.8015
95 | 2497535.565 | 1117786.4827
96 | 2497492.4852 | 1117801.7221
97 | 2497857.9724 | 1118043.2165
98 | 2497850.5894 | 1118030.8257
99 | 2497744.0716 | 1118057.0593

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1