## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6621-86_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6621-86_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6621-86_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6621-86_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6621-86_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6621-86_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6621-86_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_6621-86_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_6621-86_0_4_node_43 | 0.4 | n |  | TRUE
9 | bus_LV_6621-86_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_6621-86_0_4_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_6621-86_0_4_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_6621-86_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_6621-86_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_6621-86_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_6621-86_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_6621-86_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_6621-86_0_4_node_41 | 0.4 | n |  | TRUE
18 | bus_LV_6621-86_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_6621-86_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_6621-86_0_4_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_6621-86_0_4_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_6621-86_0_4_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_6621-86_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_6621-86_0_4_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_6621-86_0_4_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_6621-86_0_4_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_6621-86_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_6621-86_0_4_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_6621-86_0_4_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_6621-86_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_6621-86_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_6621-86_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_6621-86_0_4_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_6621-86_0_4_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_6621-86_0_4_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_6621-86_0_4_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_6621-86_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_6621-86_0_4_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_6621-86_0_4_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_6621-86_0_4_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_6621-86_0_4_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_6621-86_0_4_node_36 | 0.4 | n |  | TRUE
43 | bus_MV_658_0_node_117 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6621-86_0_4_load_0 | 0 | 0.015007 | 0.0037612 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6621-86_0_4_load_1 | 1 | 0.090031 | 0.022564 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6621-86_0_4_load_3 | 3 | 0.011787 | 0.0029542 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6621-86_0_4_load_4 | 4 | 0.024377 | 0.0061094 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6621-86_0_4_load_43 | 8 | 0.0063543 | 0.0015925 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6621-86_0_4_load_42 | 10 | 0.04597 | 0.011521 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6621-86_0_4_load_24 | 11 | 0.0063941 | 0.0016025 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6621-86_0_4_load_11 | 12 | 0.025016 | 0.0062697 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6621-86_0_4_load_8 | 13 | 0.013823 | 0.0034643 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6621-86_0_4_load_41 | 17 | 0.014064 | 0.0035249 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6621-86_0_4_load_40 | 21 | 0.015638 | 0.0039192 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6621-86_0_4_load_44 | 22 | 0.0012222 | 0.00030631 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6621-86_0_4_load_33 | 25 | 0.0058471 | 0.0014654 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6621-86_0_4_load_46 | 26 | 0.014269 | 0.003576 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6621-86_0_4_load_30 | 28 | 0.0028176 | 0.00070617 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6621-86_0_4_load_27 | 32 | 0.017726 | 0.0044425 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6621-86_0_4_load_45 | 33 | 0.060586 | 0.015184 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6621-86_0_4_load_39 | 34 | 0.00017703 | 4.4367e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6621-86_0_4_load_38 | 35 | 0.0010623 | 0.00026625 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6621-86_0_4_load_37 | 36 | 0.011164 | 0.002798 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6621-86_0_4_load_34 | 38 | 0.0056497 | 0.0014159 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6621-86_0_4_load_31 | 39 | 0.0089524 | 0.0022437 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6621-86_0_4_load_32 | 40 | 0.0088548 | 0.0022192 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6621-86_0_4_load_36 | 42 | 0.097654 | 0.024474 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6621-86_0_4_line_0 |  | 0 | 1 | 0.0085332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6621-86_0_4_line_1 |  | 0 | 2 | 0.015333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6621-86_0_4_line_2 |  | 1 | 3 | 0.01449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6621-86_0_4_line_3 |  | 2 | 4 | 0.014288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6621-86_0_4_line_4 |  | 2 | 5 | 0.07416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6621-86_0_4_line_5 |  | 2 | 6 | 0.072201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_6621-86_0_4_line_6 |  | 4 | 7 | 0.018226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6621-86_0_4_line_7 |  | 5 | 8 | 0.007904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6621-86_0_4_line_8 |  | 6 | 9 | 0.045648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_6621-86_0_4_line_9 |  | 6 | 10 | 0.050739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6621-86_0_4_line_10 |  | 7 | 12 | 0.0058261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6621-86_0_4_line_11 |  | 7 | 13 | 0.014891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6621-86_0_4_line_12 |  | 9 | 11 | 0.014353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_6621-86_0_4_line_13 |  | 11 | 14 | 0.015291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_6621-86_0_4_line_14 |  | 12 | 17 | 0.023305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6621-86_0_4_line_15 |  | 13 | 15 | 0.011563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6621-86_0_4_line_16 |  | 14 | 37 | 0.005834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_6621-86_0_4_line_17 |  | 14 | 23 | 0.056966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6621-86_0_4_line_18 |  | 15 | 16 | 0.28285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6621-86_0_4_line_19 |  | 16 | 26 | 0.028856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6621-86_0_4_line_20 |  | 18 | 19 | 0.17631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6621-86_0_4_line_21 |  | 18 | 20 | 0.049026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6621-86_0_4_line_22 |  | 18 | 21 | 0.0032469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6621-86_0_4_line_23 |  | 19 | 22 | 0.02005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6621-86_0_4_line_24 |  | 20 | 33 | 0.012667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6621-86_0_4_line_25 |  | 20 | 27 | 0.051415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6621-86_0_4_line_26 |  | 23 | 24 | 0.003438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6621-86_0_4_line_27 |  | 23 | 25 | 0.017941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6621-86_0_4_line_28 |  | 24 | 36 | 0.0011069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6621-86_0_4_line_29 |  | 25 | 38 | 0.014206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6621-86_0_4_line_30 |  | 27 | 28 | 0.039909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6621-86_0_4_line_31 |  | 28 | 39 | 0.0038376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6621-86_0_4_line_32 |  | 29 | 30 | 0.003606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6621-86_0_4_line_33 |  | 29 | 31 | 0.1057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6621-86_0_4_line_34 |  | 29 | 32 | 0.03583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6621-86_0_4_line_35 |  | 30 | 40 | 0.05041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6621-86_0_4_line_36 |  | 31 | 34 | 0.051411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6621-86_0_4_line_37 |  | 32 | 37 | 0.031793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6621-86_0_4_line_38 |  | 35 | 36 | 0.0039077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6621-86_0_4_line_39 |  | 37 | 41 | 0.003899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6621-86_0_4_line_40 |  | 39 | 40 | 0.0088997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6621-86_0_4_line_41 |  | 41 | 42 | 0.026691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6621-86_0_4_trafo_7 | 0.63 MVA 20/0.4 kV | 43 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2498288.829 | 1118904.8421 | 2498293.1613 | 1118912.1938
1 | 2498281.0432 | 1118891.6327 | 2498286.1439 | 1118900.2857 | 2498288.829 | 1118904.8421
2 | 2498300.5176 | 1118924.6772 | 2498293.1613 | 1118912.1938
3 | 2498281.0432 | 1118891.6327 | 2498282.9306 | 1118890.5002 | 2498293.2991 | 1118884.2879
4 | 2498257.3861 | 1118936.0696 | 2498260.7212 | 1118934.746 | 2498264.2126 | 1118935.3655 | 2498268.6749 | 1118932.6888 | 2498259.6579 | 1118918.7983 | 2498252.4698 | 1118911.3145 | 2498260.0888 | 1118904.0485 | 2498281.0432 | 1118891.6327
5 | 2498281.0432 | 1118891.6327 | 2498260.0888 | 1118904.0485 | 2498252.4698 | 1118911.3145 | 2498247.037 | 1118908.6153 | 2498241.0726 | 1118906.4254 | 2498233.408 | 1118907.3216 | 2498229.0414 | 1118903.3036 | 2498218.3324 | 1118899.8705
6 | 2498308.9336 | 1118874.9199 | 2498303.6077 | 1118878.1114 | 2498293.2991 | 1118884.2879
7 | 2498257.3861 | 1118936.0696 | 2498252.802 | 1118942.5175
8 | 2498217.0831 | 1118930.6443 | 2498233.408 | 1118907.3216 | 2498229.0414 | 1118903.3036 | 2498218.3324 | 1118899.8705
9 | 2498218.3324 | 1118899.8705 | 2498220.5271 | 1118883.0675 | 2498227.5536 | 1118872.6983 | 2498231.9544 | 1118860.8612 | 2498239.0805 | 1118855.9783
10 | 2498308.9336 | 1118874.9199 | 2498305.8842 | 1118869.9555
11 | 2498308.9336 | 1118874.9199 | 2498311.8693 | 1118873.2473 | 2498318.1008 | 1118882.9272
12 | 2498217.0831 | 1118930.6443 | 2498209.9194 | 1118943.0818
13 | 2498202.2877 | 1118956.3316 | 2498209.9194 | 1118943.0818
14 | 2498305.8842 | 1118869.9555 | 2498293.6862 | 1118850.0973
15 | 2498324.3596 | 1118892.6495 | 2498318.1008 | 1118882.9272
16 | 2498202.2877 | 1118956.3316 | 2498197.4699 | 1118953.0218
17 | 2498202.2877 | 1118956.3316 | 2498219.296 | 1118973.1449 | 2498233.4931 | 1118989.3941 | 2498240.0587 | 1118998.8785
18 | 2498324.3596 | 1118892.6495 | 2498325.4374 | 1118894.3213 | 2498330.0135 | 1118891.5204 | 2498337.3553 | 1118887.0387 | 2498340.1668 | 1118885.3237 | 2498342.3795 | 1118889.3112 | 2498357.3919 | 1118915.0418 | 2498359.7887 | 1118913.9119 | 2498369.6357 | 1118907.8649 | 2498365.978 | 1118901.022 | 2498364.4147 | 1118896.1786 | 2498364.3047 | 1118889.176 | 2498366.0847 | 1118882.1194 | 2498368.8681 | 1118878.2703 | 2498373.4943 | 1118873.8564 | 2498379.9612 | 1118871.046 | 2498385.3473 | 1118870.5107 | 2498394.3576 | 1118868.8583 | 2498382.9294 | 1118850.183 | 2498388.2134 | 1118847.2479 | 2498381.9595 | 1118836.5685 | 2498403.4539 | 1118823.1879 | 2498400.0971 | 1118816.7958 | 2498380.0696 | 1118827.4501 | 2498373.829 | 1118819.3943 | 2498371.5315 | 1118816.331 | 2498335.0598 | 1118838.202 | 2498332.3833 | 1118839.6813
19 | 2498323.1642 | 1118858.2924 | 2498338.2304 | 1118849.5781 | 2498332.3833 | 1118839.6813
20 | 2498131.3907 | 1119084.6839 | 2498137.9479 | 1119102.3624 | 2498140.8076 | 1119109.0184 | 2498142.503 | 1119112.0695 | 2498145.8178 | 1119114.1261 | 2498149.21 | 1119115.2808 | 2498152.8833 | 1119116.1751 | 2498156.642 | 1119116.1785 | 2498159.8185 | 1119115.5246 | 2498164.0514 | 1119114.3526 | 2498190.1702 | 1119107.0972 | 2498237.154 | 1119094.0762 | 2498235.5432 | 1119088.711 | 2498240.6356 | 1119086.7908 | 2498235.0301 | 1119066.9393 | 2498238.7887 | 1119056.3916 | 2498241.9659 | 1119052.1132
21 | 2498106.4398 | 1119054.0848 | 2498110.2453 | 1119062.8151 | 2498121.7663 | 1119089.26 | 2498131.3907 | 1119084.6839
22 | 2498131.3907 | 1119084.6839 | 2498134.2935 | 1119083.2293
23 | 2498225.2782 | 1119041.4873 | 2498232.8878 | 1119048.3414 | 2498239.6061 | 1119050.8521 | 2498241.9659 | 1119052.1132
24 | 2498118.4245 | 1119049.8803 | 2498106.4398 | 1119054.0848
25 | 2498106.4398 | 1119054.0848 | 2498099.789 | 1119040.4772 | 2498096.3328 | 1119031.8633 | 2498093.812 | 1119023.3449 | 2498092.2222 | 1119015.1109 | 2498091.3335 | 1119005.4309
26 | 2498240.0587 | 1118998.8785 | 2498237.6771 | 1119001.3645
27 | 2498240.0587 | 1118998.8785 | 2498244.0345 | 1118994.809 | 2498248.097 | 1118993.1396 | 2498254.5029 | 1118988.5865
28 | 2498237.6771 | 1119001.3645 | 2498238.3212 | 1119002.2647
29 | 2498266.3736 | 1118980.8798 | 2498263.8465 | 1118981.9454 | 2498254.5029 | 1118988.5865
30 | 2498091.3335 | 1119005.4309 | 2498091.4892 | 1118996.3559 | 2498093.0142 | 1118988.3807 | 2498095.7789 | 1118980.696 | 2498101.119 | 1118971.9449 | 2498103.6142 | 1118968.4494
31 | 2498105.8439 | 1118965.3259 | 2498103.6142 | 1118968.4494
32 | 2498140.2193 | 1118916.9962 | 2498142.2374 | 1118914.0048
33 | 2498142.2374 | 1118914.0048 | 2498138.2701 | 1118911.2476 | 2498155.4729 | 1118885.5306 | 2498161.0441 | 1118877.1982 | 2498163.3492 | 1118873.8351 | 2498172.8786 | 1118859.9326 | 2498166.0762 | 1118855.6555 | 2498169.7042 | 1118849.724 | 2498166.1804 | 1118847.6376 | 2498158.2406 | 1118836.3197 | 2498154.7531 | 1118831.353
34 | 2498142.2374 | 1118914.0048 | 2498171.5023 | 1118934.6779
35 | 2498140.2193 | 1118916.9962 | 2498138.1034 | 1118920.1338 | 2498111.0145 | 1118958.0824
36 | 2498154.7531 | 1118831.353 | 2498140.1806 | 1118831.3317 | 2498138.4589 | 1118831.761 | 2498137.0329 | 1118832.7857 | 2498135.7541 | 1118834.764 | 2498135.2438 | 1118837.919 | 2498135.2784 | 1118865.6751
37 | 2498197.4699 | 1118953.0218 | 2498171.5023 | 1118934.6779
38 | 2498238.3212 | 1119002.2647 | 2498240.5952 | 1119005.4426
39 | 2498197.4699 | 1118953.0218 | 2498195.4655 | 1118956.3687
40 | 2498111.0145 | 1118958.0824 | 2498105.8439 | 1118965.3259
41 | 2498195.4655 | 1118956.3687 | 2498173.7294 | 1118940.8779

## bus_geodata
| x | y | coords
0 | 2498288.829 | 1118904.8421
1 | 2498293.1613 | 1118912.1938
2 | 2498281.0432 | 1118891.6327
3 | 2498300.5176 | 1118924.6772
4 | 2498293.2991 | 1118884.2879
5 | 2498257.3861 | 1118936.0696
6 | 2498218.3324 | 1118899.8705
7 | 2498308.9336 | 1118874.9199
8 | 2498252.802 | 1118942.5175
9 | 2498217.0831 | 1118930.6443
10 | 2498239.0805 | 1118855.9783
11 | 2498209.9194 | 1118943.0818
12 | 2498305.8842 | 1118869.9555
13 | 2498318.1008 | 1118882.9272
14 | 2498202.2877 | 1118956.3316
15 | 2498324.3596 | 1118892.6495
16 | 2498332.3833 | 1118839.6813
17 | 2498293.6862 | 1118850.0973
18 | 2498131.3907 | 1119084.6839
19 | 2498241.9659 | 1119052.1132
20 | 2498106.4398 | 1119054.0848
21 | 2498134.2935 | 1119083.2293
22 | 2498225.2782 | 1119041.4873
23 | 2498240.0587 | 1118998.8785
24 | 2498237.6771 | 1119001.3645
25 | 2498254.5029 | 1118988.5865
26 | 2498323.1642 | 1118858.2924
27 | 2498091.3335 | 1119005.4309
28 | 2498103.6142 | 1118968.4494
29 | 2498142.2374 | 1118914.0048
30 | 2498140.2193 | 1118916.9962
31 | 2498154.7531 | 1118831.353
32 | 2498171.5023 | 1118934.6779
33 | 2498118.4245 | 1119049.8803
34 | 2498135.2784 | 1118865.6751
35 | 2498240.5952 | 1119005.4426
36 | 2498238.3212 | 1119002.2647
37 | 2498197.4699 | 1118953.0218
38 | 2498266.3736 | 1118980.8798
39 | 2498105.8439 | 1118965.3259
40 | 2498111.0145 | 1118958.0824
41 | 2498195.4655 | 1118956.3687
42 | 2498173.7294 | 1118940.8779
43 | 2498233.408 | 1118907.3216

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1