## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6630-27_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6630-27_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6630-27_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6630-27_0_5_node_33 | 0.4 | n |  | TRUE
4 | bus_LV_6630-27_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_6630-27_0_5_node_32 | 0.4 | n |  | TRUE
6 | bus_LV_6630-27_0_5_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_6630-27_0_5_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_6630-27_0_5_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_6630-27_0_5_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_6630-27_0_5_node_40 | 0.4 | n |  | TRUE
11 | bus_LV_6630-27_0_5_node_31 | 0.4 | n |  | TRUE
12 | bus_LV_6630-27_0_5_node_4 | 0.4 | n |  | TRUE
13 | bus_LV_6630-27_0_5_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_6630-27_0_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_6630-27_0_5_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_6630-27_0_5_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_6630-27_0_5_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_6630-27_0_5_node_48 | 0.4 | n |  | TRUE
19 | bus_LV_6630-27_0_5_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_6630-27_0_5_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_6630-27_0_5_node_75 | 0.4 | n |  | TRUE
22 | bus_LV_6630-27_0_5_node_76 | 0.4 | n |  | TRUE
23 | bus_LV_6630-27_0_5_node_47 | 0.4 | n |  | TRUE
24 | bus_LV_6630-27_0_5_node_149 | 0.4 | n |  | TRUE
25 | bus_LV_6630-27_0_5_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_6630-27_0_5_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_6630-27_0_5_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_6630-27_0_5_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_6630-27_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_6630-27_0_5_node_151 | 0.4 | n |  | TRUE
31 | bus_LV_6630-27_0_5_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_6630-27_0_5_node_152 | 0.4 | n |  | TRUE
33 | bus_LV_6630-27_0_5_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_6630-27_0_5_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_6630-27_0_5_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_6630-27_0_5_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_6630-27_0_5_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_6630-27_0_5_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_6630-27_0_5_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_6630-27_0_5_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_6630-27_0_5_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_6630-27_0_5_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_6630-27_0_5_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_6630-27_0_5_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_6630-27_0_5_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_6630-27_0_5_node_72 | 0.4 | n |  | TRUE
47 | bus_LV_6630-27_0_5_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_6630-27_0_5_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_6630-27_0_5_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_6630-27_0_5_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_6630-27_0_5_node_54 | 0.4 | n |  | TRUE
52 | bus_LV_6630-27_0_5_node_55 | 0.4 | n |  | TRUE
53 | bus_LV_6630-27_0_5_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_6630-27_0_5_node_73 | 0.4 | n |  | TRUE
55 | bus_LV_6630-27_0_5_node_148 | 0.4 | n |  | TRUE
56 | bus_LV_6630-27_0_5_node_150 | 0.4 | n |  | TRUE
57 | bus_LV_6630-27_0_5_node_147 | 0.4 | n |  | TRUE
58 | bus_LV_6630-27_0_5_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_6630-27_0_5_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_6630-27_0_5_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_6630-27_0_5_node_58 | 0.4 | n |  | TRUE
62 | bus_LV_6630-27_0_5_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_6630-27_0_5_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_6630-27_0_5_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_6630-27_0_5_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_6630-27_0_5_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_6630-27_0_5_node_85 | 0.4 | n |  | TRUE
68 | bus_LV_6630-27_0_5_node_64 | 0.4 | n |  | TRUE
69 | bus_LV_6630-27_0_5_node_83 | 0.4 | n |  | TRUE
70 | bus_LV_6630-27_0_5_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_6630-27_0_5_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_6630-27_0_5_node_80 | 0.4 | n |  | TRUE
73 | bus_LV_6630-27_0_5_node_127 | 0.4 | n |  | TRUE
74 | bus_LV_6630-27_0_5_node_97 | 0.4 | n |  | TRUE
75 | bus_LV_6630-27_0_5_node_78 | 0.4 | n |  | TRUE
76 | bus_LV_6630-27_0_5_node_126 | 0.4 | n |  | TRUE
77 | bus_LV_6630-27_0_5_node_95 | 0.4 | n |  | TRUE
78 | bus_LV_6630-27_0_5_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_6630-27_0_5_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_6630-27_0_5_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_6630-27_0_5_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_6630-27_0_5_node_63 | 0.4 | n |  | TRUE
83 | bus_LV_6630-27_0_5_node_110 | 0.4 | n |  | TRUE
84 | bus_LV_6630-27_0_5_node_98 | 0.4 | n |  | TRUE
85 | bus_LV_6630-27_0_5_node_108 | 0.4 | n |  | TRUE
86 | bus_LV_6630-27_0_5_node_96 | 0.4 | n |  | TRUE
87 | bus_LV_6630-27_0_5_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_6630-27_0_5_node_67 | 0.4 | n |  | TRUE
89 | bus_LV_6630-27_0_5_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_6630-27_0_5_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_6630-27_0_5_node_70 | 0.4 | n |  | TRUE
92 | bus_LV_6630-27_0_5_node_71 | 0.4 | n |  | TRUE
93 | bus_LV_6630-27_0_5_node_104 | 0.4 | n |  | TRUE
94 | bus_LV_6630-27_0_5_node_90 | 0.4 | n |  | TRUE
95 | bus_LV_6630-27_0_5_node_87 | 0.4 | n |  | TRUE
96 | bus_LV_6630-27_0_5_node_137 | 0.4 | n |  | TRUE
97 | bus_LV_6630-27_0_5_node_141 | 0.4 | n |  | TRUE
98 | bus_LV_6630-27_0_5_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_6630-27_0_5_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_6630-27_0_5_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_6630-27_0_5_node_74 | 0.4 | n |  | TRUE
102 | bus_LV_6630-27_0_5_node_143 | 0.4 | n |  | TRUE
103 | bus_LV_6630-27_0_5_node_106 | 0.4 | n |  | TRUE
104 | bus_LV_6630-27_0_5_node_77 | 0.4 | n |  | TRUE
105 | bus_LV_6630-27_0_5_node_79 | 0.4 | n |  | TRUE
106 | bus_LV_6630-27_0_5_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_6630-27_0_5_node_91 | 0.4 | n |  | TRUE
108 | bus_LV_6630-27_0_5_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_6630-27_0_5_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_6630-27_0_5_node_82 | 0.4 | n |  | TRUE
111 | bus_LV_6630-27_0_5_node_89 | 0.4 | n |  | TRUE
112 | bus_LV_6630-27_0_5_node_146 | 0.4 | n |  | TRUE
113 | bus_LV_6630-27_0_5_node_111 | 0.4 | n |  | TRUE
114 | bus_LV_6630-27_0_5_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_6630-27_0_5_node_117 | 0.4 | n |  | TRUE
116 | bus_LV_6630-27_0_5_node_118 | 0.4 | n |  | TRUE
117 | bus_LV_6630-27_0_5_node_94 | 0.4 | n |  | TRUE
118 | bus_LV_6630-27_0_5_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_6630-27_0_5_node_100 | 0.4 | n |  | TRUE
120 | bus_LV_6630-27_0_5_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_6630-27_0_5_node_102 | 0.4 | n |  | TRUE
122 | bus_LV_6630-27_0_5_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_6630-27_0_5_node_133 | 0.4 | n |  | TRUE
124 | bus_LV_6630-27_0_5_node_134 | 0.4 | n |  | TRUE
125 | bus_LV_6630-27_0_5_node_135 | 0.4 | n |  | TRUE
126 | bus_LV_6630-27_0_5_node_138 | 0.4 | n |  | TRUE
127 | bus_LV_6630-27_0_5_node_136 | 0.4 | n |  | TRUE
128 | bus_LV_6630-27_0_5_node_140 | 0.4 | n |  | TRUE
129 | bus_LV_6630-27_0_5_node_107 | 0.4 | n |  | TRUE
130 | bus_LV_6630-27_0_5_node_109 | 0.4 | n |  | TRUE
131 | bus_LV_6630-27_0_5_node_112 | 0.4 | n |  | TRUE
132 | bus_LV_6630-27_0_5_node_113 | 0.4 | n |  | TRUE
133 | bus_LV_6630-27_0_5_node_114 | 0.4 | n |  | TRUE
134 | bus_LV_6630-27_0_5_node_115 | 0.4 | n |  | TRUE
135 | bus_LV_6630-27_0_5_node_116 | 0.4 | n |  | TRUE
136 | bus_LV_6630-27_0_5_node_139 | 0.4 | n |  | TRUE
137 | bus_LV_6630-27_0_5_node_125 | 0.4 | n |  | TRUE
138 | bus_LV_6630-27_0_5_node_131 | 0.4 | n |  | TRUE
139 | bus_LV_6630-27_0_5_node_123 | 0.4 | n |  | TRUE
140 | bus_LV_6630-27_0_5_node_124 | 0.4 | n |  | TRUE
141 | bus_LV_6630-27_0_5_node_119 | 0.4 | n |  | TRUE
142 | bus_LV_6630-27_0_5_node_120 | 0.4 | n |  | TRUE
143 | bus_LV_6630-27_0_5_node_121 | 0.4 | n |  | TRUE
144 | bus_LV_6630-27_0_5_node_122 | 0.4 | n |  | TRUE
145 | bus_LV_6630-27_0_5_node_128 | 0.4 | n |  | TRUE
146 | bus_LV_6630-27_0_5_node_129 | 0.4 | n |  | TRUE
147 | bus_LV_6630-27_0_5_node_130 | 0.4 | n |  | TRUE
148 | bus_LV_6630-27_0_5_node_132 | 0.4 | n |  | TRUE
149 | bus_LV_6630-27_0_5_node_144 | 0.4 | n |  | TRUE
150 | bus_LV_6630-27_0_5_node_145 | 0.4 | n |  | TRUE
151 | bus_LV_6630-27_0_5_node_142 | 0.4 | n |  | TRUE
152 | bus_MV_665_0_node_20 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6630-27_0_5_load_0 | 0 | 0.001534 | 0.00038445 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6630-27_0_5_load_1 | 1 | 0.0031183 | 0.00078152 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6630-27_0_5_load_2 | 2 | 0.00044052 | 0.0001104 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6630-27_0_5_load_33 | 3 | 0.0042017 | 0.001053 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6630-27_0_5_load_3 | 4 | 0.0008488 | 0.00021273 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6630-27_0_5_load_10 | 6 | 0.0067454 | 0.0016906 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6630-27_0_5_load_11 | 7 | 0.00044519 | 0.00011158 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6630-27_0_5_load_13 | 9 | 0.00085275 | 0.00021372 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6630-27_0_5_load_40 | 10 | 0.003051 | 0.00076466 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6630-27_0_5_load_31 | 11 | 0.0015886 | 0.00039815 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6630-27_0_5_load_4 | 12 | 0.0027677 | 0.00069364 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6630-27_0_5_load_5 | 13 | 0.0017734 | 0.00044445 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6630-27_0_5_load_7 | 15 | 0.00078058 | 0.00019563 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6630-27_0_5_load_8 | 16 | 0.0024152 | 0.0006053 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6630-27_0_5_load_30 | 17 | 0.00083453 | 0.00020915 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6630-27_0_5_load_48 | 18 | 0.006904 | 0.0017303 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6630-27_0_5_load_9 | 20 | 0.0052736 | 0.0013217 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6630-27_0_5_load_75 | 21 | 0.00031072 | 7.7874e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6630-27_0_5_load_76 | 22 | 0.00045743 | 0.00011464 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6630-27_0_5_load_47 | 23 | 0.014052 | 0.0035218 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6630-27_0_5_load_149 | 24 | 0.0035218 | 0.00088265 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6630-27_0_5_load_37 | 25 | 0.00042426 | 0.00010633 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6630-27_0_5_load_36 | 26 | 0.001559 | 0.00039071 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6630-27_0_5_load_151 | 30 | 0.01855 | 0.0046492 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6630-27_0_5_load_152 | 32 | 0.0068017 | 0.0017047 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6630-27_0_5_load_39 | 33 | 0.00043125 | 0.00010808 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6630-27_0_5_load_17 | 34 | 0.00042126 | 0.00010558 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6630-27_0_5_load_19 | 35 | 0.0015251 | 0.00038224 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6630-27_0_5_load_20 | 36 | 0.0019505 | 0.00048885 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6630-27_0_5_load_21 | 37 | 0.0013049 | 0.00032704 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6630-27_0_5_load_22 | 38 | 0.0020468 | 0.00051297 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6630-27_0_5_load_23 | 39 | 0.0018102 | 0.00045367 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6630-27_0_5_load_24 | 40 | 0.00038267 | 9.5905e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6630-27_0_5_load_26 | 42 | 0.001358 | 0.00034034 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6630-27_0_5_load_34 | 43 | 0.00059682 | 0.00014958 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6630-27_0_5_load_35 | 44 | 0.00028529 | 7.1501e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6630-27_0_5_load_41 | 45 | 0.0010383 | 0.00026022 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6630-27_0_5_load_72 | 46 | 0.00057746 | 0.00014473 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6630-27_0_5_load_27 | 47 | 0.0017 | 0.00042605 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6630-27_0_5_load_29 | 48 | 0.0026871 | 0.00067345 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6630-27_0_5_load_44 | 49 | 0.0045223 | 0.0011334 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6630-27_0_5_load_54 | 51 | 0.002619 | 0.00065637 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6630-27_0_5_load_55 | 52 | 0.002007 | 0.00050301 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6630-27_0_5_load_73 | 54 | 0.00022291 | 5.5865e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6630-27_0_5_load_150 | 56 | 0.0014429 | 0.00036162 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6630-27_0_5_load_147 | 57 | 0.00036776 | 9.2168e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6630-27_0_5_load_42 | 58 | 0.00045109 | 0.00011305 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6630-27_0_5_load_43 | 59 | 0.000587 | 0.00014712 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6630-27_0_5_load_46 | 60 | 0.0025089 | 0.00062879 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6630-27_0_5_load_58 | 61 | 0.0018793 | 0.00047099 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6630-27_0_5_load_49 | 62 | 0.0018907 | 0.00047386 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6630-27_0_5_load_50 | 63 | 0.0018248 | 0.00045733 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6630-27_0_5_load_51 | 64 | 0.002568 | 0.00064361 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6630-27_0_5_load_52 | 65 | 0.0029364 | 0.00073594 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6630-27_0_5_load_53 | 66 | 0.0013158 | 0.00032978 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6630-27_0_5_load_85 | 67 | 0.0024387 | 0.00061121 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6630-27_0_5_load_64 | 68 | 0.0016865 | 0.00042267 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6630-27_0_5_load_83 | 69 | 0.0015077 | 0.00037786 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6630-27_0_5_load_65 | 70 | 0.00072611 | 0.00018198 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6630-27_0_5_load_127 | 73 | 0.00077389 | 0.00019396 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6630-27_0_5_load_97 | 74 | 0.0016876 | 0.00042296 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6630-27_0_5_load_78 | 75 | 0.00042456 | 0.00010641 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6630-27_0_5_load_126 | 76 | 0.00067478 | 0.00016911 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6630-27_0_5_load_95 | 77 | 0.0018267 | 0.00045781 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6630-27_0_5_load_59 | 78 | 0.00069996 | 0.00017543 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6630-27_0_5_load_60 | 79 | 0.0017753 | 0.00044494 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6630-27_0_5_load_61 | 80 | 0.0014015 | 0.00035124 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6630-27_0_5_load_62 | 81 | 0.0011393 | 0.00028553 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6630-27_0_5_load_63 | 82 | 0.0029389 | 0.00073655 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6630-27_0_5_load_110 | 83 | 0.00097837 | 0.0002452 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6630-27_0_5_load_98 | 84 | 0.002912 | 0.00072982 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6630-27_0_5_load_108 | 85 | 0.0014266 | 0.00035754 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6630-27_0_5_load_96 | 86 | 0.00093774 | 0.00023502 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6630-27_0_5_load_66 | 87 | 0.0018743 | 0.00046974 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6630-27_0_5_load_67 | 88 | 0.0016467 | 0.0004127 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6630-27_0_5_load_68 | 89 | 0.00050035 | 0.0001254 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6630-27_0_5_load_69 | 90 | 0.0014351 | 0.00035967 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6630-27_0_5_load_70 | 91 | 0.00027932 | 7.0005e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6630-27_0_5_load_90 | 94 | 0.0030394 | 0.00076175 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6630-27_0_5_load_87 | 95 | 0.001967 | 0.00049298 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6630-27_0_5_load_141 | 97 | 0.0015871 | 0.00039777 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6630-27_0_5_load_86 | 98 | 0.0026824 | 0.00067227 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6630-27_0_5_load_88 | 100 | 0.00062107 | 0.00015565 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6630-27_0_5_load_74 | 101 | 0.00081255 | 0.00020365 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6630-27_0_5_load_143 | 102 | 0.0012926 | 0.00032397 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6630-27_0_5_load_106 | 103 | 0.00040835 | 0.00010234 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6630-27_0_5_load_77 | 104 | 0.0010171 | 0.00025491 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6630-27_0_5_load_81 | 106 | 0.0019219 | 0.00048169 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_6630-27_0_5_load_92 | 108 | 0.002266 | 0.00056792 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_6630-27_0_5_load_93 | 109 | 0.00043094 | 0.000108 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_6630-27_0_5_load_82 | 110 | 0.0016182 | 0.00040555 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_6630-27_0_5_load_89 | 111 | 0.00062121 | 0.00015569 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_6630-27_0_5_load_146 | 112 | 0.00098372 | 0.00024654 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_6630-27_0_5_load_111 | 113 | 0.002107 | 0.00052806 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_6630-27_0_5_load_105 | 114 | 0.0017948 | 0.00044981 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_6630-27_0_5_load_117 | 115 | 0.001715 | 0.00042982 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_6630-27_0_5_load_118 | 116 | 0.00033265 | 8.3371e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_6630-27_0_5_load_94 | 117 | 0.0018671 | 0.00046794 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_6630-27_0_5_load_99 | 118 | 0.00094923 | 0.0002379 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_6630-27_0_5_load_100 | 119 | 0.0012374 | 0.00031012 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_6630-27_0_5_load_101 | 120 | 0.00031992 | 8.0179e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_6630-27_0_5_load_103 | 122 | 0.0011061 | 0.00027721 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_6630-27_0_5_load_134 | 124 | 0.00048883 | 0.00012251 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_6630-27_0_5_load_135 | 125 | 0.00086258 | 0.00021618 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_6630-27_0_5_load_138 | 126 | 0.00097546 | 0.00024447 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_6630-27_0_5_load_136 | 127 | 0.00074965 | 0.00018788 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_6630-27_0_5_load_140 | 128 | 0.0008241 | 0.00020654 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_6630-27_0_5_load_107 | 129 | 0.0018667 | 0.00046784 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_6630-27_0_5_load_109 | 130 | 0.0017493 | 0.00043842 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_6630-27_0_5_load_112 | 131 | 0.0029333 | 0.00073514 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_6630-27_0_5_load_113 | 132 | 0.0011613 | 0.00029104 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_6630-27_0_5_load_114 | 133 | 0.0017802 | 0.00044616 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_6630-27_0_5_load_116 | 135 | 0.0014709 | 0.00036865 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_6630-27_0_5_load_139 | 136 | 0.00069935 | 0.00017527 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_6630-27_0_5_load_125 | 137 | 0.00046318 | 0.00011608 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_6630-27_0_5_load_131 | 138 | 0.0024669 | 0.00061827 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_6630-27_0_5_load_123 | 139 | 0.0010249 | 0.00025687 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_6630-27_0_5_load_124 | 140 | 0.0010648 | 0.00026685 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_6630-27_0_5_load_119 | 141 | 0.0011031 | 0.00027645 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_6630-27_0_5_load_120 | 142 | 0.001869 | 0.00046843 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_6630-27_0_5_load_121 | 143 | 0.0043603 | 0.0010928 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_6630-27_0_5_load_128 | 145 | 0.0012861 | 0.00032234 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_6630-27_0_5_load_129 | 146 | 0.0020765 | 0.00052041 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_6630-27_0_5_load_130 | 147 | 0.0021035 | 0.00052718 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_6630-27_0_5_load_144 | 149 | 0.00085715 | 0.00021482 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_6630-27_0_5_load_145 | 150 | 0.0011963 | 0.00029983 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_6630-27_0_5_load_142 | 151 | 0.0015307 | 0.00038363 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6630-27_0_5_line_0 |  | 0 | 1 | 0.061186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_6630-27_0_5_line_1 |  | 0 | 2 | 0.062783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_6630-27_0_5_line_2 |  | 1 | 3 | 0.12105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_6630-27_0_5_line_3 |  | 2 | 4 | 0.025664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_6630-27_0_5_line_4 |  | 3 | 5 | 0.01707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_6630-27_0_5_line_5 |  | 4 | 10 | 0.0099176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_6630-27_0_5_line_6 |  | 5 | 19 | 0.079704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_6630-27_0_5_line_7 |  | 5 | 16 | 0.053904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_6630-27_0_5_line_8 |  | 6 | 7 | 0.018334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_6630-27_0_5_line_9 |  | 6 | 8 | 0.05006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_6630-27_0_5_line_10 |  | 7 | 9 | 0.024041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_6630-27_0_5_line_11 |  | 8 | 27 | 0.041461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_6630-27_0_5_line_12 |  | 8 | 28 | 0.00671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6630-27_0_5_line_13 |  | 9 | 29 | 0.032755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_6630-27_0_5_line_14 |  | 10 | 11 | 0.060942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_6630-27_0_5_line_15 |  | 11 | 37 | 0.0084846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_6630-27_0_5_line_16 |  | 12 | 13 | 0.031705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6630-27_0_5_line_17 |  | 12 | 14 | 0.0045999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6630-27_0_5_line_18 |  | 13 | 15 | 0.0047662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6630-27_0_5_line_19 |  | 14 | 16 | 0.0033957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6630-27_0_5_line_20 |  | 15 | 17 | 0.007287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6630-27_0_5_line_21 |  | 17 | 18 | 0.016878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6630-27_0_5_line_22 |  | 19 | 34 | 0.016734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_6630-27_0_5_line_23 |  | 20 | 21 | 0.055816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6630-27_0_5_line_24 |  | 21 | 22 | 0.0037105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6630-27_0_5_line_25 |  | 22 | 23 | 0.14101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6630-27_0_5_line_26 |  | 23 | 24 | 0.13019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6630-27_0_5_line_27 |  | 24 | 25 | 0.10629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_6630-27_0_5_line_28 |  | 24 | 57 | 0.018897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6630-27_0_5_line_29 |  | 25 | 26 | 0.021107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_6630-27_0_5_line_30 |  | 26 | 31 | 0.039547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_6630-27_0_5_line_31 |  | 27 | 30 | 0.021018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6630-27_0_5_line_32 |  | 27 | 31 | 0.11271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_6630-27_0_5_line_33 |  | 28 | 32 | 0.016146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6630-27_0_5_line_34 |  | 29 | 34 | 0.011763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_6630-27_0_5_line_35 |  | 31 | 33 | 0.020866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_6630-27_0_5_line_36 |  | 33 | 42 | 0.028016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_6630-27_0_5_line_37 |  | 35 | 36 | 0.062218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6630-27_0_5_line_38 |  | 36 | 37 | 0.051176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_6630-27_0_5_line_39 |  | 38 | 39 | 0.011801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_6630-27_0_5_line_40 |  | 38 | 40 | 0.001403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_6630-27_0_5_line_41 |  | 39 | 41 | 0.02257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_6630-27_0_5_line_42 |  | 40 | 42 | 0.017133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_6630-27_0_5_line_43 |  | 41 | 43 | 0.021524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6630-27_0_5_line_44 |  | 41 | 44 | 0.017239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_6630-27_0_5_line_45 |  | 43 | 45 | 0.025624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6630-27_0_5_line_46 |  | 44 | 46 | 0.024859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_6630-27_0_5_line_47 |  | 46 | 54 | 0.02196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_6630-27_0_5_line_48 |  | 47 | 48 | 0.012325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6630-27_0_5_line_49 |  | 47 | 49 | 0.072487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6630-27_0_5_line_50 |  | 49 | 50 | 0.038341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6630-27_0_5_line_51 |  | 50 | 60 | 0.010254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6630-27_0_5_line_52 |  | 50 | 59 | 0.015347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6630-27_0_5_line_53 |  | 51 | 52 | 0.036838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6630-27_0_5_line_54 |  | 51 | 53 | 0.019422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6630-27_0_5_line_55 |  | 52 | 71 | 0.018488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6630-27_0_5_line_56 |  | 53 | 61 | 0.033591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_6630-27_0_5_line_57 |  | 53 | 60 | 0.030472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_6630-27_0_5_line_58 |  | 54 | 101 | 0.020032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_6630-27_0_5_line_59 |  | 55 | 56 | 0.006232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6630-27_0_5_line_60 |  | 55 | 57 | 0.020364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6630-27_0_5_line_61 |  | 58 | 59 | 0.0081475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6630-27_0_5_line_62 |  | 61 | 74 | 0.017821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_6630-27_0_5_line_63 |  | 62 | 63 | 0.010854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6630-27_0_5_line_64 |  | 62 | 64 | 0.028195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6630-27_0_5_line_65 |  | 63 | 65 | 0.019773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6630-27_0_5_line_66 |  | 64 | 66 | 0.0059883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6630-27_0_5_line_67 |  | 65 | 67 | 0.01543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6630-27_0_5_line_68 |  | 66 | 68 | 0.031485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6630-27_0_5_line_69 |  | 67 | 69 | 0.020558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6630-27_0_5_line_70 |  | 68 | 70 | 0.025338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6630-27_0_5_line_71 |  | 69 | 110 | 0.016133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6630-27_0_5_line_72 |  | 70 | 87 | 0.011923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6630-27_0_5_line_73 |  | 71 | 72 | 0.017892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6630-27_0_5_line_74 |  | 71 | 73 | 0.017376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6630-27_0_5_line_75 |  | 72 | 75 | 0.017464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6630-27_0_5_line_76 |  | 73 | 76 | 0.028536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6630-27_0_5_line_77 |  | 74 | 77 | 0.017599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_6630-27_0_5_line_78 |  | 75 | 104 | 0.018021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6630-27_0_5_line_79 |  | 76 | 87 | 0.012665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6630-27_0_5_line_80 |  | 77 | 117 | 0.00081454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_6630-27_0_5_line_81 |  | 78 | 79 | 0.0048828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_6630-27_0_5_line_82 |  | 78 | 80 | 0.0023794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_6630-27_0_5_line_83 |  | 79 | 81 | 0.01589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_6630-27_0_5_line_84 |  | 80 | 82 | 0.029011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_6630-27_0_5_line_85 |  | 81 | 83 | 0.00067071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_6630-27_0_5_line_86 |  | 82 | 84 | 0.0015064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_6630-27_0_5_line_87 |  | 83 | 85 | 0.01191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_6630-27_0_5_line_88 |  | 84 | 86 | 0.02428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_6630-27_0_5_line_89 |  | 85 | 129 | 0.025527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_6630-27_0_5_line_90 |  | 86 | 117 | 0.009915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_6630-27_0_5_line_91 |  | 88 | 89 | 0.018184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_6630-27_0_5_line_92 |  | 88 | 90 | 0.0072141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_6630-27_0_5_line_93 |  | 89 | 91 | 0.017942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_6630-27_0_5_line_94 |  | 90 | 92 | 0.026207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_6630-27_0_5_line_95 |  | 91 | 93 | 0.010256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_6630-27_0_5_line_96 |  | 92 | 94 | 0.02226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_6630-27_0_5_line_97 |  | 92 | 95 | 0.020899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_6630-27_0_5_line_98 |  | 93 | 96 | 0.024107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_6630-27_0_5_line_99 |  | 93 | 97 | 0.025662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_6630-27_0_5_line_100 |  | 95 | 100 | 0.0018836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_6630-27_0_5_line_101 |  | 96 | 126 | 0.0025972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_6630-27_0_5_line_102 |  | 96 | 127 | 0.024207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_6630-27_0_5_line_103 |  | 97 | 128 | 0.021768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_6630-27_0_5_line_104 |  | 98 | 99 | 0.022588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_6630-27_0_5_line_105 |  | 99 | 110 | 0.032943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_6630-27_0_5_line_106 |  | 100 | 111 | 0.0097813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_6630-27_0_5_line_107 |  | 101 | 102 | 0.036251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_6630-27_0_5_line_108 |  | 102 | 103 | 0.015428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_6630-27_0_5_line_109 |  | 103 | 121 | 0.028024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_6630-27_0_5_line_110 |  | 104 | 105 | 0.020603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_6630-27_0_5_line_111 |  | 105 | 106 | 0.024209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_6630-27_0_5_line_112 |  | 106 | 107 | 0.022937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_6630-27_0_5_line_113 |  | 107 | 108 | 0.049986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_6630-27_0_5_line_114 |  | 107 | 109 | 0.0020465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_6630-27_0_5_line_115 |  | 108 | 114 | 0.0042735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_6630-27_0_5_line_116 |  | 109 | 115 | 0.020817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_6630-27_0_5_line_117 |  | 111 | 112 | 0.016509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_6630-27_0_5_line_118 |  | 112 | 113 | 0.00022567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_6630-27_0_5_line_119 |  | 113 | 130 | 0.028276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_6630-27_0_5_line_120 |  | 115 | 116 | 0.0029105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_6630-27_0_5_line_121 |  | 116 | 140 | 0.029329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_6630-27_0_5_line_122 |  | 118 | 119 | 0.034567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_6630-27_0_5_line_123 |  | 118 | 120 | 0.020891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_6630-27_0_5_line_124 |  | 119 | 121 | 0.0072664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_6630-27_0_5_line_125 |  | 120 | 122 | 0.034063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_6630-27_0_5_line_126 |  | 122 | 123 | 0.029957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_6630-27_0_5_line_127 |  | 123 | 124 | 0.024175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_6630-27_0_5_line_128 |  | 123 | 125 | 0.025597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_6630-27_0_5_line_129 |  | 124 | 126 | 0.014668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_6630-27_0_5_line_130 |  | 128 | 151 | 0.010042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_6630-27_0_5_line_131 |  | 129 | 130 | 0.0040052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_6630-27_0_5_line_132 |  | 131 | 132 | 0.038284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_6630-27_0_5_line_133 |  | 131 | 133 | 0.0023834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_6630-27_0_5_line_134 |  | 132 | 134 | 0.019778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_6630-27_0_5_line_135 |  | 133 | 135 | 0.018443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_6630-27_0_5_line_136 |  | 134 | 136 | 0.0079751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_6630-27_0_5_line_137 |  | 134 | 137 | 0.025691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_6630-27_0_5_line_138 |  | 136 | 138 | 0.006786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_6630-27_0_5_line_139 |  | 137 | 139 | 0.0074669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_6630-27_0_5_line_140 |  | 138 | 144 | 0.004323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_6630-27_0_5_line_141 |  | 139 | 140 | 0.026407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_6630-27_0_5_line_142 |  | 141 | 142 | 0.00099357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_6630-27_0_5_line_143 |  | 141 | 143 | 0.022829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_6630-27_0_5_line_144 |  | 142 | 144 | 0.017741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_6630-27_0_5_line_145 |  | 144 | 145 | 0.031238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_6630-27_0_5_line_146 |  | 145 | 146 | 0.034704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_6630-27_0_5_line_147 |  | 146 | 147 | 0.0041282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_6630-27_0_5_line_148 |  | 147 | 148 | 0.030953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_6630-27_0_5_line_149 |  | 148 | 149 | 0.040661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_6630-27_0_5_line_150 |  | 149 | 150 | 0.00040783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6630-27_0_5_trafo_46 | 0.63 MVA 20/0.4 kV | 152 | 60 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2496457.2846 | 1121011.4596 | 2496463.1612 | 1121037.3366 | 2496466.4727 | 1121048.2312 | 2496469.0383 | 1121054.3245 | 2496471.9408 | 1121059.8116 | 2496475.392 | 1121065.3561 | 2496477.7749 | 1121068.4603
1 | 2496421.6086 | 1120959.7985 | 2496457.2846 | 1121011.4596
2 | 2496366.9432 | 1121117.1355 | 2496477.7749 | 1121068.4603
3 | 2496401.2768 | 1120944.1384 | 2496421.6086 | 1120959.7985
4 | 2496356.403 | 1121130.5802 | 2496358.7624 | 1121127.7935 | 2496366.9432 | 1121117.1355
5 | 2496401.2768 | 1120944.1384 | 2496393.4196 | 1120938.0866
6 | 2496356.403 | 1121130.5802 | 2496400.478 | 1121196.9892
7 | 2496356.403 | 1121130.5802 | 2496315.5385 | 1121095.4268
8 | 2496478.7318 | 1121194.4246 | 2496482.8814 | 1121195.8328 | 2496488.9256 | 1121198.2642 | 2496495.5045 | 1121201.7316
9 | 2496537.728 | 1121228.6149 | 2496524.3076 | 1121220.3059 | 2496501.9916 | 1121205.7008 | 2496495.5045 | 1121201.7316
10 | 2496478.7318 | 1121194.4246 | 2496477.9225 | 1121194.15 | 2496470.0529 | 1121191.9055 | 2496455.3989 | 1121188.6889
11 | 2496537.728 | 1121228.6149 | 2496531.0777 | 1121236.7449 | 2496509.2425 | 1121258.7659
12 | 2496537.728 | 1121228.6149 | 2496542.3665 | 1121223.7547
13 | 2496423.697 | 1121180.5366 | 2496430.3308 | 1121182.7021 | 2496436.1891 | 1121184.1916 | 2496444.6819 | 1121186.3364 | 2496455.3989 | 1121188.6889
14 | 2496393.4196 | 1120938.0866 | 2496345.1386 | 1120900.8993
15 | 2496338.4168 | 1120895.7219 | 2496345.1386 | 1120900.8993
16 | 2496285.9596 | 1121068.9664 | 2496296.9987 | 1121078.2544 | 2496309.6073 | 1121090.0673
17 | 2496312.9642 | 1121093.2123 | 2496309.6073 | 1121090.0673
18 | 2496282.3126 | 1121065.8979 | 2496285.9596 | 1121068.9664
19 | 2496312.9642 | 1121093.2123 | 2496315.5385 | 1121095.4268
20 | 2496282.3126 | 1121065.8979 | 2496276.7366 | 1121061.2064
21 | 2496276.7366 | 1121061.2064 | 2496275.8381 | 1121060.4505 | 2496263.8147 | 1121050.3485
22 | 2496400.478 | 1121196.9892 | 2496409.6172 | 1121191.3847 | 2496414.3296 | 1121187.6495
23 | 2496675.8291 | 1121569.8885 | 2496731.0427 | 1121578.0659
24 | 2496673.096 | 1121567.3789 | 2496675.8291 | 1121569.8885
25 | 2496620.9081 | 1121436.3841 | 2496673.096 | 1121567.3789
26 | 2496505.3975 | 1121496.449 | 2496620.9081 | 1121436.3841
27 | 2496483.5313 | 1121392.4288 | 2496505.3975 | 1121496.449
28 | 2496505.3975 | 1121496.449 | 2496496.0486 | 1121502.4017 | 2496490.0351 | 1121507.1521 | 2496489.9273 | 1121507.2569
29 | 2496483.5313 | 1121392.4288 | 2496468.0589 | 1121378.0724
30 | 2496442.1126 | 1121349.306 | 2496442.7123 | 1121352.7868 | 2496443.5669 | 1121354.9291 | 2496445.2193 | 1121356.8131 | 2496448.819 | 1121360.2203 | 2496468.0589 | 1121378.0724
31 | 2496509.2425 | 1121258.7659 | 2496496.1886 | 1121248.4272 | 2496492.3705 | 1121246.2356
32 | 2496442.1126 | 1121349.306 | 2496509.2425 | 1121258.7659
33 | 2496542.3665 | 1121223.7547 | 2496546.6099 | 1121227.8068 | 2496549.844 | 1121227.8849 | 2496555.0868 | 1121232.6315
34 | 2496423.697 | 1121180.5366 | 2496417.6174 | 1121185.0436 | 2496414.3296 | 1121187.6495
35 | 2496442.1126 | 1121349.306 | 2496437.545 | 1121353.3423 | 2496429.2566 | 1121365.5675
36 | 2496429.2566 | 1121365.5675 | 2496423.4207 | 1121374.1752 | 2496418.5706 | 1121381.0849 | 2496417.4637 | 1121382.6716 | 2496413.5275 | 1121388.7484
37 | 2496297.9452 | 1120864.3999 | 2496248.8286 | 1120826.2074
38 | 2496338.4168 | 1120895.7219 | 2496320.6756 | 1120882.0572 | 2496297.9452 | 1120864.3999
39 | 2496403.4501 | 1121404.3061 | 2496397.0347 | 1121414.2104
40 | 2496404.2129 | 1121403.1286 | 2496403.4501 | 1121404.3061
41 | 2496384.8309 | 1121433.196 | 2496390.0522 | 1121424.9903 | 2496397.0347 | 1121414.2104
42 | 2496404.2129 | 1121403.1286 | 2496413.5275 | 1121388.7484
43 | 2496384.8309 | 1121433.196 | 2496374.5397 | 1121425.134 | 2496367.8852 | 1121419.9244
44 | 2496384.8309 | 1121433.196 | 2496376.1812 | 1121446.1747 | 2496375.2703 | 1121447.5411
45 | 2496347.6274 | 1121404.2358 | 2496352.956 | 1121408.2265 | 2496359.8223 | 1121413.6122 | 2496367.8852 | 1121419.9244
46 | 2496361.4815 | 1121468.2248 | 2496375.2703 | 1121447.5411
47 | 2496349.3008 | 1121486.4971 | 2496359.6639 | 1121470.9513 | 2496361.4815 | 1121468.2248
48 | 2496284.0441 | 1121261.6485 | 2496294.5377 | 1121268.1125
49 | 2496320.2398 | 1121335.8902 | 2496294.5377 | 1121268.1125
50 | 2496297.0526 | 1121366.4252 | 2496303.1335 | 1121358.4158 | 2496314.3148 | 1121343.6925 | 2496320.2398 | 1121335.8902
51 | 2496297.0526 | 1121366.4252 | 2496293.317 | 1121363.643 | 2496288.8348 | 1121360.2915
52 | 2496297.0526 | 1121366.4252 | 2496309.3448 | 1121375.614
53 | 2496249.7958 | 1121329.2614 | 2496232.7864 | 1121316.6183 | 2496220.2281 | 1121307.2893
54 | 2496264.9975 | 1121341.3369 | 2496256.6611 | 1121334.3644 | 2496249.7958 | 1121329.2614
55 | 2496205.3872 | 1121296.2646 | 2496220.2281 | 1121307.2893
56 | 2496264.9975 | 1121341.3369 | 2496252.7247 | 1121357.6356 | 2496244.7004 | 1121368.1019
57 | 2496264.9975 | 1121341.3369 | 2496275.2789 | 1121350.155 | 2496288.8348 | 1121360.2915
58 | 2496349.3008 | 1121486.4971 | 2496345.674 | 1121491.9378 | 2496339.1411 | 1121501.0333 | 2496337.801 | 1121502.8963
59 | 2496480.5933 | 1121524.7916 | 2496475.3207 | 1121521.4464
60 | 2496475.3207 | 1121521.4464 | 2496489.9273 | 1121507.2569
61 | 2496309.3448 | 1121375.614 | 2496312.5661 | 1121378.0221 | 2496315.8709 | 1121380.4918
62 | 2496233.8593 | 1121382.2467 | 2496241.081 | 1121372.8228 | 2496244.7004 | 1121368.1019
63 | 2496106.5371 | 1121423.9853 | 2496102.5685 | 1121429.2259 | 2496099.9865 | 1121432.6395
64 | 2496106.5371 | 1121423.9853 | 2496114.5707 | 1121413.3763 | 2496119.711 | 1121406.7616 | 2496122.3451 | 1121403.3586 | 2496123.696 | 1121401.6132
65 | 2496088.0473 | 1121448.4012 | 2496095.7791 | 1121438.1928 | 2496099.2795 | 1121433.5741 | 2496099.9865 | 1121432.6395
66 | 2496123.696 | 1121401.6132 | 2496125.4848 | 1121399.3021 | 2496127.364 | 1121396.8798
67 | 2496088.0473 | 1121448.4012 | 2496078.7314 | 1121460.701
68 | 2496146.6578 | 1121371.9989 | 2496138.0595 | 1121383.0869 | 2496135.4858 | 1121386.411 | 2496127.364 | 1121396.8798
69 | 2496078.7314 | 1121460.701 | 2496077.4779 | 1121462.3559 | 2496071.1166 | 1121470.6372 | 2496069.6484 | 1121472.2968 | 2496066.0752 | 1121476.8958
70 | 2496146.6578 | 1121371.9989 | 2496158.8388 | 1121356.2908 | 2496162.1846 | 1121351.9759
71 | 2496056.1772 | 1121489.6355 | 2496066.0752 | 1121476.8958
72 | 2496169.4909 | 1121342.5534 | 2496162.1846 | 1121351.9759
73 | 2496205.3872 | 1121296.2646 | 2496191.2715 | 1121285.2221
74 | 2496205.3872 | 1121296.2646 | 2496194.739 | 1121309.9952
75 | 2496191.2715 | 1121285.2221 | 2496177.9599 | 1121273.918
76 | 2496177.2515 | 1121332.5449 | 2496177.6332 | 1121332.0527 | 2496194.739 | 1121309.9952
77 | 2496233.8593 | 1121382.2467 | 2496230.2977 | 1121386.8946 | 2496223.1549 | 1121396.2163
78 | 2496177.9599 | 1121273.918 | 2496177.014 | 1121273.1148 | 2496173.068 | 1121269.7693 | 2496164.2203 | 1121262.2571
79 | 2496177.2515 | 1121332.5449 | 2496169.4909 | 1121342.5534
80 | 2496223.1549 | 1121396.2163 | 2496222.6595 | 1121396.8629
81 | 2496181.787 | 1121450.0684 | 2496178.8049 | 1121453.9348
82 | 2496183.2402 | 1121448.1843 | 2496181.787 | 1121450.0684
83 | 2496178.8049 | 1121453.9348 | 2496176.0695 | 1121457.4814 | 2496169.0968 | 1121466.5138
84 | 2496183.2402 | 1121448.1843 | 2496186.6805 | 1121443.7238 | 2496195.3521 | 1121432.49 | 2496200.9412 | 1121425.1988
85 | 2496169.0968 | 1121466.5138 | 2496168.687 | 1121467.0448
86 | 2496201.8576 | 1121424.0032 | 2496200.9412 | 1121425.1988
87 | 2496168.687 | 1121467.0448 | 2496163.9792 | 1121473.1434 | 2496162.8397 | 1121474.6305 | 2496161.4145 | 1121476.4768
88 | 2496216.629 | 1121404.7331 | 2496201.8576 | 1121424.0032
89 | 2496145.8155 | 1121496.6828 | 2496161.4145 | 1121476.4768
90 | 2496216.629 | 1121404.7331 | 2496216.6319 | 1121404.7293 | 2496222.6595 | 1121396.8629
91 | 2496121.8758 | 1121581.711 | 2496135.1818 | 1121594.1045
92 | 2496116.9869 | 1121576.4124 | 2496120.9054 | 1121580.8071 | 2496121.8758 | 1121581.711
93 | 2496148.3067 | 1121606.3385 | 2496144.8971 | 1121603.1536 | 2496135.1818 | 1121594.1045
94 | 2496095.9744 | 1121561.2675 | 2496111.2296 | 1121569.9554 | 2496116.9869 | 1121576.4124
95 | 2496155.705 | 1121613.4412 | 2496148.6371 | 1121606.6472 | 2496148.3067 | 1121606.3385
96 | 2496095.9744 | 1121561.2675 | 2496086.5732 | 1121573.5703 | 2496085.8185 | 1121574.5505 | 2496082.4511 | 1121578.9484
97 | 2496095.9744 | 1121561.2675 | 2496108.7438 | 1121544.723
98 | 2496155.705 | 1121613.4412 | 2496164.6691 | 1121622.3929 | 2496173.1493 | 1121630.1189
99 | 2496155.705 | 1121613.4412 | 2496163.7187 | 1121603.8975 | 2496167.2724 | 1121599.6894 | 2496172.2599 | 1121593.8339
100 | 2496109.8947 | 1121543.2319 | 2496108.7438 | 1121544.723
101 | 2496173.1493 | 1121630.1189 | 2496175.0524 | 1121631.8863
102 | 2496173.1493 | 1121630.1189 | 2496156.0658 | 1121647.2691
103 | 2496186.3759 | 1121577.2639 | 2496179.5838 | 1121585.2354 | 2496172.2599 | 1121593.8339
104 | 2496036.0084 | 1121515.6471 | 2496053.9855 | 1121529.3236
105 | 2496036.0084 | 1121515.6471 | 2496038.5711 | 1121513.0347 | 2496055.964 | 1121489.9099 | 2496056.1772 | 1121489.6355
106 | 2496109.8947 | 1121543.2319 | 2496115.8711 | 1121535.4887
107 | 2496337.801 | 1121502.8963 | 2496335.0193 | 1121506.7632 | 2496324.3666 | 1121520.7992 | 2496315.5603 | 1121531.5106
108 | 2496305.6233 | 1121543.3114 | 2496311.8594 | 1121536.0122 | 2496315.5603 | 1121531.5106
109 | 2496287.0318 | 1121564.2781 | 2496300.4165 | 1121549.4058 | 2496305.6233 | 1121543.3114
110 | 2496148.5146 | 1121248.9222 | 2496164.2203 | 1121262.2571
111 | 2496148.5146 | 1121248.9222 | 2496140.1223 | 1121251.2789 | 2496131.6873 | 1121262.3753 | 2496130.7468 | 1121263.6122
112 | 2496116.8697 | 1121281.8755 | 2496127.7641 | 1121267.5348 | 2496130.7468 | 1121263.6122
113 | 2496116.8697 | 1121281.8755 | 2496086.2611 | 1121254.384 | 2496079.6602 | 1121248.4982
114 | 2496116.8697 | 1121281.8755 | 2496115.6463 | 1121283.5162
115 | 2496076.4725 | 1121245.652 | 2496079.5696 | 1121248.4175 | 2496079.6602 | 1121248.4982
116 | 2496115.6463 | 1121283.5162 | 2496110.5123 | 1121290.4013 | 2496103.2 | 1121300.2024
117 | 2496115.8711 | 1121535.4887 | 2496119.3771 | 1121530.9462 | 2496125.955 | 1121522.4177
118 | 2496126.0928 | 1121522.239 | 2496125.955 | 1121522.4177
119 | 2496143.3679 | 1121499.8532 | 2496136.6743 | 1121508.5237 | 2496133.2708 | 1121512.9405 | 2496126.9465 | 1121521.1321 | 2496126.0928 | 1121522.239
120 | 2496101.4596 | 1121302.5352 | 2496103.2 | 1121300.2024
121 | 2496083.9282 | 1121326.0473 | 2496096.6059 | 1121309.041 | 2496101.4596 | 1121302.5352
122 | 2496259.3511 | 1121595.6437 | 2496278.3971 | 1121574.0658 | 2496282.2247 | 1121569.7272
123 | 2496259.3511 | 1121595.6437 | 2496251.7816 | 1121604.2193 | 2496245.5272 | 1121611.3072
124 | 2496287.0318 | 1121564.2781 | 2496282.2247 | 1121569.7272
125 | 2496222.9875 | 1121636.8466 | 2496231.6291 | 1121627.0574 | 2496245.5272 | 1121611.3072
126 | 2496202.8463 | 1121659.0162 | 2496210.9696 | 1121650.4602 | 2496222.9875 | 1121636.8466
127 | 2496202.8463 | 1121659.0162 | 2496190.4072 | 1121646.722 | 2496185.6547 | 1121642.0193
128 | 2496202.8463 | 1121659.0162 | 2496195.33 | 1121666.5278 | 2496184.5935 | 1121676.9614
129 | 2496185.6547 | 1121642.0193 | 2496180.9422 | 1121637.3563 | 2496175.0524 | 1121631.8863
130 | 2496192.8889 | 1121569.6199 | 2496186.3759 | 1121577.2639
131 | 2496143.3679 | 1121499.8532 | 2496145.8155 | 1121496.6828
132 | 2496031.8952 | 1121333.9348 | 2496019.2642 | 1121350.4968 | 2496032.8814 | 1121361.4165
133 | 2496033.3405 | 1121332.0397 | 2496031.8952 | 1121333.9348
134 | 2496048.3114 | 1121373.7899 | 2496032.8814 | 1121361.4165
135 | 2496044.5248 | 1121317.3748 | 2496033.3405 | 1121332.0397
136 | 2496048.3114 | 1121373.7899 | 2496047.6848 | 1121374.5901 | 2496043.1188 | 1121379.8415
137 | 2496048.3114 | 1121373.7899 | 2496052.5872 | 1121368.0572 | 2496063.6731 | 1121353.1979
138 | 2496038.6662 | 1121384.9625 | 2496043.1188 | 1121379.8415
139 | 2496063.6731 | 1121353.1979 | 2496068.1382 | 1121347.2131
140 | 2496035.8297 | 1121388.2248 | 2496038.6662 | 1121384.9625
141 | 2496068.1382 | 1121347.2131 | 2496068.8463 | 1121346.2639 | 2496077.202 | 1121335.0576 | 2496083.4916 | 1121326.6331 | 2496083.9282 | 1121326.0473
142 | 2496021.7148 | 1121377.4767 | 2496020.9243 | 1121376.8748
143 | 2496002.7613 | 1121363.0442 | 2496020.9243 | 1121376.8748
144 | 2496035.8297 | 1121388.2248 | 2496021.7148 | 1121377.4767
145 | 2496035.8297 | 1121388.2248 | 2496020.829 | 1121407.3616 | 2496016.559 | 1121412.811
146 | 2496016.559 | 1121412.811 | 2496014.1705 | 1121415.8593 | 2496009.3087 | 1121422.0579 | 2495995.15 | 1121440.1241
147 | 2495995.15 | 1121440.1241 | 2495992.6035 | 1121443.3733
148 | 2495973.51 | 1121467.7361 | 2495992.6035 | 1121443.3733
149 | 2495973.51 | 1121467.7361 | 2495948.4854 | 1121448.6434 | 2495941.1839 | 1121443.0714
150 | 2495940.8597 | 1121442.8239 | 2495941.1839 | 1121443.0714

## bus_geodata
| x | y | coords
0 | 2496457.2846 | 1121011.4596
1 | 2496477.7749 | 1121068.4603
2 | 2496421.6086 | 1120959.7985
3 | 2496366.9432 | 1121117.1355
4 | 2496401.2768 | 1120944.1384
5 | 2496356.403 | 1121130.5802
6 | 2496495.5045 | 1121201.7316
7 | 2496478.7318 | 1121194.4246
8 | 2496537.728 | 1121228.6149
9 | 2496455.3989 | 1121188.6889
10 | 2496393.4196 | 1120938.0866
11 | 2496345.1386 | 1120900.8993
12 | 2496309.6073 | 1121090.0673
13 | 2496285.9596 | 1121068.9664
14 | 2496312.9642 | 1121093.2123
15 | 2496282.3126 | 1121065.8979
16 | 2496315.5385 | 1121095.4268
17 | 2496276.7366 | 1121061.2064
18 | 2496263.8147 | 1121050.3485
19 | 2496400.478 | 1121196.9892
20 | 2496731.0427 | 1121578.0659
21 | 2496675.8291 | 1121569.8885
22 | 2496673.096 | 1121567.3789
23 | 2496620.9081 | 1121436.3841
24 | 2496505.3975 | 1121496.449
25 | 2496483.5313 | 1121392.4288
26 | 2496468.0589 | 1121378.0724
27 | 2496509.2425 | 1121258.7659
28 | 2496542.3665 | 1121223.7547
29 | 2496423.697 | 1121180.5366
30 | 2496492.3705 | 1121246.2356
31 | 2496442.1126 | 1121349.306
32 | 2496555.0868 | 1121232.6315
33 | 2496429.2566 | 1121365.5675
34 | 2496414.3296 | 1121187.6495
35 | 2496248.8286 | 1120826.2074
36 | 2496297.9452 | 1120864.3999
37 | 2496338.4168 | 1120895.7219
38 | 2496403.4501 | 1121404.3061
39 | 2496397.0347 | 1121414.2104
40 | 2496404.2129 | 1121403.1286
41 | 2496384.8309 | 1121433.196
42 | 2496413.5275 | 1121388.7484
43 | 2496367.8852 | 1121419.9244
44 | 2496375.2703 | 1121447.5411
45 | 2496347.6274 | 1121404.2358
46 | 2496361.4815 | 1121468.2248
47 | 2496294.5377 | 1121268.1125
48 | 2496284.0441 | 1121261.6485
49 | 2496320.2398 | 1121335.8902
50 | 2496297.0526 | 1121366.4252
51 | 2496249.7958 | 1121329.2614
52 | 2496220.2281 | 1121307.2893
53 | 2496264.9975 | 1121341.3369
54 | 2496349.3008 | 1121486.4971
55 | 2496475.3207 | 1121521.4465
56 | 2496480.5933 | 1121524.7916
57 | 2496489.9273 | 1121507.2569
58 | 2496315.8709 | 1121380.4918
59 | 2496309.3448 | 1121375.614
60 | 2496288.8348 | 1121360.2915
61 | 2496244.7004 | 1121368.1019
62 | 2496106.5371 | 1121423.9853
63 | 2496099.9865 | 1121432.6395
64 | 2496123.696 | 1121401.6132
65 | 2496088.0473 | 1121448.4012
66 | 2496127.364 | 1121396.8798
67 | 2496078.7313 | 1121460.701
68 | 2496146.6578 | 1121371.9989
69 | 2496066.0752 | 1121476.8958
70 | 2496162.1846 | 1121351.9759
71 | 2496205.3872 | 1121296.2646
72 | 2496191.2715 | 1121285.2221
73 | 2496194.739 | 1121309.9952
74 | 2496233.8593 | 1121382.2467
75 | 2496177.9599 | 1121273.918
76 | 2496177.2515 | 1121332.5449
77 | 2496223.1549 | 1121396.2163
78 | 2496181.787 | 1121450.0684
79 | 2496178.8049 | 1121453.9348
80 | 2496183.2402 | 1121448.1843
81 | 2496169.0968 | 1121466.5138
82 | 2496200.9412 | 1121425.1988
83 | 2496168.687 | 1121467.0448
84 | 2496201.8576 | 1121424.0032
85 | 2496161.4145 | 1121476.4768
86 | 2496216.629 | 1121404.7331
87 | 2496169.4909 | 1121342.5534
88 | 2496121.8758 | 1121581.711
89 | 2496135.1818 | 1121594.1045
90 | 2496116.9869 | 1121576.4124
91 | 2496148.3067 | 1121606.3385
92 | 2496095.9744 | 1121561.2675
93 | 2496155.705 | 1121613.4412
94 | 2496082.4511 | 1121578.9484
95 | 2496108.7438 | 1121544.723
96 | 2496173.1493 | 1121630.1189
97 | 2496172.2599 | 1121593.8339
98 | 2496053.9855 | 1121529.3236
99 | 2496036.0084 | 1121515.6471
100 | 2496109.8947 | 1121543.2319
101 | 2496337.801 | 1121502.8963
102 | 2496315.5603 | 1121531.5106
103 | 2496305.6233 | 1121543.3114
104 | 2496164.2203 | 1121262.2571
105 | 2496148.5146 | 1121248.9222
106 | 2496130.7468 | 1121263.6122
107 | 2496116.8697 | 1121281.8755
108 | 2496079.6602 | 1121248.4982
109 | 2496115.6463 | 1121283.5162
110 | 2496056.1772 | 1121489.6355
111 | 2496115.8711 | 1121535.4887
112 | 2496125.955 | 1121522.4177
113 | 2496126.0928 | 1121522.239
114 | 2496076.4725 | 1121245.652
115 | 2496103.2 | 1121300.2024
116 | 2496101.4596 | 1121302.5352
117 | 2496222.6595 | 1121396.8629
118 | 2496259.3511 | 1121595.6437
119 | 2496282.2247 | 1121569.7272
120 | 2496245.5272 | 1121611.3072
121 | 2496287.0318 | 1121564.2781
122 | 2496222.9875 | 1121636.8466
123 | 2496202.8463 | 1121659.0162
124 | 2496185.6547 | 1121642.0193
125 | 2496184.5935 | 1121676.9614
126 | 2496175.0524 | 1121631.8863
127 | 2496156.0658 | 1121647.2691
128 | 2496186.3759 | 1121577.2639
129 | 2496145.8155 | 1121496.6828
130 | 2496143.3679 | 1121499.8532
131 | 2496031.8952 | 1121333.9348
132 | 2496032.8814 | 1121361.4165
133 | 2496033.3405 | 1121332.0397
134 | 2496048.3114 | 1121373.7899
135 | 2496044.5248 | 1121317.3748
136 | 2496043.1188 | 1121379.8415
137 | 2496063.6731 | 1121353.1979
138 | 2496038.6662 | 1121384.9625
139 | 2496068.1382 | 1121347.2131
140 | 2496083.9282 | 1121326.0473
141 | 2496020.9243 | 1121376.8748
142 | 2496021.7148 | 1121377.4767
143 | 2496002.7613 | 1121363.0442
144 | 2496035.8297 | 1121388.2248
145 | 2496016.559 | 1121412.811
146 | 2495995.15 | 1121440.1241
147 | 2495992.6035 | 1121443.3733
148 | 2495973.51 | 1121467.7361
149 | 2495941.1839 | 1121443.0714
150 | 2495940.8597 | 1121442.8239
151 | 2496192.8889 | 1121569.6199
152 | 2496288.8348 | 1121360.2915

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1