## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6630-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6630-3_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6630-3_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6630-3_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6630-3_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6630-3_0_5_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_6630-3_0_5_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_6630-3_0_5_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_6630-3_0_5_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_6630-3_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_6630-3_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_6630-3_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_6630-3_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_6630-3_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_6630-3_0_5_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_6630-3_0_5_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_6630-3_0_5_node_152 | 0.4 | n |  | TRUE
17 | bus_LV_6630-3_0_5_node_159 | 0.4 | n |  | TRUE
18 | bus_LV_6630-3_0_5_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_6630-3_0_5_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_6630-3_0_5_node_96 | 0.4 | n |  | TRUE
21 | bus_LV_6630-3_0_5_node_94 | 0.4 | n |  | TRUE
22 | bus_LV_6630-3_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_6630-3_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_6630-3_0_5_node_107 | 0.4 | n |  | TRUE
25 | bus_LV_6630-3_0_5_node_106 | 0.4 | n |  | TRUE
26 | bus_LV_6630-3_0_5_node_153 | 0.4 | n |  | TRUE
27 | bus_LV_6630-3_0_5_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_6630-3_0_5_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_6630-3_0_5_node_56 | 0.4 | n |  | TRUE
30 | bus_LV_6630-3_0_5_node_141 | 0.4 | n |  | TRUE
31 | bus_LV_6630-3_0_5_node_99 | 0.4 | n |  | TRUE
32 | bus_LV_6630-3_0_5_node_155 | 0.4 | n |  | TRUE
33 | bus_LV_6630-3_0_5_node_108 | 0.4 | n |  | TRUE
34 | bus_LV_6630-3_0_5_node_105 | 0.4 | n |  | TRUE
35 | bus_LV_6630-3_0_5_node_130 | 0.4 | n |  | TRUE
36 | bus_LV_6630-3_0_5_node_95 | 0.4 | n |  | TRUE
37 | bus_LV_6630-3_0_5_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_6630-3_0_5_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_6630-3_0_5_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_6630-3_0_5_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_6630-3_0_5_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_6630-3_0_5_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_6630-3_0_5_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_6630-3_0_5_node_151 | 0.4 | n |  | TRUE
45 | bus_LV_6630-3_0_5_node_113 | 0.4 | n |  | TRUE
46 | bus_LV_6630-3_0_5_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_6630-3_0_5_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_6630-3_0_5_node_150 | 0.4 | n |  | TRUE
49 | bus_LV_6630-3_0_5_node_147 | 0.4 | n |  | TRUE
50 | bus_LV_6630-3_0_5_node_118 | 0.4 | n |  | TRUE
51 | bus_LV_6630-3_0_5_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_6630-3_0_5_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_6630-3_0_5_node_53 | 0.4 | n |  | TRUE
54 | bus_LV_6630-3_0_5_node_90 | 0.4 | n |  | TRUE
55 | bus_LV_6630-3_0_5_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_6630-3_0_5_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_6630-3_0_5_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_6630-3_0_5_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_6630-3_0_5_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_6630-3_0_5_node_148 | 0.4 | n |  | TRUE
61 | bus_LV_6630-3_0_5_node_41 | 0.4 | n |  | TRUE
62 | bus_LV_6630-3_0_5_node_144 | 0.4 | n |  | TRUE
63 | bus_LV_6630-3_0_5_node_38 | 0.4 | n |  | TRUE
64 | bus_LV_6630-3_0_5_node_146 | 0.4 | n |  | TRUE
65 | bus_LV_6630-3_0_5_node_122 | 0.4 | n |  | TRUE
66 | bus_LV_6630-3_0_5_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_6630-3_0_5_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_6630-3_0_5_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_6630-3_0_5_node_104 | 0.4 | n |  | TRUE
70 | bus_LV_6630-3_0_5_node_110 | 0.4 | n |  | TRUE
71 | bus_LV_6630-3_0_5_node_149 | 0.4 | n |  | TRUE
72 | bus_LV_6630-3_0_5_node_42 | 0.4 | n |  | TRUE
73 | bus_LV_6630-3_0_5_node_83 | 0.4 | n |  | TRUE
74 | bus_LV_6630-3_0_5_node_86 | 0.4 | n |  | TRUE
75 | bus_LV_6630-3_0_5_node_43 | 0.4 | n |  | TRUE
76 | bus_LV_6630-3_0_5_node_111 | 0.4 | n |  | TRUE
77 | bus_LV_6630-3_0_5_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_6630-3_0_5_node_45 | 0.4 | n |  | TRUE
79 | bus_LV_6630-3_0_5_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_6630-3_0_5_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_6630-3_0_5_node_46 | 0.4 | n |  | TRUE
82 | bus_LV_6630-3_0_5_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_6630-3_0_5_node_51 | 0.4 | n |  | TRUE
84 | bus_LV_6630-3_0_5_node_47 | 0.4 | n |  | TRUE
85 | bus_LV_6630-3_0_5_node_48 | 0.4 | n |  | TRUE
86 | bus_LV_6630-3_0_5_node_60 | 0.4 | n |  | TRUE
87 | bus_LV_6630-3_0_5_node_156 | 0.4 | n |  | TRUE
88 | bus_LV_6630-3_0_5_node_52 | 0.4 | n |  | TRUE
89 | bus_LV_6630-3_0_5_node_140 | 0.4 | n |  | TRUE
90 | bus_LV_6630-3_0_5_node_50 | 0.4 | n |  | TRUE
91 | bus_LV_6630-3_0_5_node_55 | 0.4 | n |  | TRUE
92 | bus_LV_6630-3_0_5_node_142 | 0.4 | n |  | TRUE
93 | bus_LV_6630-3_0_5_node_120 | 0.4 | n |  | TRUE
94 | bus_LV_6630-3_0_5_node_154 | 0.4 | n |  | TRUE
95 | bus_LV_6630-3_0_5_node_58 | 0.4 | n |  | TRUE
96 | bus_LV_6630-3_0_5_node_145 | 0.4 | n |  | TRUE
97 | bus_LV_6630-3_0_5_node_121 | 0.4 | n |  | TRUE
98 | bus_LV_6630-3_0_5_node_98 | 0.4 | n |  | TRUE
99 | bus_LV_6630-3_0_5_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_6630-3_0_5_node_115 | 0.4 | n |  | TRUE
101 | bus_LV_6630-3_0_5_node_71 | 0.4 | n |  | TRUE
102 | bus_LV_6630-3_0_5_node_65 | 0.4 | n |  | TRUE
103 | bus_LV_6630-3_0_5_node_62 | 0.4 | n |  | TRUE
104 | bus_LV_6630-3_0_5_node_59 | 0.4 | n |  | TRUE
105 | bus_LV_6630-3_0_5_node_158 | 0.4 | n |  | TRUE
106 | bus_LV_6630-3_0_5_node_143 | 0.4 | n |  | TRUE
107 | bus_LV_6630-3_0_5_node_57 | 0.4 | n |  | TRUE
108 | bus_LV_6630-3_0_5_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_6630-3_0_5_node_97 | 0.4 | n |  | TRUE
110 | bus_LV_6630-3_0_5_node_68 | 0.4 | n |  | TRUE
111 | bus_LV_6630-3_0_5_node_69 | 0.4 | n |  | TRUE
112 | bus_LV_6630-3_0_5_node_70 | 0.4 | n |  | TRUE
113 | bus_LV_6630-3_0_5_node_72 | 0.4 | n |  | TRUE
114 | bus_LV_6630-3_0_5_node_73 | 0.4 | n |  | TRUE
115 | bus_LV_6630-3_0_5_node_75 | 0.4 | n |  | TRUE
116 | bus_LV_6630-3_0_5_node_157 | 0.4 | n |  | TRUE
117 | bus_LV_6630-3_0_5_node_103 | 0.4 | n |  | TRUE
118 | bus_LV_6630-3_0_5_node_101 | 0.4 | n |  | TRUE
119 | bus_LV_6630-3_0_5_node_102 | 0.4 | n |  | TRUE
120 | bus_LV_6630-3_0_5_node_76 | 0.4 | n |  | TRUE
121 | bus_LV_6630-3_0_5_node_77 | 0.4 | n |  | TRUE
122 | bus_LV_6630-3_0_5_node_78 | 0.4 | n |  | TRUE
123 | bus_LV_6630-3_0_5_node_79 | 0.4 | n |  | TRUE
124 | bus_LV_6630-3_0_5_node_82 | 0.4 | n |  | TRUE
125 | bus_LV_6630-3_0_5_node_85 | 0.4 | n |  | TRUE
126 | bus_LV_6630-3_0_5_node_84 | 0.4 | n |  | TRUE
127 | bus_LV_6630-3_0_5_node_87 | 0.4 | n |  | TRUE
128 | bus_LV_6630-3_0_5_node_88 | 0.4 | n |  | TRUE
129 | bus_LV_6630-3_0_5_node_89 | 0.4 | n |  | TRUE
130 | bus_LV_6630-3_0_5_node_124 | 0.4 | n |  | TRUE
131 | bus_LV_6630-3_0_5_node_129 | 0.4 | n |  | TRUE
132 | bus_LV_6630-3_0_5_node_123 | 0.4 | n |  | TRUE
133 | bus_LV_6630-3_0_5_node_91 | 0.4 | n |  | TRUE
134 | bus_LV_6630-3_0_5_node_92 | 0.4 | n |  | TRUE
135 | bus_LV_6630-3_0_5_node_93 | 0.4 | n |  | TRUE
136 | bus_LV_6630-3_0_5_node_112 | 0.4 | n |  | TRUE
137 | bus_LV_6630-3_0_5_node_131 | 0.4 | n |  | TRUE
138 | bus_LV_6630-3_0_5_node_139 | 0.4 | n |  | TRUE
139 | bus_LV_6630-3_0_5_node_138 | 0.4 | n |  | TRUE
140 | bus_LV_6630-3_0_5_node_116 | 0.4 | n |  | TRUE
141 | bus_LV_6630-3_0_5_node_133 | 0.4 | n |  | TRUE
142 | bus_LV_6630-3_0_5_node_134 | 0.4 | n |  | TRUE
143 | bus_LV_6630-3_0_5_node_127 | 0.4 | n |  | TRUE
144 | bus_LV_6630-3_0_5_node_125 | 0.4 | n |  | TRUE
145 | bus_LV_6630-3_0_5_node_126 | 0.4 | n |  | TRUE
146 | bus_LV_6630-3_0_5_node_132 | 0.4 | n |  | TRUE
147 | bus_LV_6630-3_0_5_node_136 | 0.4 | n |  | TRUE
148 | bus_LV_6630-3_0_5_node_135 | 0.4 | n |  | TRUE
149 | bus_LV_6630-3_0_5_node_137 | 0.4 | n |  | TRUE
150 | bus_MV_463_0_node_155 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6630-3_0_5_load_0 | 0 | 0.00061513 | 0.00015417 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6630-3_0_5_load_1 | 1 | 0.00052689 | 0.00013205 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6630-3_0_5_load_2 | 2 | 0.00012512 | 3.1357e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6630-3_0_5_load_3 | 3 | 0.001322 | 0.00033134 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6630-3_0_5_load_4 | 4 | 0.00012514 | 3.1364e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6630-3_0_5_load_20 | 6 | 0.00012871 | 3.2259e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6630-3_0_5_load_18 | 8 | 0.0012695 | 0.00031817 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6630-3_0_5_load_5 | 9 | 0.0050549 | 0.0012669 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6630-3_0_5_load_6 | 10 | 0.0024074 | 0.00060335 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6630-3_0_5_load_152 | 16 | 0.002035 | 0.00051002 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6630-3_0_5_load_159 | 17 | 0.0012277 | 0.0003077 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6630-3_0_5_load_17 | 18 | 0.00088859 | 0.0002227 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6630-3_0_5_load_96 | 20 | 0.00041964 | 0.00010517 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6630-3_0_5_load_94 | 21 | 0.00078262 | 0.00019614 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6630-3_0_5_load_13 | 22 | 0.0014816 | 0.00037133 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6630-3_0_5_load_153 | 26 | 0.00093046 | 0.00023319 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6630-3_0_5_load_14 | 27 | 0.00085901 | 0.00021529 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6630-3_0_5_load_15 | 28 | 0.00026015 | 6.52e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6630-3_0_5_load_141 | 30 | 0.00053406 | 0.00013385 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6630-3_0_5_load_155 | 32 | 0.0037961 | 0.00095139 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6630-3_0_5_load_105 | 34 | 0.0019871 | 0.00049801 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6630-3_0_5_load_130 | 35 | 0.0010458 | 0.0002621 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6630-3_0_5_load_95 | 36 | 0.0061137 | 0.0015322 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6630-3_0_5_load_22 | 37 | 0.0018901 | 0.00047369 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6630-3_0_5_load_23 | 38 | 0.0003175 | 7.9574e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6630-3_0_5_load_151 | 44 | 0.003471 | 0.00086992 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6630-3_0_5_load_113 | 45 | 0.0014882 | 0.00037299 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6630-3_0_5_load_150 | 48 | 0.0015261 | 0.00038247 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6630-3_0_5_load_147 | 49 | 0.00038684 | 9.6952e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6630-3_0_5_load_118 | 50 | 0.00019142 | 4.7973e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6630-3_0_5_load_90 | 54 | 0.00023407 | 5.8664e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6630-3_0_5_load_61 | 57 | 0.0017081 | 0.00042808 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6630-3_0_5_load_148 | 60 | 0.0012834 | 0.00032164 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6630-3_0_5_load_144 | 62 | 0.00010897 | 2.7311e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6630-3_0_5_load_146 | 64 | 0.0001895 | 4.7493e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6630-3_0_5_load_122 | 65 | 0.0016984 | 0.00042565 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6630-3_0_5_load_110 | 70 | 0.0002797 | 7.0099e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6630-3_0_5_load_149 | 71 | 0.0034787 | 0.00087184 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6630-3_0_5_load_83 | 73 | 0.00037037 | 9.2823e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6630-3_0_5_load_86 | 74 | 0.00022907 | 5.741e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6630-3_0_5_load_111 | 76 | 0.0021923 | 0.00054945 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6630-3_0_5_load_74 | 77 | 0.00091581 | 0.00022952 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6630-3_0_5_load_67 | 80 | 0.001862 | 0.00046667 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6630-3_0_5_load_60 | 86 | 0.0012789 | 0.00032051 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6630-3_0_5_load_156 | 87 | 0.0018701 | 0.00046868 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6630-3_0_5_load_140 | 89 | 0.00037115 | 9.3019e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6630-3_0_5_load_142 | 92 | 0.0009345 | 0.00023421 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6630-3_0_5_load_120 | 93 | 0.00013913 | 3.487e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6630-3_0_5_load_154 | 94 | 0.0022787 | 0.00057109 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6630-3_0_5_load_145 | 96 | 0.00010811 | 2.7095e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6630-3_0_5_load_121 | 97 | 0.00058889 | 0.00014759 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6630-3_0_5_load_98 | 98 | 0.00051314 | 0.00012861 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6630-3_0_5_load_81 | 99 | 0.00022359 | 5.6037e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6630-3_0_5_load_115 | 100 | 0.001054 | 0.00026416 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6630-3_0_5_load_62 | 103 | 0.00086092 | 0.00021577 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6630-3_0_5_load_158 | 105 | 0.00021896 | 5.4878e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6630-3_0_5_load_143 | 106 | 0.00096411 | 0.00024163 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6630-3_0_5_load_57 | 107 | 0.00098721 | 0.00024742 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6630-3_0_5_load_68 | 110 | 0.0012112 | 0.00030355 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6630-3_0_5_load_72 | 113 | 0.0021694 | 0.0005437 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6630-3_0_5_load_157 | 116 | 0.00045126 | 0.0001131 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6630-3_0_5_load_103 | 117 | 0.0022655 | 0.0005678 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6630-3_0_5_load_101 | 118 | 0.00062611 | 0.00015692 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6630-3_0_5_load_102 | 119 | 0.0021843 | 0.00054744 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6630-3_0_5_load_76 | 120 | 0.00062279 | 0.00015608 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6630-3_0_5_load_77 | 121 | 0.00063773 | 0.00015983 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6630-3_0_5_load_85 | 125 | 0.00064583 | 0.00016186 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6630-3_0_5_load_84 | 126 | 0.0006404 | 0.0001605 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6630-3_0_5_load_87 | 127 | 0.008879 | 0.0022253 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6630-3_0_5_load_88 | 128 | 0.001387 | 0.00034761 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6630-3_0_5_load_129 | 131 | 0.00035426 | 8.8787e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6630-3_0_5_load_123 | 132 | 0.00029458 | 7.383e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6630-3_0_5_load_91 | 133 | 0.0012063 | 0.00030232 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6630-3_0_5_load_92 | 134 | 0.0064205 | 0.0016091 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6630-3_0_5_load_93 | 135 | 0.00041861 | 0.00010491 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6630-3_0_5_load_112 | 136 | 0.00041052 | 0.00010289 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6630-3_0_5_load_131 | 137 | 0.00010776 | 2.7007e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6630-3_0_5_load_139 | 138 | 0.00010969 | 2.7491e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6630-3_0_5_load_116 | 140 | 0.0070632 | 0.0017702 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6630-3_0_5_load_133 | 141 | 0.0021233 | 0.00053215 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6630-3_0_5_load_134 | 142 | 0.00015669 | 3.9271e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6630-3_0_5_load_127 | 143 | 0.00031939 | 8.0047e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6630-3_0_5_load_125 | 144 | 0.0003633 | 9.1051e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6630-3_0_5_load_126 | 145 | 0.0010484 | 0.00026276 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6630-3_0_5_load_132 | 146 | 0.00027736 | 6.9514e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6630-3_0_5_load_136 | 147 | 0.0005901 | 0.00014789 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6630-3_0_5_load_135 | 148 | 7.4458e-05 | 1.8661e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6630-3_0_5_load_137 | 149 | 0.00036365 | 9.1139e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6630-3_0_5_line_0 |  | 0 | 1 | 0.050944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6630-3_0_5_line_1 |  | 0 | 2 | 0.048759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6630-3_0_5_line_2 |  | 1 | 3 | 0.016577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6630-3_0_5_line_3 |  | 2 | 4 | 0.001162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6630-3_0_5_line_4 |  | 3 | 5 | 0.0032348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6630-3_0_5_line_5 |  | 4 | 6 | 0.0012052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6630-3_0_5_line_6 |  | 5 | 7 | 0.019583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6630-3_0_5_line_7 |  | 6 | 8 | 0.018658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6630-3_0_5_line_8 |  | 7 | 22 | 0.036116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6630-3_0_5_line_9 |  | 8 | 18 | 0.01185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6630-3_0_5_line_10 |  | 9 | 10 | 0.0045969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6630-3_0_5_line_11 |  | 9 | 11 | 0.019556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6630-3_0_5_line_12 |  | 10 | 12 | 0.047158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6630-3_0_5_line_13 |  | 11 | 13 | 0.030121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6630-3_0_5_line_14 |  | 11 | 14 | 0.030658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6630-3_0_5_line_15 |  | 12 | 15 | 0.027951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6630-3_0_5_line_16 |  | 13 | 16 | 0.031504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6630-3_0_5_line_17 |  | 14 | 17 | 0.003798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6630-3_0_5_line_18 |  | 15 | 18 | 0.036711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6630-3_0_5_line_19 |  | 19 | 20 | 0.0057242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6630-3_0_5_line_20 |  | 19 | 21 | 0.041046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6630-3_0_5_line_21 |  | 20 | 30 | 0.0030612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6630-3_0_5_line_22 |  | 21 | 36 | 0.00067508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6630-3_0_5_line_23 |  | 22 | 27 | 0.012496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6630-3_0_5_line_24 |  | 23 | 24 | 0.20306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_6630-3_0_5_line_25 |  | 23 | 25 | 0.028468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6630-3_0_5_line_26 |  | 23 | 26 | 0.0037598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_6630-3_0_5_line_27 |  | 24 | 32 | 0.003956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6630-3_0_5_line_28 |  | 24 | 33 | 0.24492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6630-3_0_5_line_29 |  | 25 | 34 | 0.0006808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6630-3_0_5_line_30 |  | 26 | 31 | 0.06865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_6630-3_0_5_line_31 |  | 27 | 28 | 0.016206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6630-3_0_5_line_32 |  | 28 | 29 | 0.044633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6630-3_0_5_line_33 |  | 29 | 30 | 0.028407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6630-3_0_5_line_34 |  | 29 | 31 | 0.008652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6630-3_0_5_line_35 |  | 31 | 108 | 0.058586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6630-3_0_5_line_36 |  | 31 | 109 | 0.058014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_6630-3_0_5_line_37 |  | 33 | 35 | 0.038396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6630-3_0_5_line_38 |  | 35 | 137 | 0.0037362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6630-3_0_5_line_39 |  | 37 | 38 | 0.06078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6630-3_0_5_line_40 |  | 38 | 39 | 0.018211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6630-3_0_5_line_41 |  | 39 | 40 | 0.053716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6630-3_0_5_line_42 |  | 40 | 41 | 0.11371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_6630-3_0_5_line_43 |  | 40 | 42 | 0.050576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6630-3_0_5_line_44 |  | 40 | 43 | 0.048158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6630-3_0_5_line_45 |  | 40 | 44 | 0.037337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_6630-3_0_5_line_46 |  | 41 | 45 | 0.025746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_6630-3_0_5_line_47 |  | 42 | 49 | 0.0065579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6630-3_0_5_line_48 |  | 43 | 60 | 0.019493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6630-3_0_5_line_49 |  | 44 | 48 | 0.0054943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_6630-3_0_5_line_50 |  | 45 | 67 | 0.0093934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_6630-3_0_5_line_51 |  | 46 | 47 | 0.059525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_6630-3_0_5_line_52 |  | 46 | 48 | 0.037925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_6630-3_0_5_line_53 |  | 47 | 50 | 0.10458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_6630-3_0_5_line_54 |  | 50 | 53 | 0.029495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_6630-3_0_5_line_55 |  | 51 | 52 | 0.014393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_6630-3_0_5_line_56 |  | 51 | 53 | 0.14675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_6630-3_0_5_line_57 |  | 51 | 54 | 0.0069327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6630-3_0_5_line_58 |  | 52 | 63 | 0.082338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_6630-3_0_5_line_59 |  | 52 | 64 | 0.023088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6630-3_0_5_line_60 |  | 53 | 93 | 0.033069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6630-3_0_5_line_61 |  | 55 | 56 | 0.035252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6630-3_0_5_line_62 |  | 55 | 57 | 0.011556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6630-3_0_5_line_63 |  | 56 | 71 | 0.048481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6630-3_0_5_line_64 |  | 56 | 58 | 0.065042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6630-3_0_5_line_65 |  | 57 | 83 | 0.077435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6630-3_0_5_line_66 |  | 58 | 59 | 0.050112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6630-3_0_5_line_67 |  | 58 | 60 | 0.080365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6630-3_0_5_line_68 |  | 59 | 61 | 0.029276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6630-3_0_5_line_69 |  | 59 | 62 | 0.0067242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6630-3_0_5_line_70 |  | 61 | 72 | 0.00677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6630-3_0_5_line_71 |  | 61 | 73 | 0.029826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6630-3_0_5_line_72 |  | 62 | 96 | 0.01203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6630-3_0_5_line_73 |  | 63 | 65 | 0.029332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_6630-3_0_5_line_74 |  | 65 | 97 | 0.051725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_6630-3_0_5_line_75 |  | 66 | 67 | 0.14505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_6630-3_0_5_line_76 |  | 66 | 68 | 0.2657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6630-3_0_5_line_77 |  | 66 | 69 | 0.006064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_6630-3_0_5_line_78 |  | 66 | 70 | 0.047536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6630-3_0_5_line_79 |  | 68 | 77 | 0.00943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6630-3_0_5_line_80 |  | 69 | 98 | 0.026753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_6630-3_0_5_line_81 |  | 70 | 75 | 0.028926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6630-3_0_5_line_82 |  | 71 | 88 | 0.0020807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6630-3_0_5_line_83 |  | 72 | 74 | 0.0073678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_6630-3_0_5_line_84 |  | 74 | 99 | 0.0023686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_6630-3_0_5_line_85 |  | 75 | 76 | 0.058761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6630-3_0_5_line_86 |  | 76 | 100 | 0.09753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6630-3_0_5_line_87 |  | 77 | 101 | 0.0057748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_6630-3_0_5_line_88 |  | 78 | 79 | 0.010717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_6630-3_0_5_line_89 |  | 78 | 80 | 0.0074592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_6630-3_0_5_line_90 |  | 79 | 102 | 0.006983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_6630-3_0_5_line_91 |  | 79 | 103 | 0.0096126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_6630-3_0_5_line_92 |  | 79 | 90 | 0.031007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_6630-3_0_5_line_93 |  | 81 | 82 | 0.034177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_6630-3_0_5_line_94 |  | 81 | 83 | 0.048548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_6630-3_0_5_line_95 |  | 82 | 89 | 0.01737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_6630-3_0_5_line_96 |  | 84 | 85 | 0.031048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_6630-3_0_5_line_97 |  | 84 | 86 | 0.015997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_6630-3_0_5_line_98 |  | 85 | 87 | 0.011013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_6630-3_0_5_line_99 |  | 85 | 88 | 0.072837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_6630-3_0_5_line_100 |  | 86 | 104 | 0.0053093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_6630-3_0_5_line_101 |  | 90 | 91 | 0.09591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_6630-3_0_5_line_102 |  | 90 | 92 | 0.013756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_6630-3_0_5_line_103 |  | 91 | 94 | 0.003326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_6630-3_0_5_line_104 |  | 91 | 95 | 0.029164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_6630-3_0_5_line_105 |  | 92 | 106 | 0.0076406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_6630-3_0_5_line_106 |  | 95 | 107 | 0.018753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_6630-3_0_5_line_107 |  | 97 | 132 | 0.044819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_6630-3_0_5_line_108 |  | 98 | 109 | 0.0030696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_6630-3_0_5_line_109 |  | 99 | 122 | 0.025978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_6630-3_0_5_line_110 |  | 100 | 140 | 0.063308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_6630-3_0_5_line_111 |  | 101 | 115 | 0.027302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_6630-3_0_5_line_112 |  | 101 | 111 | 0.010978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_6630-3_0_5_line_113 |  | 102 | 105 | 0.006653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_6630-3_0_5_line_114 |  | 104 | 107 | 0.023414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_6630-3_0_5_line_115 |  | 108 | 136 | 0.056473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_6630-3_0_5_line_116 |  | 109 | 135 | 0.017781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_6630-3_0_5_line_117 |  | 110 | 111 | 0.0064744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_6630-3_0_5_line_118 |  | 110 | 112 | 0.027383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_6630-3_0_5_line_119 |  | 112 | 113 | 0.043477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_6630-3_0_5_line_120 |  | 112 | 114 | 0.022533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_6630-3_0_5_line_121 |  | 114 | 116 | 0.031453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_6630-3_0_5_line_122 |  | 115 | 117 | 0.004365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_6630-3_0_5_line_123 |  | 115 | 118 | 0.02664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_6630-3_0_5_line_124 |  | 118 | 119 | 0.010163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_6630-3_0_5_line_125 |  | 120 | 121 | 0.0059358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_6630-3_0_5_line_126 |  | 120 | 122 | 0.022319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_6630-3_0_5_line_127 |  | 121 | 123 | 0.022878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_6630-3_0_5_line_128 |  | 123 | 124 | 0.018091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_6630-3_0_5_line_129 |  | 124 | 125 | 0.040743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_6630-3_0_5_line_130 |  | 124 | 126 | 0.023313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_6630-3_0_5_line_131 |  | 127 | 128 | 0.030626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_6630-3_0_5_line_132 |  | 128 | 129 | 0.36121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_6630-3_0_5_line_133 |  | 129 | 130 | 0.22749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_6630-3_0_5_line_134 |  | 130 | 131 | 0.020909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_6630-3_0_5_line_135 |  | 130 | 132 | 0.12884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_6630-3_0_5_line_136 |  | 131 | 143 | 0.013416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_6630-3_0_5_line_137 |  | 133 | 134 | 0.0013446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_6630-3_0_5_line_138 |  | 134 | 135 | 0.041708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_6630-3_0_5_line_139 |  | 137 | 146 | 0.0086321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_6630-3_0_5_line_140 |  | 138 | 139 | 0.024708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_6630-3_0_5_line_141 |  | 139 | 147 | 0.01987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_6630-3_0_5_line_142 |  | 139 | 146 | 0.013667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_6630-3_0_5_line_143 |  | 141 | 142 | 0.0045037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_6630-3_0_5_line_144 |  | 142 | 148 | 0.00020931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_6630-3_0_5_line_145 |  | 143 | 144 | 0.010933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_6630-3_0_5_line_146 |  | 144 | 145 | 0.0081687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_6630-3_0_5_line_147 |  | 147 | 149 | 0.016891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_6630-3_0_5_line_148 |  | 148 | 149 | 0.009867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6630-3_0_5_trafo_107 | 0.63 MVA 20/0.4 kV | 150 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2493346.5297 | 1121430.8125 | 2493342.2095 | 1121407.5726 | 2493342.724 | 1121396.0672 | 2493339.7246 | 1121380.566
1 | 2493346.5297 | 1121430.8125 | 2493347.9551 | 1121438.48 | 2493344.8322 | 1121452.5664 | 2493335.1957 | 1121463.0431 | 2493324.3503 | 1121468.8387
2 | 2493333.2171 | 1121365.8155 | 2493338.0801 | 1121372.0671 | 2493339.7246 | 1121380.566
3 | 2493324.3503 | 1121468.8387 | 2493323.3255 | 1121469.3863
4 | 2493332.0146 | 1121362.8126 | 2493333.2171 | 1121365.8155
5 | 2493322.2626 | 1121469.9544 | 2493323.3255 | 1121469.3863
6 | 2493327.2975 | 1121343.8502 | 2493330.7319 | 1121359.6443 | 2493332.0146 | 1121362.8126
7 | 2493322.2626 | 1121469.9544 | 2493313.0767 | 1121474.8631 | 2493305.7433 | 1121478.6258
8 | 2493327.2975 | 1121343.8502 | 2493292.0144 | 1121351.5595
9 | 2493295.2004 | 1121484.0352 | 2493305.7433 | 1121478.6258
10 | 2493195.8938 | 1121480.817 | 2493199.6275 | 1121483.4986
11 | 2493180.0097 | 1121469.4089 | 2493195.8938 | 1121480.817
12 | 2493236.9636 | 1121512.2417 | 2493222.7072 | 1121500.0745 | 2493199.6275 | 1121483.4986
13 | 2493162.1777 | 1121493.7174 | 2493168.3937 | 1121485.291 | 2493172.4864 | 1121479.8263 | 2493178.0671 | 1121472.1228 | 2493180.0097 | 1121469.4089
14 | 2493155.392 | 1121451.1655 | 2493175.9969 | 1121465.4328 | 2493180.0097 | 1121469.4089
15 | 2493236.9636 | 1121512.2417 | 2493262.5376 | 1121500.794
16 | 2493162.1777 | 1121493.7174 | 2493149.7871 | 1121484.5527 | 2493149.5644 | 1121486.3578 | 2493150.3207 | 1121492.9153 | 2493151.3811 | 1121500.5144
17 | 2493155.392 | 1121451.1655 | 2493153.2331 | 1121454.2945
18 | 2493262.5376 | 1121500.794 | 2493295.2004 | 1121484.0352
19 | 2493204.2393 | 1121397.1678 | 2493207.4853 | 1121392.453
20 | 2493204.2393 | 1121397.1678 | 2493217.0061 | 1121407.1043 | 2493220.9198 | 1121409.4033 | 2493223.7863 | 1121410.0753 | 2493225.1187 | 1121409.507 | 2493227.321 | 1121407.956 | 2493235.7292 | 1121397.7257
21 | 2493209.2213 | 1121389.9316 | 2493207.4853 | 1121392.453
22 | 2493236.1579 | 1121397.2042 | 2493235.7292 | 1121397.7257
23 | 2493292.0144 | 1121351.5595 | 2493279.8069 | 1121354.2268
24 | 2493277.063 | 1121314.5734 | 2493276.1713 | 1121313.0103 | 2493271.945 | 1121303.501 | 2493339.8358 | 1121274.3955 | 2493346.3937 | 1121290.1233 | 2493350.6231 | 1121300.2552 | 2493355.65 | 1121312.2965 | 2493358.7363 | 1121314.0543 | 2493361.657 | 1121314.7366 | 2493363.91 | 1121314.7413 | 2493366.4263 | 1121313.4961 | 2493377.5718 | 1121308.9411 | 2493407.8926 | 1121295.787 | 2493414.0225 | 1121292.5102 | 2493416.4731 | 1121291.0327 | 2493418.4974 | 1121289.0068 | 2493419.7879 | 1121286.9383 | 2493420.8678 | 1121282.9834
25 | 2493277.063 | 1121314.5734 | 2493276.1713 | 1121313.0103 | 2493271.945 | 1121303.501 | 2493265.5243 | 1121288.5603
26 | 2493277.063 | 1121314.5734 | 2493273.9802 | 1121316.7258
27 | 2493420.5437 | 1121279.0421 | 2493420.8678 | 1121282.9834
28 | 2493420.8678 | 1121282.9834 | 2493419.7879 | 1121286.9383 | 2493418.4974 | 1121289.0068 | 2493416.4731 | 1121291.0327 | 2493414.0225 | 1121292.5102 | 2493407.8926 | 1121295.787 | 2493377.5718 | 1121308.9411 | 2493366.4263 | 1121313.4961 | 2493363.91 | 1121314.7413 | 2493361.4821 | 1121316.6298 | 2493360.1269 | 1121318.5327 | 2493358.9401 | 1121321.2331 | 2493358.5321 | 1121323.9087 | 2493358.6117 | 1121326.231 | 2493359.4317 | 1121329.8522 | 2493362.6946 | 1121338.5558 | 2493415.3246 | 1121461.2512 | 2493423.0621 | 1121477.3919
29 | 2493265.5243 | 1121288.5603 | 2493265.2553 | 1121287.9349
30 | 2493217.6929 | 1121356.026 | 2493273.9802 | 1121316.7258
31 | 2493263.9741 | 1121357.6862 | 2493279.8069 | 1121354.2268
32 | 2493219.9462 | 1121364.3471 | 2493239.3098 | 1121362.9376 | 2493245.7528 | 1121361.6675 | 2493263.9741 | 1121357.6862
33 | 2493219.9462 | 1121364.3471 | 2493219.5982 | 1121369.9791 | 2493218.6913 | 1121374.5425 | 2493215.8008 | 1121380.375 | 2493209.2213 | 1121389.9316
34 | 2493217.6929 | 1121356.026 | 2493219.1521 | 1121360.0139 | 2493219.9462 | 1121364.3471
35 | 2493234.3987 | 1121320.3413 | 2493238.8732 | 1121328.1785 | 2493207.9719 | 1121346.4359 | 2493212.5497 | 1121350.5132 | 2493217.6929 | 1121356.026
36 | 2493171.4512 | 1121321.3315 | 2493196.7797 | 1121337.8614 | 2493207.9719 | 1121346.4359 | 2493212.5497 | 1121350.5132 | 2493217.6929 | 1121356.026
37 | 2493423.0621 | 1121477.3919 | 2493428.988 | 1121488.8059 | 2493442.3882 | 1121504.9356 | 2493445.3316 | 1121508.4255
38 | 2493445.3316 | 1121508.4255 | 2493447.581 | 1121511.0925 | 2493447.7418 | 1121511.2805
39 | 2493319.6072 | 1121249.0506 | 2493317.4084 | 1121248.6857 | 2493313.0759 | 1121247.139 | 2493309.1003 | 1121244.8298 | 2493305.5988 | 1121241.8453 | 2493302.6968 | 1121238.2942 | 2493300.4807 | 1121234.264 | 2493299.0382 | 1121229.9089 | 2493298.4474 | 1121226.1614 | 2493298.4265 | 1121222.3593 | 2493298.9772 | 1121218.5916 | 2493300.0858 | 1121214.9586 | 2493301.7304 | 1121211.5274 | 2493303.8659 | 1121208.3765 | 2493306.6836 | 1121205.4027 | 2493308.5919 | 1121203.8013 | 2493309.9073 | 1121202.9293
40 | 2493327.3021 | 1121199.0015 | 2493322.5687 | 1121198.7848 | 2493317.8818 | 1121199.4568 | 2493313.4029 | 1121200.9813 | 2493310.9179 | 1121202.2593 | 2493309.9073 | 1121202.9293
41 | 2493327.3021 | 1121199.0015 | 2493328.0073 | 1121194.3638 | 2493330.1598 | 1121177.3149 | 2493329.2317 | 1121171.5053 | 2493353.2783 | 1121161.7304
42 | 2493255.8639 | 1121212.0816 | 2493259.135 | 1121202.8958 | 2493260.4989 | 1121199.3027 | 2493288.9221 | 1121188.7721 | 2493329.2317 | 1121171.5053 | 2493353.2783 | 1121161.7304
43 | 2493353.2783 | 1121161.7304 | 2493351.6056 | 1121158.3244 | 2493350.416 | 1121155.6214 | 2493349.4113 | 1121153.3377 | 2493348.6157 | 1121151.5395 | 2493347.4182 | 1121148.8255 | 2493380.9389 | 1121134.6364
44 | 2493353.2783 | 1121161.7304 | 2493351.6056 | 1121158.3244 | 2493350.416 | 1121155.6214 | 2493349.4113 | 1121153.3377 | 2493348.6157 | 1121151.5395 | 2493347.4182 | 1121148.8255 | 2493346.6303 | 1121147.0271 | 2493345.6246 | 1121144.6878 | 2493344.5805 | 1121142.3603 | 2493343.8271 | 1121140.3278 | 2493343.2146 | 1121138.8488 | 2493364.5596 | 1121129.8777
45 | 2493353.2783 | 1121161.7304 | 2493365.5402 | 1121156.1551 | 2493387.3376 | 1121146.4342
46 | 2493255.8639 | 1121212.0816 | 2493235.8732 | 1121218.2052 | 2493231.3073 | 1121219.8047
47 | 2493380.9389 | 1121134.6364 | 2493384.0599 | 1121133.5473 | 2493387.1323 | 1121132.4807
48 | 2493364.5596 | 1121129.8777 | 2493379.6309 | 1121123.4745 | 2493382.5002 | 1121122.2544
49 | 2493392.3547 | 1121144.1945 | 2493389.3176 | 1121145.5512 | 2493387.3376 | 1121146.4342
50 | 2493222.1669 | 1121221.4937 | 2493224.6753 | 1121221.5384 | 2493226.4309 | 1121221.3406 | 2493228.0519 | 1121220.945 | 2493231.3073 | 1121219.8047
51 | 2493426.9895 | 1121128.743 | 2493441.2831 | 1121124.1771 | 2493450.3377 | 1121121.349 | 2493456.7831 | 1121120.2014 | 2493463.71 | 1121119.6679 | 2493470.7697 | 1121119.6658 | 2493475.2677 | 1121119.6532 | 2493475.9137 | 1121123.0329 | 2493477.1918 | 1121129.4478
52 | 2493426.9895 | 1121128.743 | 2493395.1739 | 1121142.9352 | 2493392.3547 | 1121144.1945
53 | 2493477.1918 | 1121129.4478 | 2493480.169 | 1121132.4528 | 2493484.2263 | 1121135.0163 | 2493487.5949 | 1121136.5914 | 2493491.3675 | 1121138.326 | 2493495.5836 | 1121139.8305 | 2493500.6522 | 1121141.5535 | 2493505.8797 | 1121142.6621 | 2493510.2858 | 1121143.1293 | 2493515.2239 | 1121142.6976 | 2493518.6025 | 1121142.2155 | 2493523.7667 | 1121140.6014 | 2493573.708 | 1121119.2968
54 | 2493600.8372 | 1121107.7237 | 2493573.708 | 1121119.2968
55 | 2493653.1067 | 1121007.1062 | 2493639.7463 | 1121012.5558
56 | 2493600.8372 | 1121107.7237 | 2493597.9029 | 1121101.0154 | 2493596.908 | 1121096.2187 | 2493580.5623 | 1121058.749 | 2493640.7522 | 1121035.0748 | 2493644.1145 | 1121033.6592 | 2493642.9309 | 1121030.856 | 2493642.1422 | 1121029.002 | 2493641.5466 | 1121027.6005 | 2493640.7738 | 1121025.7796 | 2493639.6063 | 1121023.0094 | 2493638.8175 | 1121021.1555 | 2493638.447 | 1121020.2725 | 2493642.3143 | 1121018.6146 | 2493641.9145 | 1121017.8211 | 2493640.973 | 1121015.614 | 2493639.7463 | 1121012.5558
57 | 2493639.7463 | 1121012.5558 | 2493633.5037 | 1121015.5712
58 | 2493653.1067 | 1121007.1062 | 2493690.2262 | 1120992.1439 | 2493691.2404 | 1120994.9724 | 2493691.9676 | 1120996.8386 | 2493692.3223 | 1120997.6996 | 2493688.0412 | 1120999.5204 | 2493688.4433 | 1121000.4473 | 2493689.2394 | 1121002.2789 | 2493690.4371 | 1121005.0152 | 2493691.233 | 1121006.8357 | 2493691.8362 | 1121008.226 | 2493692.6239 | 1121010.0244 | 2493698.9888 | 1121007.3552 | 2493708.9719 | 1121002.9102 | 2493710.0289 | 1121005.1042
59 | 2493653.1067 | 1121007.1062 | 2493651.2968 | 1121004.2251 | 2493648.3215 | 1121001.7647 | 2493634.3236 | 1120994.3825
60 | 2493600.8372 | 1121107.7237 | 2493611.4119 | 1121129.4404 | 2493614.8972 | 1121137.6451
61 | 2493412.8383 | 1121024.581 | 2493400.3128 | 1121020.0434 | 2493406.5278 | 1121036.0107 | 2493403.469 | 1121032.3178
62 | 2493412.8383 | 1121024.581 | 2493405.3586 | 1121015.7721
63 | 2493403.469 | 1121032.3178 | 2493399.7191 | 1121034.0628 | 2493394.3251 | 1121035.3365 | 2493355.5565 | 1121036.9703
64 | 2493403.469 | 1121032.3178 | 2493406.5278 | 1121036.0107 | 2493419.3995 | 1121049.6815 | 2493420.1391 | 1121050.4912 | 2493421.2957 | 1121051.7606 | 2493431.2511 | 1121062.8255 | 2493433.9013 | 1121065.6584 | 2493442.3089 | 1121074.2714 | 2493447.8694 | 1121079.8214
65 | 2493364.2647 | 1120950.9456 | 2493383.1914 | 1120990.2927 | 2493404.8486 | 1121015.1714 | 2493405.3586 | 1121015.7721
66 | 2493447.8694 | 1121079.8214 | 2493449.769 | 1121068.9698 | 2493446.9411 | 1121066.1178 | 2493451.3461 | 1121059.0801 | 2493455.3216 | 1121053.0618 | 2493460.5976 | 1121047.721 | 2493464.1223 | 1121044.1454 | 2493459.9638 | 1121038.4706
67 | 2493447.8694 | 1121079.8214 | 2493441.7742 | 1121089.8908 | 2493438.4973 | 1121094.3959 | 2493434.413 | 1121098.615 | 2493430.192 | 1121101.6469 | 2493421.609 | 1121105.4006 | 2493407.0779 | 1121111.8164 | 2493385.5506 | 1121120.9574 | 2493382.5002 | 1121122.2544
68 | 2493459.9638 | 1121038.4706 | 2493464.1223 | 1121044.1454 | 2493469.5649 | 1121038.6238 | 2493472.6274 | 1121035.5234 | 2493479.6433 | 1121028.2173
69 | 2493459.9638 | 1121038.4706 | 2493455.9872 | 1121033.0483
70 | 2493474.5946 | 1121023.6923 | 2493479.6433 | 1121028.2173
71 | 2493479.6433 | 1121028.2173 | 2493485.038 | 1121022.6076 | 2493500.2957 | 1121038.5165
72 | 2493445.8393 | 1121039.509 | 2493455.9872 | 1121033.0483
73 | 2493710.0289 | 1121005.1042 | 2493711.6504 | 1121007.7996 | 2493718.0961 | 1121014.5573 | 2493720.8199 | 1121017.2 | 2493725.7093 | 1121021.4502 | 2493730.9597 | 1121025.4064
74 | 2493772.6095 | 1121056.0691 | 2493772.041 | 1121055.6247 | 2493755.4381 | 1121043.8422 | 2493752.4043 | 1121041.5607 | 2493741.9734 | 1121033.7056 | 2493730.9597 | 1121025.4064
75 | 2493141.9138 | 1121301.0848 | 2493141.2894 | 1121292.3903 | 2493129.7575 | 1121266.3662 | 2493135.1508 | 1121264.1917 | 2493136.346 | 1121261.5356 | 2493137.8209 | 1121259.864 | 2493151.8427 | 1121255.2243 | 2493162.1106 | 1121250.3509 | 2493171.5025 | 1121245.2372 | 2493184.8078 | 1121237.1636 | 2493201.7578 | 1121224.8897 | 2493214.9741 | 1121217.4515 | 2493217.1964 | 1121219.647 | 2493222.1669 | 1121221.4937
76 | 2493141.9138 | 1121301.0848 | 2493141.2894 | 1121292.3903 | 2493129.7575 | 1121266.3662 | 2493127.6765 | 1121261.6889 | 2493125.6651 | 1121257.0214 | 2493119.6128 | 1121243.7421 | 2493116.3985 | 1121236.4942 | 2493110.9994 | 1121224.3819 | 2493108.7337 | 1121219.2964 | 2493105.5286 | 1121212.1374 | 2493102.9877 | 1121205.8894 | 2493093.3499 | 1121190.9946 | 2493079.507 | 1121158.2183 | 2493088.7823 | 1121153.9293 | 2493094.4951 | 1121151.4934 | 2493125.6088 | 1121137.3565 | 2493141.3905 | 1121127.071 | 2493157.3298 | 1121122.6421 | 2493169.9737 | 1121116.8594 | 2493178.1563 | 1121112.7233
77 | 2493146.3918 | 1121305.1861 | 2493141.9138 | 1121301.0848
78 | 2493141.9138 | 1121301.0848 | 2493133.2414 | 1121306.7417 | 2493098.3237 | 1121319.519
79 | 2493178.1563 | 1121112.7233 | 2493186.5701 | 1121108.4648
80 | 2493146.3918 | 1121305.1861 | 2493151.1541 | 1121307.9148 | 2493157.1454 | 1121311.6447 | 2493168.9095 | 1121319.6104
81 | 2493070.1934 | 1121325.1682 | 2493087.1703 | 1121323.6003 | 2493098.3237 | 1121319.519
82 | 2493353.4777 | 1121037.0579 | 2493355.5565 | 1121036.9703
83 | 2493474.5946 | 1121023.6923 | 2493480.3466 | 1121019.088 | 2493480.3466 | 1121019.088
84 | 2493482.4667 | 1121018.032 | 2493480.3466 | 1121019.088
85 | 2493070.1934 | 1121325.1682 | 2493092.4948 | 1121379.5331
86 | 2493078.3244 | 1121457.4132 | 2493094.9542 | 1121450.0219 | 2493096.8874 | 1121448.9648 | 2493106.1385 | 1121434.1695 | 2493110.628 | 1121426.7075 | 2493111.2115 | 1121425.2407 | 2493109.8635 | 1121421.8735 | 2493092.4948 | 1121379.5331
87 | 2493191.7225 | 1121105.857 | 2493186.5701 | 1121108.4648
88 | 2493224.2539 | 1120971.0513 | 2493224.316 | 1120977.1875 | 2493228.8941 | 1120977.3401
89 | 2493228.8941 | 1120977.3401 | 2493229.0413 | 1120984.7979
90 | 2493224.2539 | 1120971.0513 | 2493224.1768 | 1120964.0704
91 | 2493224.2539 | 1120971.0513 | 2493218.9623 | 1120972.4457 | 2493214.8259 | 1120972.6294
92 | 2493224.2539 | 1120971.0513 | 2493231.4271 | 1120969.1679 | 2493254.9969 | 1120968.1845
93 | 2493373.4327 | 1120919.1079 | 2493369.2369 | 1120915.2683 | 2493392.2977 | 1120898.5399
94 | 2493364.2647 | 1120950.9456 | 2493361.0188 | 1120952.3927 | 2493353.6755 | 1120932.8429 | 2493360.0699 | 1120929.2278 | 2493369.9333 | 1120921.9381 | 2493373.4327 | 1120919.1079
95 | 2493392.2977 | 1120898.5399 | 2493401.6242 | 1120913.1938
96 | 2493296.2844 | 1121064.7735 | 2493295.6894 | 1121066.9076 | 2493294.9564 | 1121070.4006 | 2493294.3414 | 1121078.3943 | 2493301.8219 | 1121087.8017 | 2493303.6904 | 1121092.683
97 | 2493303.6904 | 1121092.683 | 2493295.9261 | 1121106.6692
98 | 2493296.2844 | 1121064.7735 | 2493301.8664 | 1121066.7207 | 2493306.9975 | 1121066.7302
99 | 2493296.2844 | 1121064.7735 | 2493297.4042 | 1121060.8957 | 2493298.0288 | 1121060.44 | 2493298.5277 | 1121059.853 | 2493298.8703 | 1121059.1576 | 2493300.4323 | 1121058.0404 | 2493312.6064 | 1121045.2952 | 2493314.3085 | 1121045.1206 | 2493321.9491 | 1121044.3631 | 2493321.6863 | 1121038.653 | 2493353.4777 | 1121037.0579
100 | 2493293.3486 | 1121111.3108 | 2493295.1134 | 1121108.1332 | 2493295.9261 | 1121106.6692
101 | 2493254.9969 | 1120968.1845 | 2493270.6939 | 1120967.4848 | 2493271.151 | 1120975.0149 | 2493271.3331 | 1120978.336 | 2493272.4608 | 1120996.3166 | 2493273.0843 | 1121007.157 | 2493274.5417 | 1121032.4475 | 2493275.87 | 1121034.2586 | 2493278.0272 | 1121036.6999 | 2493273.6983 | 1121040.6121 | 2493273.4409 | 1121044.3858
102 | 2493254.9969 | 1120968.1845 | 2493254.5838 | 1120959.2083 | 2493251.4549 | 1120959.4192 | 2493251.4183 | 1120957.7854
103 | 2493270.1113 | 1121044.5891 | 2493273.4409 | 1121044.3858
104 | 2493273.4409 | 1121044.3858 | 2493273.9087 | 1121055.5847 | 2493274.6498 | 1121073.5165
105 | 2493256.0616 | 1120954.6348 | 2493256.2119 | 1120957.4673 | 2493251.4183 | 1120957.7854
106 | 2493274.6498 | 1121073.5165 | 2493282.9657 | 1121090.3248
107 | 2493772.6095 | 1121056.0691 | 2493789.9873 | 1121069.6518 | 2493805.2501 | 1121081.5803 | 2493807.8703 | 1121083.733
108 | 2493171.4512 | 1121321.3315 | 2493168.9095 | 1121319.6104
109 | 2493506.2223 | 1121007.547 | 2493489.3489 | 1121014.6043 | 2493482.4667 | 1121018.032
110 | 2493078.3244 | 1121457.4132 | 2493020.4735 | 1121483.1257
111 | 2493185.8476 | 1121079.4771 | 2493185.966 | 1121084.4338 | 2493186.2785 | 1121089.8873 | 2493188.0356 | 1121095.8824 | 2493191.7225 | 1121105.857
112 | 2493201.5416 | 1121100.8915 | 2493191.7225 | 1121105.857
113 | 2493220.3376 | 1120959.8911 | 2493219.8247 | 1120960.5561 | 2493219.9623 | 1120961.3542 | 2493224.1768 | 1120964.0704
114 | 2493293.3486 | 1121111.3108 | 2493282.9657 | 1121090.3248
115 | 2493234.3987 | 1121320.3413 | 2493238.4006 | 1121314.9672 | 2493239.5652 | 1121307.5197 | 2493237.9707 | 1121300.2431 | 2493231.0388 | 1121283.8883 | 2493224.3039 | 1121268.2554
116 | 2493171.4512 | 1121321.3315 | 2493161.1316 | 1121335.8115
117 | 2493201.5416 | 1121100.8915 | 2493207.9848 | 1121100.2569
118 | 2493235.3063 | 1121098.7717 | 2493220.1116 | 1121099.0624 | 2493207.9848 | 1121100.2569
119 | 2493214.1373 | 1121129.0538 | 2493212.4087 | 1121123.7921 | 2493213.3592 | 1121119.9506 | 2493216.1114 | 1121115.4547 | 2493233.0003 | 1121109.3081 | 2493235.3063 | 1121098.7717
120 | 2493244.5102 | 1121078.196 | 2493235.3063 | 1121098.7717
121 | 2493244.5102 | 1121078.196 | 2493246.2939 | 1121052.0699 | 2493246.2859 | 1121046.8111
122 | 2493185.8476 | 1121079.4771 | 2493181.4775 | 1121079.7434
123 | 2493185.8476 | 1121079.4771 | 2493185.8118 | 1121078.7662 | 2493185.8218 | 1121076.2755 | 2493186.0948 | 1121074.2583 | 2493192.0917 | 1121063.0118 | 2493194.0059 | 1121060.4319 | 2493198.2773 | 1121057.0571
124 | 2493204.1728 | 1121048.9449 | 2493200.3826 | 1121055.3938 | 2493198.2773 | 1121057.0571
125 | 2493521.0493 | 1121024.2276 | 2493524.964 | 1121028.6895
126 | 2493506.2223 | 1121007.547 | 2493510.7537 | 1121012.4926 | 2493521.0493 | 1121024.2276
127 | 2493540.0522 | 1121045.8871 | 2493524.964 | 1121028.6895
128 | 2493540.0522 | 1121045.8871 | 2493557.0058 | 1121039.4401
129 | 2493557.0058 | 1121039.4401 | 2493573.439 | 1121031.9238 | 2493558.1816 | 1121015.1527
130 | 2493557.0058 | 1121039.4401 | 2493541.4476 | 1121022.0779
131 | 2494253.4014 | 1121674.3396 | 2494237.4689 | 1121648.3349 | 2494237.4017 | 1121648.2251
132 | 2494026.4535 | 1121359.878 | 2494079.2762 | 1121412.4862 | 2494086.0526 | 1121419.2274 | 2494138.8148 | 1121470.2028 | 2494143.389 | 1121475.8819 | 2494149.7121 | 1121485.822 | 2494155.1527 | 1121496.478 | 2494194.2437 | 1121572.1868 | 2494212.6267 | 1121607.7768 | 2494227.5414 | 1121632.1204 | 2494237.4017 | 1121648.2251
133 | 2493873.6355 | 1121191.5169 | 2493882.4097 | 1121202.1586 | 2493908.252 | 1121230.4678 | 2493974.4593 | 1121295.615 | 2493988.6884 | 1121311.5646 | 2493997.96 | 1121322.876 | 2494018.5742 | 1121350.966 | 2494026.4535 | 1121359.878
134 | 2493873.6355 | 1121191.5169 | 2493864.9002 | 1121203.3 | 2493860.0916 | 1121207.279
135 | 2493873.6355 | 1121191.5169 | 2493869.6374 | 1121182.648 | 2493866.244 | 1121173.5017 | 2493858.3731 | 1121152.3597 | 2493855.7477 | 1121145.6459 | 2493852.3677 | 1121138.1449 | 2493846.154 | 1121125.2568 | 2493842.2207 | 1121118.3214 | 2493838.7185 | 1121113.0906 | 2493833.5487 | 1121106.0435 | 2493829.6112 | 1121101.9434 | 2493824.8137 | 1121097.6471 | 2493818.778 | 1121092.6943 | 2493807.8703 | 1121083.733
136 | 2493860.0916 | 1121207.279 | 2493850.39 | 1121215.3068 | 2493849.7151 | 1121215.7797
137 | 2493136.1451 | 1121370.8715 | 2493136.9255 | 1121369.7765
138 | 2493161.1316 | 1121335.8115 | 2493136.9255 | 1121369.7765
139 | 2493447.7418 | 1121511.2805 | 2493453.3519 | 1121517.841
140 | 2493462.2408 | 1121528.223 | 2493444.6458 | 1121545.5699
141 | 2493462.2408 | 1121528.223 | 2493471.9113 | 1121545.581
142 | 2493462.2408 | 1121528.223 | 2493456.9078 | 1121521.9907 | 2493455.7579 | 1121520.6546 | 2493453.3519 | 1121517.841
143 | 2493493.2139 | 1121568.6731 | 2493490.5946 | 1121565.9144 | 2493490.1129 | 1121565.4071
144 | 2493489.9688 | 1121565.2553 | 2493490.1129 | 1121565.4071
145 | 2493840.7652 | 1121222.0592 | 2493845.9465 | 1121218.4202 | 2493849.7151 | 1121215.7797
146 | 2493840.7652 | 1121222.0592 | 2493835.7338 | 1121225.593 | 2493834.0795 | 1121226.7527
147 | 2493471.9113 | 1121545.581 | 2493472.7973 | 1121547.1714 | 2493483.1747 | 1121558.1002
148 | 2493489.9688 | 1121565.2553 | 2493483.1747 | 1121558.1002

## bus_geodata
| x | y | coords
0 | 2493346.5297 | 1121430.8125
1 | 2493339.7246 | 1121380.566
2 | 2493324.3503 | 1121468.8387
3 | 2493333.2171 | 1121365.8155
4 | 2493323.3255 | 1121469.3863
5 | 2493332.0146 | 1121362.8126
6 | 2493322.2626 | 1121469.9544
7 | 2493327.2975 | 1121343.8502
8 | 2493305.7433 | 1121478.6258
9 | 2493195.8938 | 1121480.817
10 | 2493199.6275 | 1121483.4986
11 | 2493180.0097 | 1121469.4089
12 | 2493236.9636 | 1121512.2417
13 | 2493162.1777 | 1121493.7174
14 | 2493155.392 | 1121451.1655
15 | 2493262.5376 | 1121500.794
16 | 2493151.3811 | 1121500.5144
17 | 2493153.2331 | 1121454.2945
18 | 2493295.2004 | 1121484.0352
19 | 2493204.2393 | 1121397.1678
20 | 2493207.4853 | 1121392.453
21 | 2493235.7292 | 1121397.7257
22 | 2493292.0144 | 1121351.5595
23 | 2493277.063 | 1121314.5734
24 | 2493420.8678 | 1121282.9834
25 | 2493265.5243 | 1121288.5603
26 | 2493273.9802 | 1121316.7258
27 | 2493279.8069 | 1121354.2268
28 | 2493263.9741 | 1121357.6862
29 | 2493219.9462 | 1121364.3471
30 | 2493209.2213 | 1121389.9316
31 | 2493217.6929 | 1121356.026
32 | 2493420.5437 | 1121279.0421
33 | 2493423.0621 | 1121477.3919
34 | 2493265.2553 | 1121287.9349
35 | 2493445.3316 | 1121508.4255
36 | 2493236.1579 | 1121397.2042
37 | 2493319.6072 | 1121249.0506
38 | 2493309.9073 | 1121202.9293
39 | 2493327.3021 | 1121199.0015
40 | 2493353.2783 | 1121161.7304
41 | 2493255.8639 | 1121212.0816
42 | 2493380.9389 | 1121134.6364
43 | 2493364.5596 | 1121129.8777
44 | 2493387.3376 | 1121146.4342
45 | 2493231.3073 | 1121219.8047
46 | 2493426.9895 | 1121128.743
47 | 2493477.1918 | 1121129.4478
48 | 2493392.3547 | 1121144.1945
49 | 2493387.1323 | 1121132.4807
50 | 2493573.708 | 1121119.2968
51 | 2493639.7463 | 1121012.5558
52 | 2493653.1067 | 1121007.1062
53 | 2493600.8372 | 1121107.7237
54 | 2493633.5037 | 1121015.5712
55 | 2493412.8383 | 1121024.581
56 | 2493403.469 | 1121032.3178
57 | 2493405.3586 | 1121015.7721
58 | 2493447.8694 | 1121079.8214
59 | 2493459.9638 | 1121038.4706
60 | 2493382.5002 | 1121122.2544
61 | 2493479.6433 | 1121028.2173
62 | 2493455.9872 | 1121033.0483
63 | 2493710.0289 | 1121005.1042
64 | 2493634.3236 | 1120994.3825
65 | 2493730.9597 | 1121025.4064
66 | 2493141.9138 | 1121301.0848
67 | 2493222.1669 | 1121221.4937
68 | 2493178.1563 | 1121112.7233
69 | 2493146.3918 | 1121305.1861
70 | 2493098.3237 | 1121319.519
71 | 2493355.5565 | 1121036.9703
72 | 2493474.5946 | 1121023.6923
73 | 2493500.2957 | 1121038.5165
74 | 2493480.3466 | 1121019.088
75 | 2493070.1934 | 1121325.1682
76 | 2493092.4948 | 1121379.5331
77 | 2493186.5701 | 1121108.4648
78 | 2493228.8941 | 1120977.3401
79 | 2493224.2539 | 1120971.0513
80 | 2493229.0413 | 1120984.7979
81 | 2493373.4327 | 1120919.1079
82 | 2493392.2977 | 1120898.5399
83 | 2493364.2647 | 1120950.9456
84 | 2493303.6904 | 1121092.683
85 | 2493296.2844 | 1121064.7735
86 | 2493295.9261 | 1121106.6692
87 | 2493306.9975 | 1121066.7302
88 | 2493353.4777 | 1121037.0579
89 | 2493401.6242 | 1120913.1938
90 | 2493254.9969 | 1120968.1845
91 | 2493273.4409 | 1121044.3858
92 | 2493251.4183 | 1120957.7854
93 | 2493614.8972 | 1121137.6451
94 | 2493270.1113 | 1121044.5891
95 | 2493274.6498 | 1121073.5165
96 | 2493445.8393 | 1121039.509
97 | 2493772.6095 | 1121056.0691
98 | 2493168.9095 | 1121319.6104
99 | 2493482.4667 | 1121018.032
100 | 2493078.3244 | 1121457.4132
101 | 2493191.7225 | 1121105.857
102 | 2493224.1768 | 1120964.0704
103 | 2493214.8259 | 1120972.6294
104 | 2493293.3486 | 1121111.3108
105 | 2493220.3376 | 1120959.8911
106 | 2493256.0616 | 1120954.6348
107 | 2493282.9657 | 1121090.3248
108 | 2493234.3987 | 1121320.3414
109 | 2493171.4512 | 1121321.3315
110 | 2493207.9848 | 1121100.2569
111 | 2493201.5416 | 1121100.8915
112 | 2493235.3063 | 1121098.7717
113 | 2493214.1373 | 1121129.0538
114 | 2493244.5102 | 1121078.196
115 | 2493185.8476 | 1121079.4771
116 | 2493246.2859 | 1121046.8111
117 | 2493181.4775 | 1121079.7434
118 | 2493198.2773 | 1121057.0571
119 | 2493204.1728 | 1121048.9449
120 | 2493521.0493 | 1121024.2276
121 | 2493524.964 | 1121028.6895
122 | 2493506.2223 | 1121007.547
123 | 2493540.0522 | 1121045.8871
124 | 2493557.0058 | 1121039.4401
125 | 2493558.1816 | 1121015.1527
126 | 2493541.4476 | 1121022.0779
127 | 2494253.4014 | 1121674.3396
128 | 2494237.4017 | 1121648.2251
129 | 2494026.4535 | 1121359.878
130 | 2493873.6355 | 1121191.5169
131 | 2493860.0916 | 1121207.279
132 | 2493807.8703 | 1121083.733
133 | 2493136.1451 | 1121370.8715
134 | 2493136.9255 | 1121369.7765
135 | 2493161.1316 | 1121335.8115
136 | 2493224.3039 | 1121268.2554
137 | 2493447.7418 | 1121511.2805
138 | 2493444.6458 | 1121545.5699
139 | 2493462.2408 | 1121528.223
140 | 2493020.4735 | 1121483.1257
141 | 2493493.2139 | 1121568.6731
142 | 2493490.1129 | 1121565.4071
143 | 2493849.7151 | 1121215.7797
144 | 2493840.7652 | 1121222.0592
145 | 2493834.0795 | 1121226.7527
146 | 2493453.3519 | 1121517.841
147 | 2493471.9113 | 1121545.581
148 | 2493489.9688 | 1121565.2553
149 | 2493483.1747 | 1121558.1002
150 | 2493420.5437 | 1121279.0421

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1