## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6640-7_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6640-7_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6640-7_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6640-7_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6640-7_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6640-7_0_5_node_94 | 0.4 | n |  | TRUE
6 | bus_LV_6640-7_0_5_node_172 | 0.4 | n |  | TRUE
7 | bus_LV_6640-7_0_5_node_95 | 0.4 | n |  | TRUE
8 | bus_LV_6640-7_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_6640-7_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_6640-7_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_6640-7_0_5_node_163 | 0.4 | n |  | TRUE
12 | bus_LV_6640-7_0_5_node_159 | 0.4 | n |  | TRUE
13 | bus_LV_6640-7_0_5_node_135 | 0.4 | n |  | TRUE
14 | bus_LV_6640-7_0_5_node_129 | 0.4 | n |  | TRUE
15 | bus_LV_6640-7_0_5_node_158 | 0.4 | n |  | TRUE
16 | bus_LV_6640-7_0_5_node_104 | 0.4 | n |  | TRUE
17 | bus_LV_6640-7_0_5_node_133 | 0.4 | n |  | TRUE
18 | bus_LV_6640-7_0_5_node_102 | 0.4 | n |  | TRUE
19 | bus_LV_6640-7_0_5_node_127 | 0.4 | n |  | TRUE
20 | bus_LV_6640-7_0_5_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_6640-7_0_5_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_6640-7_0_5_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_6640-7_0_5_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_6640-7_0_5_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_6640-7_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_6640-7_0_5_node_152 | 0.4 | n |  | TRUE
27 | bus_LV_6640-7_0_5_node_150 | 0.4 | n |  | TRUE
28 | bus_LV_6640-7_0_5_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_6640-7_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_6640-7_0_5_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_6640-7_0_5_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_6640-7_0_5_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_6640-7_0_5_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_6640-7_0_5_node_96 | 0.4 | n |  | TRUE
35 | bus_LV_6640-7_0_5_node_167 | 0.4 | n |  | TRUE
36 | bus_LV_6640-7_0_5_node_60 | 0.4 | n |  | TRUE
37 | bus_LV_6640-7_0_5_node_168 | 0.4 | n |  | TRUE
38 | bus_LV_6640-7_0_5_node_72 | 0.4 | n |  | TRUE
39 | bus_LV_6640-7_0_5_node_57 | 0.4 | n |  | TRUE
40 | bus_LV_6640-7_0_5_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_6640-7_0_5_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_6640-7_0_5_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_6640-7_0_5_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_6640-7_0_5_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_6640-7_0_5_node_157 | 0.4 | n |  | TRUE
46 | bus_LV_6640-7_0_5_node_87 | 0.4 | n |  | TRUE
47 | bus_LV_6640-7_0_5_node_156 | 0.4 | n |  | TRUE
48 | bus_LV_6640-7_0_5_node_85 | 0.4 | n |  | TRUE
49 | bus_LV_6640-7_0_5_node_128 | 0.4 | n |  | TRUE
50 | bus_LV_6640-7_0_5_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_6640-7_0_5_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_6640-7_0_5_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_6640-7_0_5_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_6640-7_0_5_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_6640-7_0_5_node_124 | 0.4 | n |  | TRUE
56 | bus_LV_6640-7_0_5_node_161 | 0.4 | n |  | TRUE
57 | bus_LV_6640-7_0_5_node_125 | 0.4 | n |  | TRUE
58 | bus_LV_6640-7_0_5_node_162 | 0.4 | n |  | TRUE
59 | bus_LV_6640-7_0_5_node_31 | 0.4 | n |  | TRUE
60 | bus_LV_6640-7_0_5_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_6640-7_0_5_node_33 | 0.4 | n |  | TRUE
62 | bus_LV_6640-7_0_5_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_6640-7_0_5_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_6640-7_0_5_node_144 | 0.4 | n |  | TRUE
65 | bus_LV_6640-7_0_5_node_155 | 0.4 | n |  | TRUE
66 | bus_LV_6640-7_0_5_node_142 | 0.4 | n |  | TRUE
67 | bus_LV_6640-7_0_5_node_170 | 0.4 | n |  | TRUE
68 | bus_LV_6640-7_0_5_node_171 | 0.4 | n |  | TRUE
69 | bus_LV_6640-7_0_5_node_40 | 0.4 | n |  | TRUE
70 | bus_LV_6640-7_0_5_node_36 | 0.4 | n |  | TRUE
71 | bus_LV_6640-7_0_5_node_37 | 0.4 | n |  | TRUE
72 | bus_LV_6640-7_0_5_node_38 | 0.4 | n |  | TRUE
73 | bus_LV_6640-7_0_5_node_39 | 0.4 | n |  | TRUE
74 | bus_LV_6640-7_0_5_node_77 | 0.4 | n |  | TRUE
75 | bus_LV_6640-7_0_5_node_76 | 0.4 | n |  | TRUE
76 | bus_LV_6640-7_0_5_node_41 | 0.4 | n |  | TRUE
77 | bus_LV_6640-7_0_5_node_42 | 0.4 | n |  | TRUE
78 | bus_LV_6640-7_0_5_node_43 | 0.4 | n |  | TRUE
79 | bus_LV_6640-7_0_5_node_44 | 0.4 | n |  | TRUE
80 | bus_LV_6640-7_0_5_node_45 | 0.4 | n |  | TRUE
81 | bus_LV_6640-7_0_5_node_49 | 0.4 | n |  | TRUE
82 | bus_LV_6640-7_0_5_node_112 | 0.4 | n |  | TRUE
83 | bus_LV_6640-7_0_5_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_6640-7_0_5_node_148 | 0.4 | n |  | TRUE
85 | bus_LV_6640-7_0_5_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_6640-7_0_5_node_46 | 0.4 | n |  | TRUE
87 | bus_LV_6640-7_0_5_node_47 | 0.4 | n |  | TRUE
88 | bus_LV_6640-7_0_5_node_92 | 0.4 | n |  | TRUE
89 | bus_LV_6640-7_0_5_node_131 | 0.4 | n |  | TRUE
90 | bus_LV_6640-7_0_5_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_6640-7_0_5_node_114 | 0.4 | n |  | TRUE
92 | bus_LV_6640-7_0_5_node_116 | 0.4 | n |  | TRUE
93 | bus_LV_6640-7_0_5_node_113 | 0.4 | n |  | TRUE
94 | bus_LV_6640-7_0_5_node_89 | 0.4 | n |  | TRUE
95 | bus_LV_6640-7_0_5_node_115 | 0.4 | n |  | TRUE
96 | bus_LV_6640-7_0_5_node_50 | 0.4 | n |  | TRUE
97 | bus_LV_6640-7_0_5_node_51 | 0.4 | n |  | TRUE
98 | bus_LV_6640-7_0_5_node_52 | 0.4 | n |  | TRUE
99 | bus_LV_6640-7_0_5_node_53 | 0.4 | n |  | TRUE
100 | bus_LV_6640-7_0_5_node_118 | 0.4 | n |  | TRUE
101 | bus_LV_6640-7_0_5_node_154 | 0.4 | n |  | TRUE
102 | bus_LV_6640-7_0_5_node_54 | 0.4 | n |  | TRUE
103 | bus_LV_6640-7_0_5_node_55 | 0.4 | n |  | TRUE
104 | bus_LV_6640-7_0_5_node_56 | 0.4 | n |  | TRUE
105 | bus_LV_6640-7_0_5_node_58 | 0.4 | n |  | TRUE
106 | bus_LV_6640-7_0_5_node_59 | 0.4 | n |  | TRUE
107 | bus_LV_6640-7_0_5_node_65 | 0.4 | n |  | TRUE
108 | bus_LV_6640-7_0_5_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_6640-7_0_5_node_97 | 0.4 | n |  | TRUE
110 | bus_LV_6640-7_0_5_node_74 | 0.4 | n |  | TRUE
111 | bus_LV_6640-7_0_5_node_71 | 0.4 | n |  | TRUE
112 | bus_LV_6640-7_0_5_node_61 | 0.4 | n |  | TRUE
113 | bus_LV_6640-7_0_5_node_62 | 0.4 | n |  | TRUE
114 | bus_LV_6640-7_0_5_node_66 | 0.4 | n |  | TRUE
115 | bus_LV_6640-7_0_5_node_67 | 0.4 | n |  | TRUE
116 | bus_LV_6640-7_0_5_node_68 | 0.4 | n |  | TRUE
117 | bus_LV_6640-7_0_5_node_69 | 0.4 | n |  | TRUE
118 | bus_LV_6640-7_0_5_node_70 | 0.4 | n |  | TRUE
119 | bus_LV_6640-7_0_5_node_75 | 0.4 | n |  | TRUE
120 | bus_LV_6640-7_0_5_node_84 | 0.4 | n |  | TRUE
121 | bus_LV_6640-7_0_5_node_83 | 0.4 | n |  | TRUE
122 | bus_LV_6640-7_0_5_node_106 | 0.4 | n |  | TRUE
123 | bus_LV_6640-7_0_5_node_73 | 0.4 | n |  | TRUE
124 | bus_LV_6640-7_0_5_node_78 | 0.4 | n |  | TRUE
125 | bus_LV_6640-7_0_5_node_79 | 0.4 | n |  | TRUE
126 | bus_LV_6640-7_0_5_node_80 | 0.4 | n |  | TRUE
127 | bus_LV_6640-7_0_5_node_81 | 0.4 | n |  | TRUE
128 | bus_LV_6640-7_0_5_node_82 | 0.4 | n |  | TRUE
129 | bus_LV_6640-7_0_5_node_109 | 0.4 | n |  | TRUE
130 | bus_LV_6640-7_0_5_node_108 | 0.4 | n |  | TRUE
131 | bus_LV_6640-7_0_5_node_107 | 0.4 | n |  | TRUE
132 | bus_LV_6640-7_0_5_node_86 | 0.4 | n |  | TRUE
133 | bus_LV_6640-7_0_5_node_88 | 0.4 | n |  | TRUE
134 | bus_LV_6640-7_0_5_node_130 | 0.4 | n |  | TRUE
135 | bus_LV_6640-7_0_5_node_91 | 0.4 | n |  | TRUE
136 | bus_LV_6640-7_0_5_node_93 | 0.4 | n |  | TRUE
137 | bus_LV_6640-7_0_5_node_166 | 0.4 | n |  | TRUE
138 | bus_LV_6640-7_0_5_node_98 | 0.4 | n |  | TRUE
139 | bus_LV_6640-7_0_5_node_100 | 0.4 | n |  | TRUE
140 | bus_LV_6640-7_0_5_node_101 | 0.4 | n |  | TRUE
141 | bus_LV_6640-7_0_5_node_103 | 0.4 | n |  | TRUE
142 | bus_LV_6640-7_0_5_node_105 | 0.4 | n |  | TRUE
143 | bus_LV_6640-7_0_5_node_146 | 0.4 | n |  | TRUE
144 | bus_LV_6640-7_0_5_node_134 | 0.4 | n |  | TRUE
145 | bus_LV_6640-7_0_5_node_147 | 0.4 | n |  | TRUE
146 | bus_LV_6640-7_0_5_node_123 | 0.4 | n |  | TRUE
147 | bus_LV_6640-7_0_5_node_121 | 0.4 | n |  | TRUE
148 | bus_LV_6640-7_0_5_node_110 | 0.4 | n |  | TRUE
149 | bus_LV_6640-7_0_5_node_111 | 0.4 | n |  | TRUE
150 | bus_LV_6640-7_0_5_node_117 | 0.4 | n |  | TRUE
151 | bus_LV_6640-7_0_5_node_153 | 0.4 | n |  | TRUE
152 | bus_LV_6640-7_0_5_node_169 | 0.4 | n |  | TRUE
153 | bus_LV_6640-7_0_5_node_151 | 0.4 | n |  | TRUE
154 | bus_LV_6640-7_0_5_node_165 | 0.4 | n |  | TRUE
155 | bus_LV_6640-7_0_5_node_119 | 0.4 | n |  | TRUE
156 | bus_LV_6640-7_0_5_node_120 | 0.4 | n |  | TRUE
157 | bus_LV_6640-7_0_5_node_122 | 0.4 | n |  | TRUE
158 | bus_LV_6640-7_0_5_node_141 | 0.4 | n |  | TRUE
159 | bus_LV_6640-7_0_5_node_126 | 0.4 | n |  | TRUE
160 | bus_LV_6640-7_0_5_node_140 | 0.4 | n |  | TRUE
161 | bus_LV_6640-7_0_5_node_138 | 0.4 | n |  | TRUE
162 | bus_LV_6640-7_0_5_node_136 | 0.4 | n |  | TRUE
163 | bus_LV_6640-7_0_5_node_137 | 0.4 | n |  | TRUE
164 | bus_LV_6640-7_0_5_node_139 | 0.4 | n |  | TRUE
165 | bus_LV_6640-7_0_5_node_143 | 0.4 | n |  | TRUE
166 | bus_LV_6640-7_0_5_node_145 | 0.4 | n |  | TRUE
167 | bus_LV_6640-7_0_5_node_160 | 0.4 | n |  | TRUE
168 | bus_LV_6640-7_0_5_node_164 | 0.4 | n |  | TRUE
169 | bus_LV_6640-7_0_5_node_149 | 0.4 | n |  | TRUE
170 | bus_MV_459_1_node_98 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6640-7_0_5_load_0 | 0 | 0.00059732 | 0.0001497 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6640-7_0_5_load_1 | 1 | 0.00041347 | 0.00010363 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6640-7_0_5_load_2 | 2 | 0.0015547 | 0.00038965 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6640-7_0_5_load_3 | 3 | 0.00062706 | 0.00015716 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6640-7_0_5_load_4 | 4 | 0.0015523 | 0.00038904 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6640-7_0_5_load_94 | 5 | 0.0010857 | 0.00027209 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6640-7_0_5_load_172 | 6 | 0.0038231 | 0.00095816 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6640-7_0_5_load_95 | 7 | 0.00072006 | 0.00018046 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6640-7_0_5_load_5 | 8 | 0.00099407 | 0.00024914 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6640-7_0_5_load_6 | 9 | 0.00021111 | 5.291e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6640-7_0_5_load_8 | 10 | 0.00038381 | 9.6192e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6640-7_0_5_load_163 | 11 | 0.00020769 | 5.2052e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6640-7_0_5_load_159 | 12 | 0.0011751 | 0.0002945 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6640-7_0_5_load_135 | 13 | 0.0018807 | 0.00047134 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6640-7_0_5_load_129 | 14 | 0.00097756 | 0.000245 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6640-7_0_5_load_158 | 15 | 0.0021418 | 0.00053677 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6640-7_0_5_load_104 | 16 | 0.0015983 | 0.00040056 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6640-7_0_5_load_133 | 17 | 0.00038018 | 9.5283e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6640-7_0_5_load_102 | 18 | 0.0013273 | 0.00033266 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6640-7_0_5_load_127 | 19 | 0.00034041 | 8.5315e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6640-7_0_5_load_9 | 20 | 0.0012613 | 0.00031612 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6640-7_0_5_load_10 | 21 | 0.0045256 | 0.0011342 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6640-7_0_5_load_11 | 22 | 0.0011387 | 0.00028538 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6640-7_0_5_load_12 | 23 | 0.0019832 | 0.00049702 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6640-7_0_5_load_13 | 24 | 0.0018738 | 0.00046963 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6640-7_0_5_load_14 | 25 | 0.00098752 | 0.00024749 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6640-7_0_5_load_152 | 26 | 0.0018788 | 0.00047086 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6640-7_0_5_load_150 | 27 | 0.0026299 | 0.00065911 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6640-7_0_5_load_15 | 28 | 0.0009863 | 0.00024719 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6640-7_0_5_load_16 | 29 | 0.00092579 | 0.00023203 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6640-7_0_5_load_18 | 31 | 0.00099344 | 0.00024898 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6640-7_0_5_load_19 | 32 | 0.0013193 | 0.00033065 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6640-7_0_5_load_20 | 33 | 0.00038755 | 9.7128e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6640-7_0_5_load_96 | 34 | 0.0014645 | 0.00036703 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6640-7_0_5_load_167 | 35 | 0.0011491 | 0.00028799 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6640-7_0_5_load_168 | 37 | 0.0018056 | 0.00045253 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6640-7_0_5_load_57 | 39 | 0.0018151 | 0.00045492 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6640-7_0_5_load_21 | 40 | 0.0038722 | 0.00097046 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6640-7_0_5_load_22 | 41 | 0.0016993 | 0.0004259 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6640-7_0_5_load_23 | 42 | 0.00049741 | 0.00012466 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6640-7_0_5_load_24 | 43 | 0.00095212 | 0.00023862 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6640-7_0_5_load_25 | 44 | 0.00095057 | 0.00023823 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6640-7_0_5_load_157 | 45 | 0.0010588 | 0.00026536 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6640-7_0_5_load_87 | 46 | 0.00076652 | 0.00019211 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6640-7_0_5_load_156 | 47 | 0.00079574 | 0.00019943 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6640-7_0_5_load_85 | 48 | 0.0036157 | 0.00090618 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6640-7_0_5_load_128 | 49 | 0.0011004 | 0.00027579 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6640-7_0_5_load_26 | 50 | 0.0036401 | 0.00091229 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6640-7_0_5_load_27 | 51 | 0.0021525 | 0.00053947 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6640-7_0_5_load_28 | 52 | 0.0020712 | 0.00051909 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6640-7_0_5_load_29 | 53 | 0.00089121 | 0.00022336 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6640-7_0_5_load_30 | 54 | 0.0035144 | 0.0008808 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6640-7_0_5_load_124 | 55 | 0.0022709 | 0.00056914 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6640-7_0_5_load_161 | 56 | 0.0020559 | 0.00051525 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6640-7_0_5_load_125 | 57 | 0.0013131 | 0.00032909 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6640-7_0_5_load_162 | 58 | 0.002709 | 0.00067893 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6640-7_0_5_load_31 | 59 | 0.0028398 | 0.00071171 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6640-7_0_5_load_32 | 60 | 0.001312 | 0.00032883 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6640-7_0_5_load_34 | 62 | 0.0073904 | 0.0018522 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6640-7_0_5_load_35 | 63 | 0.0017945 | 0.00044973 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6640-7_0_5_load_155 | 65 | 0.00059943 | 0.00015023 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6640-7_0_5_load_142 | 66 | 0.019626 | 0.0049186 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6640-7_0_5_load_170 | 67 | 0.011423 | 0.0028628 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6640-7_0_5_load_40 | 69 | 0.0017045 | 0.00042719 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6640-7_0_5_load_36 | 70 | 0.004395 | 0.0011015 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6640-7_0_5_load_37 | 71 | 0.002669 | 0.00066892 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6640-7_0_5_load_38 | 72 | 0.0017785 | 0.00044574 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6640-7_0_5_load_39 | 73 | 0.001743 | 0.00043685 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6640-7_0_5_load_77 | 74 | 0.0023334 | 0.00058481 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6640-7_0_5_load_76 | 75 | 0.00051029 | 0.00012789 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6640-7_0_5_load_41 | 76 | 0.002015 | 0.00050501 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6640-7_0_5_load_42 | 77 | 0.0011293 | 0.00028303 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6640-7_0_5_load_43 | 78 | 0.0011989 | 0.00030047 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6640-7_0_5_load_44 | 79 | 0.0020233 | 0.0005071 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6640-7_0_5_load_49 | 81 | 0.0014551 | 0.00036468 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6640-7_0_5_load_112 | 82 | 0.0051991 | 0.001303 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6640-7_0_5_load_64 | 83 | 0.001766 | 0.00044261 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6640-7_0_5_load_46 | 86 | 0.0014574 | 0.00036526 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6640-7_0_5_load_47 | 87 | 0.0013869 | 0.00034759 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6640-7_0_5_load_92 | 88 | 0.0012518 | 0.00031373 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6640-7_0_5_load_131 | 89 | 0.001009 | 0.00025289 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6640-7_0_5_load_90 | 90 | 0.0025046 | 0.0006277 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6640-7_0_5_load_114 | 91 | 0.0014418 | 0.00036136 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6640-7_0_5_load_116 | 92 | 0.0013208 | 0.00033103 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6640-7_0_5_load_113 | 93 | 0.0030402 | 0.00076196 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6640-7_0_5_load_89 | 94 | 0.00099574 | 0.00024956 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6640-7_0_5_load_50 | 96 | 0.0017534 | 0.00043944 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6640-7_0_5_load_51 | 97 | 0.0018316 | 0.00045903 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_6640-7_0_5_load_52 | 98 | 0.00074642 | 0.00018707 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_6640-7_0_5_load_53 | 99 | 0.001439 | 0.00036064 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_6640-7_0_5_load_118 | 100 | 0.00082053 | 0.00020564 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_6640-7_0_5_load_154 | 101 | 0.0014116 | 0.00035379 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_6640-7_0_5_load_54 | 102 | 0.0047107 | 0.0011806 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_6640-7_0_5_load_55 | 103 | 0.0018064 | 0.00045273 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_6640-7_0_5_load_58 | 105 | 0.00062979 | 0.00015784 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_6640-7_0_5_load_59 | 106 | 0.00038991 | 9.7722e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_6640-7_0_5_load_65 | 107 | 0.00040236 | 0.00010084 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_6640-7_0_5_load_99 | 108 | 0.0021147 | 0.00052999 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_6640-7_0_5_load_97 | 109 | 0.0004073 | 0.00010208 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_6640-7_0_5_load_74 | 110 | 0.00045987 | 0.00011526 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_6640-7_0_5_load_71 | 111 | 0.0031164 | 0.00078104 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_6640-7_0_5_load_61 | 112 | 0.0030255 | 0.00075825 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_6640-7_0_5_load_62 | 113 | 0.0050157 | 0.0012571 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_6640-7_0_5_load_66 | 114 | 0.0039597 | 0.00099239 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_6640-7_0_5_load_67 | 115 | 0.0049335 | 0.0012365 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_6640-7_0_5_load_68 | 116 | 0.0014589 | 0.00036564 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_6640-7_0_5_load_69 | 117 | 0.0023035 | 0.00057732 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_6640-7_0_5_load_75 | 119 | 0.0059358 | 0.0014876 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_6640-7_0_5_load_84 | 120 | 0.0009656 | 0.000242 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_6640-7_0_5_load_83 | 121 | 0.0011444 | 0.00028681 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_6640-7_0_5_load_106 | 122 | 0.0013994 | 0.00035073 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_6640-7_0_5_load_73 | 123 | 0.00081502 | 0.00020426 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_6640-7_0_5_load_78 | 124 | 0.00065638 | 0.0001645 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_6640-7_0_5_load_79 | 125 | 0.0012443 | 0.00031184 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_6640-7_0_5_load_80 | 126 | 0.00038425 | 9.6303e-05 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_6640-7_0_5_load_81 | 127 | 0.0010202 | 0.00025567 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_6640-7_0_5_load_82 | 128 | 0.0071473 | 0.0017913 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_6640-7_0_5_load_109 | 129 | 0.0009725 | 0.00024373 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_6640-7_0_5_load_108 | 130 | 0.00043703 | 0.00010953 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_6640-7_0_5_load_107 | 131 | 0.001167 | 0.00029248 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_6640-7_0_5_load_86 | 132 | 0.0025711 | 0.00064438 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_6640-7_0_5_load_88 | 133 | 0.0068946 | 0.0017279 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_6640-7_0_5_load_130 | 134 | 0.0010728 | 0.00026887 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_6640-7_0_5_load_91 | 135 | 0.0025958 | 0.00065057 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_6640-7_0_5_load_93 | 136 | 0.0013779 | 0.00034534 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_6640-7_0_5_load_166 | 137 | 0.0012332 | 0.00030906 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_6640-7_0_5_load_98 | 138 | 0.0019489 | 0.00048845 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_6640-7_0_5_load_100 | 139 | 0.00225 | 0.00056389 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_6640-7_0_5_load_101 | 140 | 0.002109 | 0.00052858 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_6640-7_0_5_load_146 | 143 | 0.0019023 | 0.00047677 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_6640-7_0_5_load_134 | 144 | 0.0021647 | 0.00054253 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_6640-7_0_5_load_147 | 145 | 0.0022548 | 0.0005651 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_6640-7_0_5_load_123 | 146 | 0.0019153 | 0.00048001 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_6640-7_0_5_load_121 | 147 | 0.00086924 | 0.00021785 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_6640-7_0_5_load_110 | 148 | 0.00089356 | 0.00022395 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_6640-7_0_5_load_111 | 149 | 0.00086435 | 0.00021663 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_6640-7_0_5_load_169 | 152 | 0.0016469 | 0.00041276 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_6640-7_0_5_load_151 | 153 | 0.00078587 | 0.00019696 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_6640-7_0_5_load_165 | 154 | 0.0017786 | 0.00044576 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_6640-7_0_5_load_119 | 155 | 0.0027193 | 0.00068151 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_6640-7_0_5_load_120 | 156 | 0.0027543 | 0.00069029 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_6640-7_0_5_load_122 | 157 | 0.0016087 | 0.00040318 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_6640-7_0_5_load_141 | 158 | 0.0013639 | 0.00034182 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_6640-7_0_5_load_126 | 159 | 0.0022103 | 0.00055396 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_6640-7_0_5_load_140 | 160 | 0.0040395 | 0.0010124 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_6640-7_0_5_load_138 | 161 | 0.00080895 | 0.00020274 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_6640-7_0_5_load_136 | 162 | 0.00062631 | 0.00015697 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_6640-7_0_5_load_137 | 163 | 0.00090747 | 0.00022743 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_6640-7_0_5_load_139 | 164 | 0.002503 | 0.0006273 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_6640-7_0_5_load_143 | 165 | 0.0069203 | 0.0017344 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_6640-7_0_5_load_145 | 166 | 0.0021442 | 0.00053739 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_6640-7_0_5_load_160 | 167 | 0.0067606 | 0.0016944 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_6640-7_0_5_load_164 | 168 | 0.0079999 | 0.002005 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_6640-7_0_5_load_149 | 169 | 0.00036833 | 9.2312e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6640-7_0_5_line_0 |  | 0 | 1 | 0.0030109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6640-7_0_5_line_1 |  | 0 | 2 | 0.011835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6640-7_0_5_line_2 |  | 1 | 3 | 0.011073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6640-7_0_5_line_3 |  | 2 | 4 | 0.021069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6640-7_0_5_line_4 |  | 3 | 5 | 0.014271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6640-7_0_5_line_5 |  | 4 | 6 | 0.051283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6640-7_0_5_line_6 |  | 5 | 7 | 0.00048227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6640-7_0_5_line_7 |  | 7 | 34 | 0.030728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6640-7_0_5_line_8 |  | 8 | 9 | 0.010393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6640-7_0_5_line_9 |  | 9 | 10 | 0.0020903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6640-7_0_5_line_10 |  | 10 | 14 | 0.009396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6640-7_0_5_line_11 |  | 11 | 12 | 0.017823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6640-7_0_5_line_12 |  | 11 | 13 | 0.0077525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6640-7_0_5_line_13 |  | 12 | 15 | 0.0015821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6640-7_0_5_line_14 |  | 13 | 144 | 0.0019102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6640-7_0_5_line_15 |  | 14 | 19 | 0.050693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6640-7_0_5_line_16 |  | 15 | 47 | 0.0038724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6640-7_0_5_line_17 |  | 16 | 17 | 0.0011281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6640-7_0_5_line_18 |  | 16 | 18 | 0.017819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6640-7_0_5_line_19 |  | 17 | 144 | 0.0053078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6640-7_0_5_line_20 |  | 18 | 140 | 0.0093607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6640-7_0_5_line_21 |  | 19 | 49 | 0.030712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6640-7_0_5_line_22 |  | 20 | 21 | 0.0013404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6640-7_0_5_line_23 |  | 20 | 22 | 0.018061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6640-7_0_5_line_24 |  | 21 | 23 | 0.00060606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6640-7_0_5_line_25 |  | 22 | 24 | 0.0020366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6640-7_0_5_line_26 |  | 23 | 25 | 0.019039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6640-7_0_5_line_27 |  | 25 | 26 | 0.0071211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6640-7_0_5_line_28 |  | 26 | 27 | 0.0074656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6640-7_0_5_line_29 |  | 27 | 169 | 0.024303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6640-7_0_5_line_30 |  | 28 | 29 | 0.042572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6640-7_0_5_line_31 |  | 28 | 30 | 0.001429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6640-7_0_5_line_32 |  | 30 | 31 | 0.01737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6640-7_0_5_line_33 |  | 30 | 32 | 0.050144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6640-7_0_5_line_34 |  | 30 | 33 | 0.033358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6640-7_0_5_line_35 |  | 31 | 34 | 0.034904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6640-7_0_5_line_36 |  | 32 | 35 | 0.0095581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6640-7_0_5_line_37 |  | 33 | 36 | 0.019371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6640-7_0_5_line_38 |  | 35 | 37 | 0.01683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6640-7_0_5_line_39 |  | 36 | 38 | 0.02468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_6640-7_0_5_line_40 |  | 36 | 39 | 0.033908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_6640-7_0_5_line_41 |  | 38 | 110 | 0.029551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_6640-7_0_5_line_42 |  | 38 | 111 | 0.033202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6640-7_0_5_line_43 |  | 39 | 103 | 0.00423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_6640-7_0_5_line_44 |  | 40 | 41 | 0.0067591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6640-7_0_5_line_45 |  | 40 | 42 | 0.005315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6640-7_0_5_line_46 |  | 41 | 43 | 0.010609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6640-7_0_5_line_47 |  | 42 | 44 | 0.0086833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6640-7_0_5_line_48 |  | 43 | 45 | 0.0082989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6640-7_0_5_line_49 |  | 44 | 46 | 0.0079169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6640-7_0_5_line_50 |  | 45 | 47 | 0.014994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6640-7_0_5_line_51 |  | 46 | 48 | 0.013507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6640-7_0_5_line_52 |  | 48 | 132 | 0.0065908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6640-7_0_5_line_53 |  | 49 | 134 | 0.045622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6640-7_0_5_line_54 |  | 50 | 51 | 0.025188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6640-7_0_5_line_55 |  | 50 | 52 | 0.0028785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6640-7_0_5_line_56 |  | 51 | 53 | 0.0077567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6640-7_0_5_line_57 |  | 52 | 54 | 0.00060377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6640-7_0_5_line_58 |  | 53 | 55 | 0.0069068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6640-7_0_5_line_59 |  | 54 | 56 | 0.0039636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6640-7_0_5_line_60 |  | 55 | 57 | 0.00058011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6640-7_0_5_line_61 |  | 56 | 58 | 0.067444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_6640-7_0_5_line_62 |  | 57 | 159 | 0.017904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6640-7_0_5_line_63 |  | 58 | 139 | 0.0060197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_6640-7_0_5_line_64 |  | 59 | 60 | 0.019761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_6640-7_0_5_line_65 |  | 59 | 61 | 0.061348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_6640-7_0_5_line_66 |  | 60 | 62 | 0.033199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6640-7_0_5_line_67 |  | 61 | 63 | 0.048734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_6640-7_0_5_line_68 |  | 62 | 64 | 0.0073781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6640-7_0_5_line_69 |  | 63 | 65 | 0.019611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_6640-7_0_5_line_70 |  | 64 | 66 | 0.033282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6640-7_0_5_line_71 |  | 65 | 69 | 0.0020005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_6640-7_0_5_line_72 |  | 66 | 165 | 0.035398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6640-7_0_5_line_73 |  | 66 | 68 | 0.17476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6640-7_0_5_line_74 |  | 67 | 68 | 0.065839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6640-7_0_5_line_75 |  | 69 | 72 | 0.01093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_6640-7_0_5_line_76 |  | 70 | 71 | 0.018672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_6640-7_0_5_line_77 |  | 70 | 72 | 0.0040695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_6640-7_0_5_line_78 |  | 71 | 73 | 0.0064466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_6640-7_0_5_line_79 |  | 73 | 74 | 0.0021969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_6640-7_0_5_line_80 |  | 74 | 75 | 0.0096553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_6640-7_0_5_line_81 |  | 75 | 119 | 0.015808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_6640-7_0_5_line_82 |  | 76 | 77 | 0.015407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6640-7_0_5_line_83 |  | 76 | 78 | 0.0067816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_6640-7_0_5_line_84 |  | 77 | 79 | 0.030725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_6640-7_0_5_line_85 |  | 78 | 80 | 0.020297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6640-7_0_5_line_86 |  | 79 | 81 | 0.0076053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6640-7_0_5_line_87 |  | 80 | 82 | 0.016746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_6640-7_0_5_line_88 |  | 80 | 83 | 0.0081056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_6640-7_0_5_line_89 |  | 82 | 84 | 0.034448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_6640-7_0_5_line_90 |  | 83 | 85 | 0.018834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_6640-7_0_5_line_91 |  | 84 | 101 | 0.023911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_6640-7_0_5_line_92 |  | 84 | 142 | 0.042988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_6640-7_0_5_line_93 |  | 85 | 107 | 0.027234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_6640-7_0_5_line_94 |  | 85 | 112 | 0.030559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_6640-7_0_5_line_95 |  | 86 | 87 | 0.021593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_6640-7_0_5_line_96 |  | 86 | 88 | 0.060692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_6640-7_0_5_line_97 |  | 88 | 89 | 0.0043577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_6640-7_0_5_line_98 |  | 88 | 90 | 0.029687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_6640-7_0_5_line_99 |  | 90 | 94 | 0.0088742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_6640-7_0_5_line_100 |  | 91 | 92 | 0.0086117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_6640-7_0_5_line_101 |  | 91 | 93 | 0.021492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_6640-7_0_5_line_102 |  | 92 | 137 | 0.0047686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_6640-7_0_5_line_103 |  | 93 | 95 | 0.037062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_6640-7_0_5_line_104 |  | 94 | 135 | 0.03479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_6640-7_0_5_line_105 |  | 95 | 150 | 0.031214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_6640-7_0_5_line_106 |  | 96 | 97 | 0.017249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_6640-7_0_5_line_107 |  | 96 | 98 | 0.0078655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_6640-7_0_5_line_108 |  | 97 | 99 | 0.028249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_6640-7_0_5_line_109 |  | 99 | 100 | 0.019853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_6640-7_0_5_line_110 |  | 100 | 101 | 0.0031857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_6640-7_0_5_line_111 |  | 102 | 103 | 0.017745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_6640-7_0_5_line_112 |  | 102 | 104 | 0.0068381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_6640-7_0_5_line_113 |  | 104 | 105 | 0.0080845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_6640-7_0_5_line_114 |  | 104 | 106 | 0.027612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_6640-7_0_5_line_115 |  | 105 | 107 | 0.013764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_6640-7_0_5_line_116 |  | 106 | 108 | 0.0032433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_6640-7_0_5_line_117 |  | 108 | 109 | 0.0096849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_6640-7_0_5_line_118 |  | 109 | 138 | 0.0051911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_6640-7_0_5_line_119 |  | 110 | 121 | 0.011718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_6640-7_0_5_line_120 |  | 111 | 123 | 0.022363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_6640-7_0_5_line_121 |  | 112 | 113 | 0.032634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_6640-7_0_5_line_122 |  | 114 | 115 | 0.034789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_6640-7_0_5_line_123 |  | 114 | 116 | 0.00063602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_6640-7_0_5_line_124 |  | 115 | 117 | 0.0016932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_6640-7_0_5_line_125 |  | 116 | 118 | 0.028846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_6640-7_0_5_line_126 |  | 117 | 119 | 0.031531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_6640-7_0_5_line_127 |  | 118 | 120 | 0.041359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_6640-7_0_5_line_128 |  | 118 | 121 | 0.014586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_6640-7_0_5_line_129 |  | 120 | 122 | 0.011892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_6640-7_0_5_line_130 |  | 122 | 131 | 0.016701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_6640-7_0_5_line_131 |  | 124 | 125 | 0.0024332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_6640-7_0_5_line_132 |  | 124 | 126 | 0.0085883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_6640-7_0_5_line_133 |  | 125 | 127 | 0.011088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_6640-7_0_5_line_134 |  | 126 | 128 | 0.0024352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_6640-7_0_5_line_135 |  | 127 | 129 | 0.024066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_6640-7_0_5_line_136 |  | 129 | 130 | 0.010871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_6640-7_0_5_line_137 |  | 130 | 148 | 0.039373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_6640-7_0_5_line_138 |  | 131 | 146 | 0.013508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_6640-7_0_5_line_139 |  | 132 | 133 | 0.008522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_6640-7_0_5_line_140 |  | 133 | 134 | 0.1068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_6640-7_0_5_line_141 |  | 135 | 136 | 0.0067943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_6640-7_0_5_line_142 |  | 136 | 137 | 0.045596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_6640-7_0_5_line_143 |  | 138 | 139 | 0.0234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
144 | LV_6640-7_0_5_line_144 |  | 140 | 141 | 0.023277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_6640-7_0_5_line_145 |  | 141 | 142 | 0.024517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_6640-7_0_5_line_146 |  | 142 | 143 | 0.022508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_6640-7_0_5_line_147 |  | 143 | 145 | 0.039856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_6640-7_0_5_line_148 |  | 145 | 149 | 0.031243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_6640-7_0_5_line_149 |  | 146 | 147 | 0.012674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_6640-7_0_5_line_150 |  | 147 | 155 | 0.019144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_6640-7_0_5_line_151 |  | 148 | 149 | 0.012164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_6640-7_0_5_line_152 |  | 150 | 151 | 0.073589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_6640-7_0_5_line_153 |  | 150 | 152 | 0.027968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_6640-7_0_5_line_154 |  | 151 | 153 | 0.059938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_6640-7_0_5_line_155 |  | 152 | 154 | 0.0075128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_6640-7_0_5_line_156 |  | 153 | 169 | 0.012336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_6640-7_0_5_line_157 |  | 154 | 158 | 0.024337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_6640-7_0_5_line_158 |  | 155 | 156 | 0.013773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_6640-7_0_5_line_159 |  | 156 | 157 | 0.013714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_6640-7_0_5_line_160 |  | 157 | 158 | 0.011181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_6640-7_0_5_line_161 |  | 159 | 160 | 0.0076456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_6640-7_0_5_line_162 |  | 160 | 161 | 0.0014505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_6640-7_0_5_line_163 |  | 161 | 162 | 0.01331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_6640-7_0_5_line_164 |  | 162 | 163 | 0.0015715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_6640-7_0_5_line_165 |  | 163 | 164 | 0.020206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_6640-7_0_5_line_166 |  | 165 | 166 | 0.0096144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_6640-7_0_5_line_167 |  | 166 | 167 | 0.022171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_6640-7_0_5_line_168 |  | 167 | 168 | 0.033567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6640-7_0_5_trafo_161 | 0.63 MVA 20/0.4 kV | 170 | 56 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2504733.5576 | 1117083.6264 | 2504735.6731 | 1117085.7688
1 | 2504733.5576 | 1117083.6264 | 2504725.242 | 1117075.2054
2 | 2504735.6731 | 1117085.7688 | 2504743.4532 | 1117093.6475
3 | 2504725.242 | 1117075.2054 | 2504723.7924 | 1117073.7374 | 2504719.2755 | 1117071.2515 | 2504709.6458 | 1117061.297
4 | 2504743.4532 | 1117093.6475 | 2504753.4807 | 1117103.8022
5 | 2504709.6458 | 1117061.297 | 2504738.3287 | 1117018.786
6 | 2504753.4807 | 1117103.8022 | 2504753.8196 | 1117104.1453
7 | 2504753.8196 | 1117104.1453 | 2504765.0671 | 1117115.5355 | 2504775.5823 | 1117125.8377
8 | 2504766.4418 | 1117573.3501 | 2504771.9438 | 1117573.7081 | 2504776.7367 | 1117574.6221
9 | 2504778.6221 | 1117575.5248 | 2504776.7367 | 1117574.6221 | 2504776.7367 | 1117574.6221
10 | 2504785.6762 | 1117581.4968 | 2504781.4581 | 1117576.8826 | 2504778.6221 | 1117575.5248
11 | 2504835.2071 | 1117459.227 | 2504850.0374 | 1117469.112
12 | 2504835.2071 | 1117459.227 | 2504828.7563 | 1117454.9272
13 | 2504851.3539 | 1117469.9895 | 2504850.0374 | 1117469.112
14 | 2504827.1668 | 1117453.8678 | 2504828.7563 | 1117454.9272
15 | 2504785.6762 | 1117581.4968 | 2504785.6762 | 1117581.4968 | 2504789.7618 | 1117588.9704 | 2504792.5225 | 1117592.707 | 2504794.4501 | 1117595.0114 | 2504796.5431 | 1117596.0569 | 2504800.346 | 1117597.3423 | 2504810.3933 | 1117600.0525 | 2504823.4474 | 1117604.9724 | 2504826.9339 | 1117606.52
16 | 2504851.3539 | 1117469.9895 | 2504854.5761 | 1117472.1373
17 | 2504822.7502 | 1117450.9239 | 2504821.8115 | 1117450.2982
18 | 2504821.8115 | 1117450.2982 | 2504806.9846 | 1117440.4155
19 | 2504827.1668 | 1117453.8678 | 2504822.7502 | 1117450.9239
20 | 2504799.1956 | 1117435.2237 | 2504806.9846 | 1117440.4155
21 | 2504855.5196 | 1117617.6951 | 2504851.9284 | 1117616.4759 | 2504837.3316 | 1117611.1355 | 2504826.9339 | 1117606.52
22 | 2505058.7257 | 1117153.5716 | 2505059.217 | 1117152.3245
23 | 2505052.1055 | 1117170.3757 | 2505058.7257 | 1117153.5716
24 | 2505059.217 | 1117152.3245 | 2505059.4392 | 1117151.7606
25 | 2505051.359 | 1117172.2706 | 2505052.1055 | 1117170.3757
26 | 2505059.4392 | 1117151.7606 | 2505066.4178 | 1117134.0468
27 | 2505069.028 | 1117127.4213 | 2505066.4178 | 1117134.0468
28 | 2505069.028 | 1117127.4213 | 2505071.7645 | 1117120.4754
29 | 2505071.7645 | 1117120.4754 | 2505078.2349 | 1117104.0515 | 2505080.6565 | 1117097.858
30 | 2504767.226 | 1117153.5915 | 2504777.214 | 1117156.903 | 2504788.1238 | 1117160.4112 | 2504808.414 | 1117163.9072
31 | 2504809.8223 | 1117164.1499 | 2504808.414 | 1117163.9072
32 | 2504809.8223 | 1117164.1499 | 2504808.4445 | 1117158.0344 | 2504800.5144 | 1117150.265
33 | 2504809.8223 | 1117164.1499 | 2504814.2522 | 1117158.6657 | 2504839.5432 | 1117134.1195 | 2504845.1187 | 1117128.5932
34 | 2504809.8223 | 1117164.1499 | 2504835.4758 | 1117169.0159 | 2504842.485 | 1117170.8559
35 | 2504800.5144 | 1117150.265 | 2504775.5823 | 1117125.8377
36 | 2504851.9073 | 1117121.8647 | 2504845.1187 | 1117128.5932
37 | 2504860.4743 | 1117177.8949 | 2504847.9025 | 1117172.278 | 2504842.485 | 1117170.8559
38 | 2504861.4976 | 1117108.4918 | 2504859.2163 | 1117114.6203 | 2504851.9073 | 1117121.8647
39 | 2504860.4743 | 1117177.8949 | 2504871.239 | 1117181.5056 | 2504884.0317 | 1117185.4625
40 | 2504860.4743 | 1117177.8949 | 2504855.738 | 1117189.9101 | 2504849.4641 | 1117209.9432
41 | 2504884.0317 | 1117185.4625 | 2504912.0438 | 1117194.8745
42 | 2504884.0317 | 1117185.4625 | 2504886.7308 | 1117178.8938 | 2504899.1967 | 1117155.9628
43 | 2504848.1999 | 1117213.98 | 2504849.4641 | 1117209.9432
44 | 2504888.4097 | 1117494.6889 | 2504882.7855 | 1117490.9401
45 | 2504892.8323 | 1117497.6367 | 2504888.4097 | 1117494.6889
46 | 2504882.7855 | 1117490.9401 | 2504873.9578 | 1117485.0561
47 | 2504892.8323 | 1117497.6367 | 2504900.0576 | 1117502.4527
48 | 2504867.0524 | 1117480.4533 | 2504873.9578 | 1117485.0561
49 | 2504906.6452 | 1117506.8437 | 2504900.0576 | 1117502.4527
50 | 2504867.0524 | 1117480.4533 | 2504854.5761 | 1117472.1373
51 | 2504917.8846 | 1117514.3352 | 2504906.6452 | 1117506.8437
52 | 2504917.8846 | 1117514.3352 | 2504923.3688 | 1117517.9906
53 | 2504855.5196 | 1117617.6951 | 2504861.5366 | 1117619.7379 | 2504873.2922 | 1117622.5992 | 2504883.2391 | 1117624.3328 | 2504895.5054 | 1117625.3072 | 2504900.2707 | 1117625.1604
54 | 2504940.7644 | 1117336.4637 | 2504951.8324 | 1117313.8376
55 | 2504953.0973 | 1117311.2519 | 2504951.8324 | 1117313.8376
56 | 2504937.356 | 1117343.4314 | 2504940.7644 | 1117336.4637
57 | 2504953.0973 | 1117311.2519 | 2504953.3626 | 1117310.7095
58 | 2504937.356 | 1117343.4314 | 2504934.321 | 1117349.6357
59 | 2504953.3626 | 1117310.7095 | 2504955.1043 | 1117307.1491
60 | 2504934.0661 | 1117350.1568 | 2504934.321 | 1117349.6357
61 | 2504910.0314 | 1117266.3173 | 2504947.2039 | 1117286.5205 | 2504953.7164 | 1117290.743 | 2504956.3468 | 1117295.0265 | 2504956.679 | 1117301.4252 | 2504955.2063 | 1117306.9406 | 2504955.1043 | 1117307.1491
62 | 2504934.0661 | 1117350.1568 | 2504926.1987 | 1117366.2399
63 | 2504910.0314 | 1117266.3173 | 2504904.7424 | 1117263.4428
64 | 2505142.3015 | 1117363.4838 | 2505142.4838 | 1117362.969 | 2505145.7612 | 1117353.3896 | 2505148.0171 | 1117344.5836
65 | 2505158.2239 | 1117284.174 | 2505157.4046 | 1117291.4913 | 2505155.8048 | 1117304.1797 | 2505154.0354 | 1117317.8603 | 2505151.2797 | 1117331.6564 | 2505149.413 | 1117339.1347 | 2505148.0171 | 1117344.5836
66 | 2505142.3015 | 1117363.4838 | 2505138.7728 | 1117373.4447 | 2505134.3412 | 1117383.7539 | 2505129.8176 | 1117394.2296
67 | 2505158.2239 | 1117284.174 | 2505137.1039 | 1117276.9118 | 2505119.5623 | 1117270.4051 | 2505114.0175 | 1117268.3241 | 2505112.36 | 1117267.7064
68 | 2505126.822 | 1117400.9712 | 2505127.8157 | 1117398.8654 | 2505129.8176 | 1117394.2296
69 | 2505094.0189 | 1117260.7637 | 2505109.7233 | 1117266.7238 | 2505112.36 | 1117267.7064
70 | 2505126.822 | 1117400.9712 | 2505122.7583 | 1117409.6291 | 2505115.7542 | 1117422.7692 | 2505111.4112 | 1117430.4543
71 | 2505092.1486 | 1117260.0539 | 2505094.0189 | 1117260.7637
72 | 2505111.4112 | 1117430.4543 | 2505107.5069 | 1117437.3631 | 2505100.4544 | 1117448.8919 | 2505092.3196 | 1117460.2218
73 | 2505111.4112 | 1117430.4543 | 2505262.6119 | 1117518.0927
74 | 2505262.6119 | 1117518.0927 | 2505265.4287 | 1117513.6014 | 2505301.5586 | 1117465.0279
75 | 2505092.1486 | 1117260.0539 | 2505084.4052 | 1117257.1151 | 2505081.9293 | 1117256.177
76 | 2505078.1238 | 1117254.7351 | 2505060.6628 | 1117248.1191
77 | 2505078.1238 | 1117254.7351 | 2505081.9293 | 1117256.177
78 | 2505060.6628 | 1117248.1191 | 2505057.5262 | 1117246.9306 | 2505054.6344 | 1117245.8351
79 | 2505052.58 | 1117245.0568 | 2505054.6344 | 1117245.8351
80 | 2505043.5509 | 1117241.6363 | 2505052.58 | 1117245.0568
81 | 2505043.5509 | 1117241.6363 | 2505041.2948 | 1117240.7816 | 2505030.6626 | 1117236.746 | 2505028.7703 | 1117236.0288
82 | 2504841.9053 | 1117320.2727 | 2504856.0711 | 1117326.3301
83 | 2504841.9053 | 1117320.2727 | 2504835.6698 | 1117317.6064
84 | 2504856.0711 | 1117326.3301 | 2504884.3214 | 1117338.4102
85 | 2504817.007 | 1117309.626 | 2504835.6698 | 1117317.6064
86 | 2504884.3214 | 1117338.4102 | 2504891.3142 | 1117341.4004
87 | 2504817.007 | 1117309.626 | 2504811.7599 | 1117325.5283
88 | 2504817.007 | 1117309.626 | 2504819.5477 | 1117301.9289
89 | 2504800.9661 | 1117358.2415 | 2504811.7599 | 1117325.5283
90 | 2504825.4514 | 1117284.0441 | 2504819.5477 | 1117301.9289
91 | 2504800.9661 | 1117358.2415 | 2504822.6419 | 1117368.3366
92 | 2504800.9661 | 1117358.2415 | 2504788.5754 | 1117399.4062
93 | 2504825.4514 | 1117284.0441 | 2504833.997 | 1117258.1854
94 | 2504825.4514 | 1117284.0441 | 2504796.9462 | 1117273.0304
95 | 2504905.4198 | 1116951.5162 | 2504905.4198 | 1116951.5162 | 2504909.589 | 1116953.9855 | 2504925.3748 | 1116959.5795
96 | 2504855.0882 | 1116985.4316 | 2504905.4198 | 1116951.5162
97 | 2504855.0882 | 1116985.4316 | 2504852.1825 | 1116982.184
98 | 2504855.0882 | 1116985.4316 | 2504874.8834 | 1117007.555
99 | 2504880.8007 | 1117014.1683 | 2504874.8834 | 1117007.555
100 | 2504957.6964 | 1117040.2115 | 2504964.2115 | 1117034.5799
101 | 2504964.2115 | 1117034.5799 | 2504980.4707 | 1117020.5255
102 | 2504954.0888 | 1117043.33 | 2504957.6964 | 1117040.2115
103 | 2505006.9157 | 1116994.9707 | 2505003.8041 | 1117000.3562 | 2504980.4707 | 1117020.5255
104 | 2504880.8007 | 1117014.1683 | 2504903.9987 | 1117040.0947
105 | 2505032.9579 | 1117012.2614 | 2505018.5157 | 1117002.1041 | 2505006.9157 | 1116994.9707
106 | 2504884.7711 | 1117397.2721 | 2504869.135 | 1117389.9899
107 | 2504891.9011 | 1117400.5928 | 2504884.7711 | 1117397.2721
108 | 2504843.5268 | 1117378.0634 | 2504869.135 | 1117389.9899
109 | 2504843.5268 | 1117378.0634 | 2504825.5298 | 1117369.6816
110 | 2504822.6419 | 1117368.3366 | 2504825.5298 | 1117369.6816
111 | 2504842.8964 | 1117230.9144 | 2504848.1999 | 1117213.98
112 | 2504840.8527 | 1117237.44 | 2504842.8964 | 1117230.9144
113 | 2504840.8527 | 1117237.44 | 2504838.316 | 1117245.1162
114 | 2504840.8527 | 1117237.44 | 2504866.8201 | 1117246.8274
115 | 2504833.997 | 1117258.1854 | 2504838.316 | 1117245.1162
116 | 2504869.8702 | 1117247.93 | 2504866.8201 | 1117246.8274
117 | 2504869.8702 | 1117247.93 | 2504878.9782 | 1117251.2227
118 | 2504878.9782 | 1117251.2227 | 2504883.8601 | 1117252.9875
119 | 2504912.0438 | 1117194.8745 | 2504923.1519 | 1117198.6068
120 | 2504909.8778 | 1117136.315 | 2504899.1967 | 1117155.9628
121 | 2504766.5056 | 1117261.2689 | 2504796.9462 | 1117273.0304
122 | 2504965.0136 | 1117212.3739 | 2504974.4967 | 1117215.4593 | 2504997.7019 | 1117224.2571
123 | 2504964.4088 | 1117212.1771 | 2504965.0136 | 1117212.3739
124 | 2504997.7019 | 1117224.2571 | 2504999.2851 | 1117224.8573
125 | 2504936.9781 | 1117203.2523 | 2504964.4088 | 1117212.1771
126 | 2505028.7703 | 1117236.0288 | 2505009.3675 | 1117228.6754 | 2505002.8516 | 1117226.2095 | 2504999.2851 | 1117224.8573
127 | 2504936.9781 | 1117203.2523 | 2504940.0205 | 1117196.4226 | 2504955.1683 | 1117166.1152
128 | 2504936.9781 | 1117203.2523 | 2504923.1519 | 1117198.6068
129 | 2504960.4847 | 1117155.4782 | 2504955.1683 | 1117166.1152
130 | 2504960.4847 | 1117155.4782 | 2504967.9512 | 1117140.5394
131 | 2504956.2901 | 1117496.1193 | 2504954.1822 | 1117494.9038
132 | 2504963.73 | 1117500.4096 | 2504956.2901 | 1117496.1193
133 | 2504944.5765 | 1117489.3647 | 2504954.1822 | 1117494.9038
134 | 2504965.8396 | 1117501.6261 | 2504963.73 | 1117500.4096
135 | 2504923.7284 | 1117477.3426 | 2504944.5765 | 1117489.3647
136 | 2504914.3113 | 1117471.9122 | 2504923.7284 | 1117477.3426
137 | 2504880.2028 | 1117452.2434 | 2504914.3113 | 1117471.9122
138 | 2504973.9901 | 1117128.4567 | 2504967.9512 | 1117140.5394
139 | 2504930.4598 | 1117522.7172 | 2504923.3688 | 1117517.9906
140 | 2504930.4598 | 1117522.7172 | 2504900.2707 | 1117625.1604
141 | 2504908.5292 | 1117045.1581 | 2504903.9987 | 1117040.0947
142 | 2504954.0888 | 1117043.33 | 2504908.5292 | 1117045.1581
143 | 2504904.7424 | 1117263.4428 | 2504888.7735 | 1117254.7637 | 2504883.8601 | 1117252.9875
144 | 2504779.8267 | 1117422.3135 | 2504799.1956 | 1117435.2237
145 | 2504788.5754 | 1117399.4062 | 2504779.8267 | 1117422.3135
146 | 2504788.5754 | 1117399.4062 | 2504808.0739 | 1117410.6501
147 | 2504808.0739 | 1117410.6501 | 2504842.6002 | 1117430.5598
148 | 2504842.6002 | 1117430.5598 | 2504869.6657 | 1117446.1671
149 | 2504973.9901 | 1117128.4567 | 2504979.6563 | 1117117.1198
150 | 2504988.253 | 1117100.0156 | 2504987.3497 | 1117101.9101 | 2504984.9891 | 1117106.45 | 2504979.6563 | 1117117.1198
151 | 2504880.2028 | 1117452.2434 | 2504869.6657 | 1117446.1671
152 | 2505032.9579 | 1117012.2614 | 2505041.0646 | 1117017.693 | 2505048.3988 | 1117022.6031 | 2505063.5019 | 1117028.1473 | 2505080.8868 | 1117030.0312 | 2505082.9242 | 1117029.9881 | 2505102.3155 | 1117029.8505
153 | 2505032.9579 | 1117012.2614 | 2505020.2473 | 1117037.1747
154 | 2505102.3155 | 1117029.8505 | 2505103.1219 | 1117040.3999 | 2505085.1486 | 1117086.369
155 | 2505016.8331 | 1117043.8669 | 2505020.2473 | 1117037.1747
156 | 2505085.1486 | 1117086.369 | 2505080.6565 | 1117097.858
157 | 2505005.7729 | 1117065.5454 | 2505016.8331 | 1117043.8669
158 | 2504988.253 | 1117100.0156 | 2504989.2032 | 1117098.0231 | 2504994.4591 | 1117087.7212
159 | 2505000.6916 | 1117075.5051 | 2504994.4591 | 1117087.7212
160 | 2505000.6916 | 1117075.5051 | 2505005.7729 | 1117065.5454
161 | 2504922.8391 | 1117373.1078 | 2504926.1987 | 1117366.2399
162 | 2504922.2018 | 1117374.4108 | 2504922.8391 | 1117373.1078
163 | 2504922.2018 | 1117374.4108 | 2504916.3532 | 1117386.3668
164 | 2504916.3532 | 1117386.3668 | 2504915.6626 | 1117387.7785
165 | 2504906.784 | 1117405.9288 | 2504915.6626 | 1117387.7785
166 | 2505086.7122 | 1117468.0317 | 2505092.3196 | 1117460.2218
167 | 2505073.2376 | 1117485.635 | 2505075.5919 | 1117482.5136 | 2505081.8631 | 1117474.3324 | 2505085.0581 | 1117470.3354 | 2505086.7122 | 1117468.0317
168 | 2505073.2376 | 1117485.635 | 2505070.3814 | 1117489.4218 | 2505059.8574 | 1117502.0725 | 2505053.2278 | 1117510.5373 | 2505052.1614 | 1117511.7513

## bus_geodata
| x | y | coords
0 | 2504733.5576 | 1117083.6264
1 | 2504735.6731 | 1117085.7688
2 | 2504725.242 | 1117075.2054
3 | 2504743.4532 | 1117093.6475
4 | 2504709.6458 | 1117061.297
5 | 2504753.4807 | 1117103.8022
6 | 2504738.3287 | 1117018.786
7 | 2504753.8196 | 1117104.1453
8 | 2504766.4418 | 1117573.3501
9 | 2504776.7367 | 1117574.6221
10 | 2504778.6221 | 1117575.5248
11 | 2504835.2071 | 1117459.227
12 | 2504850.0374 | 1117469.112
13 | 2504828.7563 | 1117454.9272
14 | 2504785.6762 | 1117581.4968
15 | 2504851.3539 | 1117469.9895
16 | 2504821.8115 | 1117450.2982
17 | 2504822.7502 | 1117450.9239
18 | 2504806.9846 | 1117440.4155
19 | 2504826.9339 | 1117606.52
20 | 2505058.7257 | 1117153.5716
21 | 2505059.217 | 1117152.3245
22 | 2505052.1055 | 1117170.3757
23 | 2505059.4392 | 1117151.7606
24 | 2505051.359 | 1117172.2706
25 | 2505066.4178 | 1117134.0468
26 | 2505069.028 | 1117127.4213
27 | 2505071.7645 | 1117120.4754
28 | 2504808.414 | 1117163.9072
29 | 2504767.226 | 1117153.5915
30 | 2504809.8223 | 1117164.1499
31 | 2504800.5144 | 1117150.265
32 | 2504845.1187 | 1117128.5932
33 | 2504842.485 | 1117170.8559
34 | 2504775.5823 | 1117125.8377
35 | 2504851.9073 | 1117121.8647
36 | 2504860.4743 | 1117177.8949
37 | 2504861.4976 | 1117108.4918
38 | 2504884.0317 | 1117185.4625
39 | 2504849.4641 | 1117209.9432
40 | 2504888.4097 | 1117494.6889
41 | 2504882.7855 | 1117490.9401
42 | 2504892.8323 | 1117497.6367
43 | 2504873.9578 | 1117485.0561
44 | 2504900.0576 | 1117502.4527
45 | 2504867.0524 | 1117480.4533
46 | 2504906.6452 | 1117506.8437
47 | 2504854.5761 | 1117472.1373
48 | 2504917.8846 | 1117514.3352
49 | 2504855.5196 | 1117617.6951
50 | 2504951.8324 | 1117313.8376
51 | 2504940.7644 | 1117336.4637
52 | 2504953.0973 | 1117311.2519
53 | 2504937.356 | 1117343.4314
54 | 2504953.3626 | 1117310.7095
55 | 2504934.321 | 1117349.6357
56 | 2504955.1043 | 1117307.1491
57 | 2504934.0661 | 1117350.1568
58 | 2504910.0314 | 1117266.3173
59 | 2505148.0171 | 1117344.5836
60 | 2505142.3015 | 1117363.4838
61 | 2505158.2239 | 1117284.174
62 | 2505129.8176 | 1117394.2296
63 | 2505112.36 | 1117267.7064
64 | 2505126.822 | 1117400.9712
65 | 2505094.0189 | 1117260.7637
66 | 2505111.4112 | 1117430.4543
67 | 2505301.5586 | 1117465.0279
68 | 2505262.6119 | 1117518.0927
69 | 2505092.1486 | 1117260.0539
70 | 2505078.1238 | 1117254.7351
71 | 2505060.6628 | 1117248.1191
72 | 2505081.9293 | 1117256.177
73 | 2505054.6344 | 1117245.8351
74 | 2505052.58 | 1117245.0568
75 | 2505043.5509 | 1117241.6363
76 | 2504841.9053 | 1117320.2727
77 | 2504856.0711 | 1117326.3301
78 | 2504835.6698 | 1117317.6064
79 | 2504884.3214 | 1117338.4102
80 | 2504817.007 | 1117309.626
81 | 2504891.3142 | 1117341.4004
82 | 2504811.7599 | 1117325.5283
83 | 2504819.5477 | 1117301.9289
84 | 2504800.9661 | 1117358.2415
85 | 2504825.4514 | 1117284.0441
86 | 2504905.4198 | 1116951.5162
87 | 2504925.3748 | 1116959.5795
88 | 2504855.0882 | 1116985.4316
89 | 2504852.1825 | 1116982.184
90 | 2504874.8834 | 1117007.555
91 | 2504964.2115 | 1117034.5799
92 | 2504957.6964 | 1117040.2115
93 | 2504980.4707 | 1117020.5255
94 | 2504880.8007 | 1117014.1683
95 | 2505006.9157 | 1116994.9707
96 | 2504884.7711 | 1117397.2721
97 | 2504869.135 | 1117389.9899
98 | 2504891.9011 | 1117400.5928
99 | 2504843.5268 | 1117378.0634
100 | 2504825.5298 | 1117369.6816
101 | 2504822.6419 | 1117368.3366
102 | 2504842.8964 | 1117230.9144
103 | 2504848.1999 | 1117213.98
104 | 2504840.8527 | 1117237.44
105 | 2504838.316 | 1117245.1162
106 | 2504866.8201 | 1117246.8274
107 | 2504833.997 | 1117258.1854
108 | 2504869.8702 | 1117247.93
109 | 2504878.9782 | 1117251.2227
110 | 2504912.0438 | 1117194.8745
111 | 2504899.1967 | 1117155.9628
112 | 2504796.9462 | 1117273.0304
113 | 2504766.5056 | 1117261.2689
114 | 2504965.0136 | 1117212.3739
115 | 2504997.7019 | 1117224.2571
116 | 2504964.4088 | 1117212.1771
117 | 2504999.2851 | 1117224.8573
118 | 2504936.9781 | 1117203.2523
119 | 2505028.7703 | 1117236.0288
120 | 2504955.1683 | 1117166.1152
121 | 2504923.1519 | 1117198.6068
122 | 2504960.4847 | 1117155.4782
123 | 2504909.8778 | 1117136.315
124 | 2504956.2901 | 1117496.1193
125 | 2504954.1822 | 1117494.9038
126 | 2504963.73 | 1117500.4096
127 | 2504944.5765 | 1117489.3647
128 | 2504965.8396 | 1117501.6261
129 | 2504923.7284 | 1117477.3426
130 | 2504914.3113 | 1117471.9122
131 | 2504967.9512 | 1117140.5394
132 | 2504923.3688 | 1117517.9906
133 | 2504930.4598 | 1117522.7172
134 | 2504900.2707 | 1117625.1604
135 | 2504903.9987 | 1117040.0947
136 | 2504908.5292 | 1117045.1581
137 | 2504954.0888 | 1117043.33
138 | 2504883.8601 | 1117252.9875
139 | 2504904.7424 | 1117263.4428
140 | 2504799.1956 | 1117435.2237
141 | 2504779.8267 | 1117422.3135
142 | 2504788.5754 | 1117399.4062
143 | 2504808.0739 | 1117410.6501
144 | 2504827.1668 | 1117453.8678
145 | 2504842.6002 | 1117430.5598
146 | 2504973.9901 | 1117128.4567
147 | 2504979.6563 | 1117117.1198
148 | 2504880.2028 | 1117452.2434
149 | 2504869.6657 | 1117446.1671
150 | 2505032.9579 | 1117012.2614
151 | 2505102.3155 | 1117029.8505
152 | 2505020.2473 | 1117037.1747
153 | 2505085.1486 | 1117086.369
154 | 2505016.8331 | 1117043.8669
155 | 2504988.253 | 1117100.0156
156 | 2504994.4591 | 1117087.7212
157 | 2505000.6916 | 1117075.5051
158 | 2505005.7729 | 1117065.5454
159 | 2504926.1987 | 1117366.2399
160 | 2504922.8391 | 1117373.1078
161 | 2504922.2018 | 1117374.4108
162 | 2504916.3532 | 1117386.3668
163 | 2504915.6626 | 1117387.7785
164 | 2504906.784 | 1117405.9288
165 | 2505092.3196 | 1117460.2218
166 | 2505086.7122 | 1117468.0317
167 | 2505073.2376 | 1117485.635
168 | 2505052.1614 | 1117511.7513
169 | 2505080.6565 | 1117097.858
170 | 2504906.784 | 1117405.9288

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1