## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6642-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6642-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6642-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6642-4_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6642-4_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6642-4_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6642-4_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_6642-4_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_6642-4_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_6642-4_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_6642-4_0_3_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_6642-4_0_3_node_333 | 0.4 | n |  | TRUE
12 | bus_LV_6642-4_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_6642-4_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_6642-4_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_6642-4_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_6642-4_0_3_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_6642-4_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_6642-4_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_6642-4_0_3_node_39 | 0.4 | n |  | TRUE
20 | bus_LV_6642-4_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_6642-4_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_6642-4_0_3_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_6642-4_0_3_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_6642-4_0_3_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_6642-4_0_3_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_6642-4_0_3_node_52 | 0.4 | n |  | TRUE
27 | bus_LV_6642-4_0_3_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_6642-4_0_3_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_6642-4_0_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_6642-4_0_3_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_6642-4_0_3_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_6642-4_0_3_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_6642-4_0_3_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_6642-4_0_3_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_6642-4_0_3_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_6642-4_0_3_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_6642-4_0_3_node_50 | 0.4 | n |  | TRUE
38 | bus_LV_6642-4_0_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_6642-4_0_3_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_6642-4_0_3_node_51 | 0.4 | n |  | TRUE
41 | bus_LV_6642-4_0_3_node_132 | 0.4 | n |  | TRUE
42 | bus_LV_6642-4_0_3_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_6642-4_0_3_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_6642-4_0_3_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_6642-4_0_3_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_6642-4_0_3_node_47 | 0.4 | n |  | TRUE
47 | bus_LV_6642-4_0_3_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_6642-4_0_3_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_6642-4_0_3_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_6642-4_0_3_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_6642-4_0_3_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_6642-4_0_3_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_6642-4_0_3_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_6642-4_0_3_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_6642-4_0_3_node_170 | 0.4 | n |  | TRUE
56 | bus_LV_6642-4_0_3_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_6642-4_0_3_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_6642-4_0_3_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_6642-4_0_3_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_6642-4_0_3_node_57 | 0.4 | n |  | TRUE
61 | bus_LV_6642-4_0_3_node_207 | 0.4 | n |  | TRUE
62 | bus_LV_6642-4_0_3_node_114 | 0.4 | n |  | TRUE
63 | bus_LV_6642-4_0_3_node_115 | 0.4 | n |  | TRUE
64 | bus_LV_6642-4_0_3_node_116 | 0.4 | n |  | TRUE
65 | bus_LV_6642-4_0_3_node_117 | 0.4 | n |  | TRUE
66 | bus_LV_6642-4_0_3_node_118 | 0.4 | n |  | TRUE
67 | bus_LV_6642-4_0_3_node_119 | 0.4 | n |  | TRUE
68 | bus_LV_6642-4_0_3_node_120 | 0.4 | n |  | TRUE
69 | bus_LV_6642-4_0_3_node_121 | 0.4 | n |  | TRUE
70 | bus_LV_6642-4_0_3_node_122 | 0.4 | n |  | TRUE
71 | bus_LV_6642-4_0_3_node_137 | 0.4 | n |  | TRUE
72 | bus_LV_6642-4_0_3_node_136 | 0.4 | n |  | TRUE
73 | bus_LV_6642-4_0_3_node_168 | 0.4 | n |  | TRUE
74 | bus_LV_6642-4_0_3_node_123 | 0.4 | n |  | TRUE
75 | bus_LV_6642-4_0_3_node_124 | 0.4 | n |  | TRUE
76 | bus_LV_6642-4_0_3_node_125 | 0.4 | n |  | TRUE
77 | bus_LV_6642-4_0_3_node_126 | 0.4 | n |  | TRUE
78 | bus_LV_6642-4_0_3_node_127 | 0.4 | n |  | TRUE
79 | bus_LV_6642-4_0_3_node_128 | 0.4 | n |  | TRUE
80 | bus_LV_6642-4_0_3_node_129 | 0.4 | n |  | TRUE
81 | bus_LV_6642-4_0_3_node_162 | 0.4 | n |  | TRUE
82 | bus_LV_6642-4_0_3_node_139 | 0.4 | n |  | TRUE
83 | bus_LV_6642-4_0_3_node_130 | 0.4 | n |  | TRUE
84 | bus_LV_6642-4_0_3_node_131 | 0.4 | n |  | TRUE
85 | bus_LV_6642-4_0_3_node_133 | 0.4 | n |  | TRUE
86 | bus_LV_6642-4_0_3_node_134 | 0.4 | n |  | TRUE
87 | bus_LV_6642-4_0_3_node_135 | 0.4 | n |  | TRUE
88 | bus_LV_6642-4_0_3_node_145 | 0.4 | n |  | TRUE
89 | bus_LV_6642-4_0_3_node_157 | 0.4 | n |  | TRUE
90 | bus_LV_6642-4_0_3_node_140 | 0.4 | n |  | TRUE
91 | bus_LV_6642-4_0_3_node_138 | 0.4 | n |  | TRUE
92 | bus_LV_6642-4_0_3_node_144 | 0.4 | n |  | TRUE
93 | bus_LV_6642-4_0_3_node_156 | 0.4 | n |  | TRUE
94 | bus_LV_6642-4_0_3_node_141 | 0.4 | n |  | TRUE
95 | bus_LV_6642-4_0_3_node_181 | 0.4 | n |  | TRUE
96 | bus_LV_6642-4_0_3_node_142 | 0.4 | n |  | TRUE
97 | bus_LV_6642-4_0_3_node_143 | 0.4 | n |  | TRUE
98 | bus_LV_6642-4_0_3_node_146 | 0.4 | n |  | TRUE
99 | bus_LV_6642-4_0_3_node_147 | 0.4 | n |  | TRUE
100 | bus_LV_6642-4_0_3_node_148 | 0.4 | n |  | TRUE
101 | bus_LV_6642-4_0_3_node_149 | 0.4 | n |  | TRUE
102 | bus_LV_6642-4_0_3_node_150 | 0.4 | n |  | TRUE
103 | bus_LV_6642-4_0_3_node_151 | 0.4 | n |  | TRUE
104 | bus_LV_6642-4_0_3_node_152 | 0.4 | n |  | TRUE
105 | bus_LV_6642-4_0_3_node_153 | 0.4 | n |  | TRUE
106 | bus_LV_6642-4_0_3_node_154 | 0.4 | n |  | TRUE
107 | bus_LV_6642-4_0_3_node_155 | 0.4 | n |  | TRUE
108 | bus_LV_6642-4_0_3_node_160 | 0.4 | n |  | TRUE
109 | bus_LV_6642-4_0_3_node_178 | 0.4 | n |  | TRUE
110 | bus_LV_6642-4_0_3_node_158 | 0.4 | n |  | TRUE
111 | bus_LV_6642-4_0_3_node_159 | 0.4 | n |  | TRUE
112 | bus_LV_6642-4_0_3_node_161 | 0.4 | n |  | TRUE
113 | bus_LV_6642-4_0_3_node_164 | 0.4 | n |  | TRUE
114 | bus_LV_6642-4_0_3_node_163 | 0.4 | n |  | TRUE
115 | bus_LV_6642-4_0_3_node_165 | 0.4 | n |  | TRUE
116 | bus_LV_6642-4_0_3_node_166 | 0.4 | n |  | TRUE
117 | bus_LV_6642-4_0_3_node_167 | 0.4 | n |  | TRUE
118 | bus_LV_6642-4_0_3_node_169 | 0.4 | n |  | TRUE
119 | bus_LV_6642-4_0_3_node_173 | 0.4 | n |  | TRUE
120 | bus_LV_6642-4_0_3_node_336 | 0.4 | n |  | TRUE
121 | bus_LV_6642-4_0_3_node_268 | 0.4 | n |  | TRUE
122 | bus_LV_6642-4_0_3_node_171 | 0.4 | n |  | TRUE
123 | bus_LV_6642-4_0_3_node_172 | 0.4 | n |  | TRUE
124 | bus_LV_6642-4_0_3_node_176 | 0.4 | n |  | TRUE
125 | bus_LV_6642-4_0_3_node_174 | 0.4 | n |  | TRUE
126 | bus_LV_6642-4_0_3_node_184 | 0.4 | n |  | TRUE
127 | bus_LV_6642-4_0_3_node_175 | 0.4 | n |  | TRUE
128 | bus_LV_6642-4_0_3_node_177 | 0.4 | n |  | TRUE
129 | bus_LV_6642-4_0_3_node_179 | 0.4 | n |  | TRUE
130 | bus_LV_6642-4_0_3_node_180 | 0.4 | n |  | TRUE
131 | bus_LV_6642-4_0_3_node_182 | 0.4 | n |  | TRUE
132 | bus_LV_6642-4_0_3_node_183 | 0.4 | n |  | TRUE
133 | bus_LV_6642-4_0_3_node_185 | 0.4 | n |  | TRUE
134 | bus_LV_6642-4_0_3_node_186 | 0.4 | n |  | TRUE
135 | bus_LV_6642-4_0_3_node_187 | 0.4 | n |  | TRUE
136 | bus_LV_6642-4_0_3_node_280 | 0.4 | n |  | TRUE
137 | bus_LV_6642-4_0_3_node_281 | 0.4 | n |  | TRUE
138 | bus_LV_6642-4_0_3_node_211 | 0.4 | n |  | TRUE
139 | bus_LV_6642-4_0_3_node_188 | 0.4 | n |  | TRUE
140 | bus_LV_6642-4_0_3_node_279 | 0.4 | n |  | TRUE
141 | bus_LV_6642-4_0_3_node_208 | 0.4 | n |  | TRUE
142 | bus_LV_6642-4_0_3_node_209 | 0.4 | n |  | TRUE
143 | bus_LV_6642-4_0_3_node_248 | 0.4 | n |  | TRUE
144 | bus_LV_6642-4_0_3_node_210 | 0.4 | n |  | TRUE
145 | bus_LV_6642-4_0_3_node_212 | 0.4 | n |  | TRUE
146 | bus_LV_6642-4_0_3_node_213 | 0.4 | n |  | TRUE
147 | bus_LV_6642-4_0_3_node_214 | 0.4 | n |  | TRUE
148 | bus_LV_6642-4_0_3_node_226 | 0.4 | n |  | TRUE
149 | bus_LV_6642-4_0_3_node_311 | 0.4 | n |  | TRUE
150 | bus_LV_6642-4_0_3_node_223 | 0.4 | n |  | TRUE
151 | bus_LV_6642-4_0_3_node_224 | 0.4 | n |  | TRUE
152 | bus_LV_6642-4_0_3_node_225 | 0.4 | n |  | TRUE
153 | bus_LV_6642-4_0_3_node_227 | 0.4 | n |  | TRUE
154 | bus_LV_6642-4_0_3_node_265 | 0.4 | n |  | TRUE
155 | bus_LV_6642-4_0_3_node_266 | 0.4 | n |  | TRUE
156 | bus_LV_6642-4_0_3_node_267 | 0.4 | n |  | TRUE
157 | bus_LV_6642-4_0_3_node_269 | 0.4 | n |  | TRUE
158 | bus_LV_6642-4_0_3_node_271 | 0.4 | n |  | TRUE
159 | bus_LV_6642-4_0_3_node_350 | 0.4 | n |  | TRUE
160 | bus_LV_6642-4_0_3_node_330 | 0.4 | n |  | TRUE
161 | bus_LV_6642-4_0_3_node_309 | 0.4 | n |  | TRUE
162 | bus_LV_6642-4_0_3_node_310 | 0.4 | n |  | TRUE
163 | bus_LV_6642-4_0_3_node_312 | 0.4 | n |  | TRUE
164 | bus_LV_6642-4_0_3_node_314 | 0.4 | n |  | TRUE
165 | bus_LV_6642-4_0_3_node_328 | 0.4 | n |  | TRUE
166 | bus_LV_6642-4_0_3_node_329 | 0.4 | n |  | TRUE
167 | bus_LV_6642-4_0_3_node_331 | 0.4 | n |  | TRUE
168 | bus_LV_6642-4_0_3_node_332 | 0.4 | n |  | TRUE
169 | bus_LV_6642-4_0_3_node_337 | 0.4 | n |  | TRUE
170 | bus_LV_6642-4_0_3_node_338 | 0.4 | n |  | TRUE
171 | bus_LV_6642-4_0_3_node_339 | 0.4 | n |  | TRUE
172 | bus_MV_459_1_node_100 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6642-4_0_3_load_0 | 0 | 0.00056215 | 0.00014089 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6642-4_0_3_load_1 | 1 | 0.00085523 | 0.00021434 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6642-4_0_3_load_3 | 3 | 0.00028993 | 7.2663e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6642-4_0_3_load_6 | 6 | 0.0010035 | 0.00025149 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6642-4_0_3_load_7 | 7 | 0.0012807 | 0.00032097 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6642-4_0_3_load_8 | 8 | 0.00099856 | 0.00025026 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6642-4_0_3_load_9 | 9 | 0.00027837 | 6.9767e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6642-4_0_3_load_18 | 10 | 0.001467 | 0.00036766 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6642-4_0_3_load_333 | 11 | 0.0020685 | 0.00051843 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6642-4_0_3_load_12 | 12 | 0.0012191 | 0.00030554 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6642-4_0_3_load_10 | 13 | 0.010756 | 0.0026958 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6642-4_0_3_load_13 | 15 | 0.0098724 | 0.0024743 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6642-4_0_3_load_14 | 16 | 0.0025329 | 0.00063479 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6642-4_0_3_load_15 | 17 | 0.0027001 | 0.00067671 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6642-4_0_3_load_16 | 18 | 0.0025576 | 0.00064099 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6642-4_0_3_load_39 | 19 | 0.0049453 | 0.0012394 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6642-4_0_3_load_17 | 20 | 0.00085772 | 0.00021496 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6642-4_0_3_load_20 | 22 | 0.0014871 | 0.0003727 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6642-4_0_3_load_21 | 23 | 0.0014543 | 0.00036447 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6642-4_0_3_load_22 | 24 | 0.0013879 | 0.00034784 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6642-4_0_3_load_23 | 25 | 0.0023213 | 0.00058176 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6642-4_0_3_load_52 | 26 | 0.00049228 | 0.00012338 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6642-4_0_3_load_24 | 27 | 0.0030536 | 0.0007653 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6642-4_0_3_load_25 | 28 | 0.001658 | 0.00041553 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6642-4_0_3_load_27 | 30 | 0.0042667 | 0.0010693 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6642-4_0_3_load_28 | 31 | 0.0015473 | 0.0003878 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6642-4_0_3_load_30 | 33 | 0.0048801 | 0.0012231 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6642-4_0_3_load_31 | 34 | 0.001165 | 0.00029198 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6642-4_0_3_load_33 | 35 | 0.0043034 | 0.0010785 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6642-4_0_3_load_40 | 36 | 0.00049421 | 0.00012386 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6642-4_0_3_load_50 | 37 | 0.00054685 | 0.00013705 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6642-4_0_3_load_51 | 40 | 0.00059626 | 0.00014944 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6642-4_0_3_load_34 | 42 | 0.0024584 | 0.00061612 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6642-4_0_3_load_35 | 43 | 0.00081087 | 0.00020322 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6642-4_0_3_load_36 | 44 | 0.00081087 | 0.00020322 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6642-4_0_3_load_47 | 46 | 0.0096397 | 0.0024159 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6642-4_0_3_load_41 | 48 | 0.00139 | 0.00034837 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6642-4_0_3_load_44 | 50 | 0.011779 | 0.0029521 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6642-4_0_3_load_46 | 52 | 0.0058747 | 0.0014723 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6642-4_0_3_load_48 | 53 | 0.0013106 | 0.00032846 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6642-4_0_3_load_49 | 54 | 0.0025581 | 0.00064112 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6642-4_0_3_load_170 | 55 | 0.00086858 | 0.00021769 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6642-4_0_3_load_53 | 56 | 0.00104 | 0.00026066 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6642-4_0_3_load_54 | 57 | 0.0017387 | 0.00043575 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6642-4_0_3_load_56 | 59 | 0.0014788 | 0.00037063 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6642-4_0_3_load_57 | 60 | 0.0012068 | 0.00030246 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6642-4_0_3_load_207 | 61 | 0.0016537 | 0.00041446 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6642-4_0_3_load_114 | 62 | 0.00035245 | 8.8332e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6642-4_0_3_load_115 | 63 | 0.001375 | 0.00034461 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6642-4_0_3_load_117 | 65 | 0.0015269 | 0.00038267 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6642-4_0_3_load_118 | 66 | 0.00084557 | 0.00021192 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6642-4_0_3_load_121 | 69 | 0.0013006 | 0.00032597 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6642-4_0_3_load_122 | 70 | 0.00076414 | 0.00019151 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6642-4_0_3_load_137 | 71 | 0.0019541 | 0.00048975 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6642-4_0_3_load_136 | 72 | 0.00097807 | 0.00024513 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6642-4_0_3_load_123 | 74 | 0.0010347 | 0.00025931 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6642-4_0_3_load_124 | 75 | 0.00091625 | 0.00022963 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6642-4_0_3_load_125 | 76 | 0.0014725 | 0.00036905 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6642-4_0_3_load_126 | 77 | 0.00065143 | 0.00016326 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6642-4_0_3_load_127 | 78 | 0.002528 | 0.00063358 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6642-4_0_3_load_128 | 79 | 0.00094579 | 0.00023704 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6642-4_0_3_load_129 | 80 | 0.0022683 | 0.00056849 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6642-4_0_3_load_162 | 81 | 0.0011467 | 0.00028738 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6642-4_0_3_load_130 | 83 | 0.00088417 | 0.00022159 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6642-4_0_3_load_131 | 84 | 0.0010347 | 0.00025931 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6642-4_0_3_load_135 | 87 | 0.0020966 | 0.00052546 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6642-4_0_3_load_145 | 88 | 0.0021266 | 0.00053297 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6642-4_0_3_load_157 | 89 | 0.0047854 | 0.0011993 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6642-4_0_3_load_141 | 94 | 0.0020337 | 0.0005097 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6642-4_0_3_load_181 | 95 | 0.0031781 | 0.0007965 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6642-4_0_3_load_142 | 96 | 0.0020281 | 0.00050829 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6642-4_0_3_load_143 | 97 | 0.0013743 | 0.00034443 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6642-4_0_3_load_146 | 98 | 0.0051513 | 0.001291 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6642-4_0_3_load_149 | 101 | 0.0040857 | 0.001024 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6642-4_0_3_load_150 | 102 | 0.00049774 | 0.00012474 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6642-4_0_3_load_151 | 103 | 0.00047625 | 0.00011936 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6642-4_0_3_load_152 | 104 | 0.0016523 | 0.00041412 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6642-4_0_3_load_154 | 106 | 0.00023404 | 5.8657e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6642-4_0_3_load_155 | 107 | 0.00040151 | 0.00010063 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6642-4_0_3_load_160 | 108 | 0.0009968 | 0.00024982 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6642-4_0_3_load_178 | 109 | 0.00045124 | 0.00011309 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6642-4_0_3_load_158 | 110 | 0.001316 | 0.00032982 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6642-4_0_3_load_159 | 111 | 0.00059173 | 0.0001483 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6642-4_0_3_load_161 | 112 | 0.0041362 | 0.0010366 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6642-4_0_3_load_164 | 113 | 0.0049462 | 0.0012396 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6642-4_0_3_load_163 | 114 | 0.0034023 | 0.00085269 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6642-4_0_3_load_166 | 116 | 0.0012753 | 0.00031962 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6642-4_0_3_load_167 | 117 | 0.00097799 | 0.00024511 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_6642-4_0_3_load_173 | 119 | 0.0016213 | 0.00040633 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_6642-4_0_3_load_268 | 121 | 0.0018428 | 0.00046184 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_6642-4_0_3_load_171 | 122 | 0.001312 | 0.00032882 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_6642-4_0_3_load_172 | 123 | 0.00035058 | 8.7864e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_6642-4_0_3_load_176 | 124 | 0.00034836 | 8.7307e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_6642-4_0_3_load_174 | 125 | 0.0014431 | 0.00036168 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_6642-4_0_3_load_184 | 126 | 0.002246 | 0.00056291 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_6642-4_0_3_load_175 | 127 | 0.00039746 | 9.9612e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_6642-4_0_3_load_177 | 128 | 0.00022671 | 5.6819e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_6642-4_0_3_load_179 | 129 | 0.00059052 | 0.000148 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_6642-4_0_3_load_180 | 130 | 0.0016903 | 0.00042363 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_6642-4_0_3_load_182 | 131 | 0.0014672 | 0.00036772 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_6642-4_0_3_load_183 | 132 | 0.0026279 | 0.0006586 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_6642-4_0_3_load_186 | 134 | 0.0022548 | 0.00056511 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_6642-4_0_3_load_187 | 135 | 0.0010902 | 0.00027323 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_6642-4_0_3_load_280 | 136 | 0.0022523 | 0.00056448 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_6642-4_0_3_load_281 | 137 | 0.0014547 | 0.00036457 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_6642-4_0_3_load_211 | 138 | 0.0022751 | 0.00057018 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_6642-4_0_3_load_188 | 139 | 0.0033315 | 0.00083496 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_6642-4_0_3_load_279 | 140 | 0.001969 | 0.00049349 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_6642-4_0_3_load_208 | 141 | 0.0011775 | 0.00029511 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_6642-4_0_3_load_209 | 142 | 0.0017385 | 0.0004357 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_6642-4_0_3_load_248 | 143 | 0.0027632 | 0.00069253 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_6642-4_0_3_load_210 | 144 | 0.0025465 | 0.00063821 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_6642-4_0_3_load_212 | 145 | 0.0013988 | 0.00035057 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_6642-4_0_3_load_213 | 146 | 0.0010549 | 0.00026439 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_6642-4_0_3_load_226 | 148 | 0.001374 | 0.00034435 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_6642-4_0_3_load_223 | 150 | 0.0060577 | 0.0015182 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_6642-4_0_3_load_224 | 151 | 0.0059222 | 0.0014842 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_6642-4_0_3_load_225 | 152 | 0.002751 | 0.00068947 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_6642-4_0_3_load_227 | 153 | 0.005685 | 0.0014248 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_6642-4_0_3_load_265 | 154 | 0.0037888 | 0.00094957 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_6642-4_0_3_load_266 | 155 | 0.0023696 | 0.00059388 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_6642-4_0_3_load_267 | 156 | 0.0025241 | 0.00063259 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_6642-4_0_3_load_271 | 158 | 0.0018358 | 0.0004601 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_6642-4_0_3_load_350 | 159 | 0.0022767 | 0.00057059 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_6642-4_0_3_load_330 | 160 | 0.0018937 | 0.0004746 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_6642-4_0_3_load_309 | 161 | 0.00094007 | 0.0002356 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_6642-4_0_3_load_310 | 162 | 0.0006621 | 0.00016594 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_6642-4_0_3_load_312 | 163 | 0.0010455 | 0.00026203 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_6642-4_0_3_load_314 | 164 | 0.0011272 | 0.00028249 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_6642-4_0_3_load_328 | 165 | 0.00073128 | 0.00018328 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_6642-4_0_3_load_329 | 166 | 0.0051174 | 0.0012825 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_6642-4_0_3_load_331 | 167 | 0.0015932 | 0.00039929 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_6642-4_0_3_load_332 | 168 | 0.0017004 | 0.00042617 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_6642-4_0_3_load_337 | 169 | 0.0011009 | 0.00027591 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_6642-4_0_3_load_338 | 170 | 0.00074597 | 0.00018696 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_6642-4_0_3_load_339 | 171 | 0.0017463 | 0.00043766 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 70 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6642-4_0_3_line_0 |  | 0 | 1 | 0.02232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6642-4_0_3_line_1 |  | 0 | 2 | 0.0080559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6642-4_0_3_line_2 |  | 1 | 3 | 0.015168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6642-4_0_3_line_3 |  | 2 | 4 | 0.003773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_6642-4_0_3_line_4 |  | 2 | 5 | 0.009118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_6642-4_0_3_line_5 |  | 3 | 6 | 0.010679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6642-4_0_3_line_6 |  | 4 | 7 | 0.025318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_6642-4_0_3_line_7 |  | 5 | 8 | 0.009042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6642-4_0_3_line_8 |  | 5 | 9 | 0.02878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_6642-4_0_3_line_9 |  | 6 | 10 | 0.018306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6642-4_0_3_line_10 |  | 7 | 11 | 0.0082185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_6642-4_0_3_line_11 |  | 9 | 12 | 0.018049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6642-4_0_3_line_12 |  | 9 | 13 | 0.021247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_6642-4_0_3_line_13 |  | 10 | 20 | 0.019746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6642-4_0_3_line_14 |  | 11 | 136 | 0.017258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_6642-4_0_3_line_15 |  | 13 | 14 | 0.024591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_6642-4_0_3_line_16 |  | 14 | 15 | 0.0084635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_6642-4_0_3_line_17 |  | 14 | 16 | 0.028492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6642-4_0_3_line_18 |  | 15 | 17 | 0.0014489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_6642-4_0_3_line_19 |  | 16 | 18 | 0.0094817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6642-4_0_3_line_20 |  | 17 | 19 | 0.031593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_6642-4_0_3_line_21 |  | 19 | 36 | 0.01694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_6642-4_0_3_line_22 |  | 20 | 21 | 0.014656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6642-4_0_3_line_23 |  | 21 | 22 | 0.0017262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6642-4_0_3_line_24 |  | 21 | 23 | 0.03015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6642-4_0_3_line_25 |  | 22 | 24 | 0.031816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6642-4_0_3_line_26 |  | 23 | 25 | 1.2571e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6642-4_0_3_line_27 |  | 24 | 26 | 0.017941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6642-4_0_3_line_28 |  | 26 | 56 | 0.008742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6642-4_0_3_line_29 |  | 27 | 28 | 0.0033774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_6642-4_0_3_line_30 |  | 27 | 29 | 0.021773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6642-4_0_3_line_31 |  | 28 | 30 | 0.018386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_6642-4_0_3_line_32 |  | 29 | 31 | 0.014847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6642-4_0_3_line_33 |  | 29 | 32 | 0.036903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6642-4_0_3_line_34 |  | 30 | 33 | 0.030134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_6642-4_0_3_line_35 |  | 31 | 34 | 0.023719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6642-4_0_3_line_36 |  | 32 | 35 | 0.0235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6642-4_0_3_line_37 |  | 33 | 36 | 0.0076327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_6642-4_0_3_line_38 |  | 34 | 37 | 0.025012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6642-4_0_3_line_39 |  | 35 | 41 | 0.012128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6642-4_0_3_line_40 |  | 37 | 40 | 0.022442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6642-4_0_3_line_41 |  | 38 | 39 | 0.040563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6642-4_0_3_line_42 |  | 38 | 40 | 0.012146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6642-4_0_3_line_43 |  | 39 | 45 | 0.023237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6642-4_0_3_line_44 |  | 39 | 43 | 0.020783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6642-4_0_3_line_45 |  | 41 | 84 | 0.013303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6642-4_0_3_line_46 |  | 42 | 43 | 0.006169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6642-4_0_3_line_47 |  | 42 | 44 | 0.013333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6642-4_0_3_line_48 |  | 45 | 46 | 0.039855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6642-4_0_3_line_49 |  | 45 | 47 | 0.030064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6642-4_0_3_line_50 |  | 46 | 55 | 0.058137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6642-4_0_3_line_51 |  | 47 | 50 | 0.047425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6642-4_0_3_line_52 |  | 47 | 48 | 0.009385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6642-4_0_3_line_53 |  | 48 | 49 | 0.015824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6642-4_0_3_line_54 |  | 49 | 51 | 0.004538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6642-4_0_3_line_55 |  | 49 | 52 | 0.032193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6642-4_0_3_line_56 |  | 51 | 53 | 0.040184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6642-4_0_3_line_57 |  | 51 | 54 | 0.051177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6642-4_0_3_line_58 |  | 55 | 122 | 0.0089264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6642-4_0_3_line_59 |  | 56 | 57 | 0.0047406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6642-4_0_3_line_60 |  | 57 | 58 | 0.026666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6642-4_0_3_line_61 |  | 58 | 59 | 0.018117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6642-4_0_3_line_62 |  | 59 | 60 | 0.020511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6642-4_0_3_line_63 |  | 60 | 61 | 0.039029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6642-4_0_3_line_64 |  | 61 | 141 | 0.020097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6642-4_0_3_line_65 |  | 62 | 63 | 0.010227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6642-4_0_3_line_66 |  | 62 | 64 | 0.013584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6642-4_0_3_line_67 |  | 63 | 65 | 0.02744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6642-4_0_3_line_68 |  | 64 | 66 | 0.023233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6642-4_0_3_line_69 |  | 64 | 67 | 0.029025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6642-4_0_3_line_70 |  | 65 | 68 | 0.0055133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6642-4_0_3_line_71 |  | 67 | 69 | 0.0063078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_6642-4_0_3_line_72 |  | 67 | 70 | 0.017998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_6642-4_0_3_line_73 |  | 68 | 71 | 0.030361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6642-4_0_3_line_74 |  | 68 | 72 | 0.016897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6642-4_0_3_line_75 |  | 69 | 73 | 0.026946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_6642-4_0_3_line_76 |  | 71 | 91 | 0.014835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6642-4_0_3_line_77 |  | 73 | 119 | 0.0027069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_6642-4_0_3_line_78 |  | 73 | 116 | 0.03034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_6642-4_0_3_line_79 |  | 74 | 75 | 0.01182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6642-4_0_3_line_80 |  | 74 | 76 | 0.01967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_6642-4_0_3_line_81 |  | 75 | 77 | 0.014185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6642-4_0_3_line_82 |  | 76 | 78 | 0.0066365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6642-4_0_3_line_83 |  | 77 | 79 | 0.0072234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_6642-4_0_3_line_84 |  | 78 | 80 | 0.020247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_6642-4_0_3_line_85 |  | 79 | 81 | 0.019771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6642-4_0_3_line_86 |  | 80 | 82 | 0.010078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6642-4_0_3_line_87 |  | 82 | 90 | 0.004098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_6642-4_0_3_line_88 |  | 82 | 94 | 0.02255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_6642-4_0_3_line_89 |  | 83 | 84 | 0.01207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_6642-4_0_3_line_90 |  | 85 | 86 | 0.004586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_6642-4_0_3_line_91 |  | 85 | 87 | 0.018372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_6642-4_0_3_line_92 |  | 86 | 88 | 0.013096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_6642-4_0_3_line_93 |  | 86 | 89 | 0.026692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_6642-4_0_3_line_94 |  | 87 | 90 | 0.01912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_6642-4_0_3_line_95 |  | 88 | 92 | 0.021277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_6642-4_0_3_line_96 |  | 90 | 95 | 0.060703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_6642-4_0_3_line_97 |  | 91 | 92 | 0.032483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_6642-4_0_3_line_98 |  | 91 | 93 | 0.003364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_6642-4_0_3_line_99 |  | 92 | 97 | 0.015618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_6642-4_0_3_line_100 |  | 93 | 110 | 0.014389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_6642-4_0_3_line_101 |  | 93 | 104 | 0.012623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_6642-4_0_3_line_102 |  | 96 | 97 | 0.033253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_6642-4_0_3_line_103 |  | 98 | 99 | 0.017804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_6642-4_0_3_line_104 |  | 98 | 100 | 0.013256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_6642-4_0_3_line_105 |  | 99 | 101 | 0.028868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_6642-4_0_3_line_106 |  | 99 | 102 | 0.01505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_6642-4_0_3_line_107 |  | 100 | 103 | 0.015343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_6642-4_0_3_line_108 |  | 100 | 104 | 0.015699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_6642-4_0_3_line_109 |  | 101 | 105 | 0.017981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_6642-4_0_3_line_110 |  | 102 | 106 | 0.027321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_6642-4_0_3_line_111 |  | 103 | 107 | 0.028849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_6642-4_0_3_line_112 |  | 105 | 108 | 0.016776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_6642-4_0_3_line_113 |  | 106 | 109 | 0.00032959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_6642-4_0_3_line_114 |  | 108 | 112 | 0.013102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_6642-4_0_3_line_115 |  | 109 | 129 | 0.029747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_6642-4_0_3_line_116 |  | 110 | 111 | 0.030917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_6642-4_0_3_line_117 |  | 112 | 113 | 0.0048657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_6642-4_0_3_line_118 |  | 114 | 115 | 0.013771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_6642-4_0_3_line_119 |  | 115 | 116 | 0.028906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_6642-4_0_3_line_120 |  | 115 | 117 | 0.019114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_6642-4_0_3_line_121 |  | 117 | 118 | 0.023164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_6642-4_0_3_line_122 |  | 118 | 120 | 0.022837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_6642-4_0_3_line_123 |  | 118 | 121 | 0.021089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_6642-4_0_3_line_124 |  | 119 | 125 | 0.041923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_6642-4_0_3_line_125 |  | 120 | 169 | 0.013566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_6642-4_0_3_line_126 |  | 121 | 155 | 0.03931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_6642-4_0_3_line_127 |  | 122 | 123 | 0.011716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_6642-4_0_3_line_128 |  | 123 | 124 | 0.010502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_6642-4_0_3_line_129 |  | 124 | 127 | 0.021306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_6642-4_0_3_line_130 |  | 125 | 126 | 0.012339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
131 | LV_6642-4_0_3_line_131 |  | 126 | 131 | 0.017759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_6642-4_0_3_line_132 |  | 127 | 128 | 0.012696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_6642-4_0_3_line_133 |  | 129 | 130 | 0.031553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_6642-4_0_3_line_134 |  | 131 | 132 | 0.019031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
135 | LV_6642-4_0_3_line_135 |  | 132 | 133 | 0.031451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_6642-4_0_3_line_136 |  | 133 | 134 | 0.038745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_6642-4_0_3_line_137 |  | 133 | 135 | 0.023518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
138 | LV_6642-4_0_3_line_138 |  | 134 | 136 | 0.016143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
139 | LV_6642-4_0_3_line_139 |  | 134 | 137 | 0.013511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_6642-4_0_3_line_140 |  | 135 | 138 | 0.0063191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
141 | LV_6642-4_0_3_line_141 |  | 137 | 160 | 0.0080701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_6642-4_0_3_line_142 |  | 138 | 145 | 0.027174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_6642-4_0_3_line_143 |  | 139 | 140 | 0.00081765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_6642-4_0_3_line_144 |  | 140 | 144 | 0.032096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_6642-4_0_3_line_145 |  | 141 | 142 | 0.035864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_6642-4_0_3_line_146 |  | 141 | 143 | 0.067027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_6642-4_0_3_line_147 |  | 142 | 144 | 0.010376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_6642-4_0_3_line_148 |  | 145 | 146 | 0.013054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_6642-4_0_3_line_149 |  | 146 | 147 | 0.032252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_6642-4_0_3_line_150 |  | 147 | 148 | 0.018324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_6642-4_0_3_line_151 |  | 147 | 149 | 0.010623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_6642-4_0_3_line_152 |  | 148 | 151 | 0.010395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_6642-4_0_3_line_153 |  | 149 | 161 | 0.021241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_6642-4_0_3_line_154 |  | 150 | 151 | 0.022861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_6642-4_0_3_line_155 |  | 150 | 152 | 0.0038731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_6642-4_0_3_line_156 |  | 152 | 153 | 0.00062569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_6642-4_0_3_line_157 |  | 154 | 155 | 0.0020011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_6642-4_0_3_line_158 |  | 154 | 156 | 0.026683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_6642-4_0_3_line_159 |  | 156 | 157 | 0.019435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_6642-4_0_3_line_160 |  | 157 | 158 | 0.022161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_6642-4_0_3_line_161 |  | 158 | 159 | 0.03689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_6642-4_0_3_line_162 |  | 160 | 167 | 0.032079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_6642-4_0_3_line_163 |  | 161 | 162 | 0.030636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_6642-4_0_3_line_164 |  | 162 | 163 | 0.00096446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_6642-4_0_3_line_165 |  | 163 | 164 | 0.00052102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_6642-4_0_3_line_166 |  | 164 | 165 | 0.015801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_6642-4_0_3_line_167 |  | 165 | 166 | 0.0017787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_6642-4_0_3_line_168 |  | 167 | 168 | 0.0051414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_6642-4_0_3_line_169 |  | 169 | 170 | 0.010981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_6642-4_0_3_line_170 |  | 170 | 171 | 0.0046179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6642-4_0_3_trafo_122 | 0.63 MVA 20/0.4 kV | 172 | 70 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2504944.9169 | 1118482.6546 | 2504932.5059 | 1118476.5247 | 2504924.861 | 1118472.86
1 | 2504952.1399 | 1118486.2221 | 2504944.9169 | 1118482.6546
2 | 2504911.1936 | 1118466.2815 | 2504916.3373 | 1118468.7741 | 2504924.861 | 1118472.86
3 | 2504952.1399 | 1118486.2221 | 2504950.3629 | 1118489.552
4 | 2504960.376 | 1118490.184 | 2504952.1399 | 1118486.2221
5 | 2504911.1936 | 1118466.2815 | 2504901.5833 | 1118461.6247
6 | 2504950.3629 | 1118489.552 | 2504938.2086 | 1118511.7614
7 | 2504960.376 | 1118490.184 | 2504961.9556 | 1118486.5792 | 2504966.6944 | 1118488.517
8 | 2504960.376 | 1118490.184 | 2504973.7532 | 1118496.1441 | 2504986.9792 | 1118501.3284
9 | 2504885.0583 | 1118453.7477 | 2504897.9818 | 1118459.8794 | 2504901.5833 | 1118461.6247
10 | 2504938.2086 | 1118511.7614 | 2504934.2631 | 1118518.9709
11 | 2504986.9792 | 1118501.3284 | 2504983.4639 | 1118508.4769 | 2504979.0176 | 1118517.5267
12 | 2504986.9792 | 1118501.3284 | 2504988.3304 | 1118501.852 | 2505002.0185 | 1118506.4843 | 2505007.1791 | 1118507.8858
13 | 2504885.0583 | 1118453.7477 | 2504884.9405 | 1118453.6918 | 2504868.2804 | 1118447.0942 | 2504866.658 | 1118446.5971
14 | 2504925.9781 | 1118534.1098 | 2504934.2631 | 1118518.9709
15 | 2505031.1257 | 1118513.4203 | 2505017.2658 | 1118510.6251 | 2505007.1791 | 1118507.8858
16 | 2505031.1257 | 1118513.4203 | 2505037.5445 | 1118514.7092 | 2505039.4327 | 1118515.038
17 | 2505031.1257 | 1118513.4203 | 2505016.7796 | 1118538.0374
18 | 2505040.86 | 1118515.2866 | 2505039.4327 | 1118515.038
19 | 2505012.0055 | 1118546.2295 | 2505016.7796 | 1118538.0374
20 | 2505040.86 | 1118515.2866 | 2505053.3565 | 1118517.4627 | 2505072.107 | 1118519.8998
21 | 2505088.9052 | 1118522.0831 | 2505072.107 | 1118519.8998
22 | 2504852.6445 | 1118442.3039 | 2504866.658 | 1118446.5971
23 | 2504852.6445 | 1118442.3039 | 2504850.9896 | 1118441.8129
24 | 2504852.6445 | 1118442.3039 | 2504839.3367 | 1118469.3583
25 | 2504850.9896 | 1118441.8129 | 2504845.4559 | 1118440.1712 | 2504819.8462 | 1118435.4326
26 | 2504839.3312 | 1118469.3695 | 2504839.3367 | 1118469.3583
27 | 2504802.2048 | 1118432.1684 | 2504819.8462 | 1118435.4326
28 | 2504793.6087 | 1118430.5779 | 2504802.2048 | 1118432.1684
29 | 2505144.5273 | 1118529.742 | 2505147.5441 | 1118530.2373 | 2505147.8564 | 1118530.3078
30 | 2505168.9697 | 1118535.6046 | 2505157.9856 | 1118532.5972 | 2505147.8564 | 1118530.3078
31 | 2505144.5273 | 1118529.742 | 2505131.9668 | 1118527.68 | 2505126.3571 | 1118526.9509
32 | 2505168.9697 | 1118535.6046 | 2505172.6709 | 1118528.9759 | 2505176.383 | 1118527.9615 | 2505179.7518 | 1118528.4679
33 | 2505168.9697 | 1118535.6046 | 2505184.6495 | 1118540.762 | 2505202.9101 | 1118550.0481
34 | 2505126.3571 | 1118526.9509 | 2505096.4743 | 1118523.0669
35 | 2505179.7518 | 1118528.4679 | 2505185.7598 | 1118529.3709 | 2505196.0496 | 1118531.9112 | 2505202.6612 | 1118534.1756 | 2505202.7115 | 1118534.201
36 | 2505202.9101 | 1118550.0481 | 2505191.59 | 1118570.6416
37 | 2505088.9052 | 1118522.0831 | 2505096.4743 | 1118523.0669
38 | 2505202.7115 | 1118534.201 | 2505208.1772 | 1118536.9576 | 2505215.6627 | 1118542.288 | 2505222.792 | 1118548.8672
39 | 2505185.7479 | 1118581.2695 | 2505191.59 | 1118570.6416
40 | 2505222.792 | 1118548.8672 | 2505224.1209 | 1118550.0935 | 2505238.8527 | 1118564.5408
41 | 2505238.3754 | 1118574.1293 | 2505250.168 | 1118584.4064 | 2505257.838 | 1118591.6685 | 2505266.829 | 1118600.4775 | 2505268.1228 | 1118601.7692
42 | 2505238.3754 | 1118574.1293 | 2505242.2758 | 1118567.8978 | 2505238.8527 | 1118564.5408
43 | 2505284.6869 | 1118618.0642 | 2505275.8232 | 1118609.4977 | 2505268.1228 | 1118601.7692
44 | 2505268.1228 | 1118601.7692 | 2505276.7781 | 1118592.1166 | 2505281.6725 | 1118586.02
45 | 2505185.7479 | 1118581.2695 | 2505197.4467 | 1118587.6018
46 | 2505281.6725 | 1118586.02 | 2505285.5344 | 1118581.2094
47 | 2505288.9635 | 1118568.8449 | 2505288.1945 | 1118577.8958 | 2505285.5344 | 1118581.2094
48 | 2505284.6869 | 1118618.0642 | 2505263.4568 | 1118651.7943
49 | 2505307.4857 | 1118637.7081 | 2505300.1328 | 1118631.9642 | 2505293.3071 | 1118625.8784 | 2505285.1963 | 1118618.5565 | 2505284.6869 | 1118618.0642
50 | 2505231.6078 | 1118700.4166 | 2505246.3177 | 1118679.0246 | 2505263.4568 | 1118651.7943
51 | 2505307.4857 | 1118637.7081 | 2505281.0138 | 1118677.0573
52 | 2505307.4857 | 1118637.7081 | 2505315.325 | 1118642.868
53 | 2505328.6249 | 1118651.4412 | 2505317.7643 | 1118644.4736 | 2505315.325 | 1118642.868
54 | 2505328.6249 | 1118651.4412 | 2505332.5509 | 1118653.7367
55 | 2505328.6249 | 1118651.4412 | 2505313.2497 | 1118679.7248
56 | 2505332.5509 | 1118653.7367 | 2505340.574 | 1118657.9248 | 2505368.7827 | 1118671.0999
57 | 2505332.5509 | 1118653.7367 | 2505343.2472 | 1118633.4569 | 2505354.5316 | 1118618.6824 | 2505360.0247 | 1118610.7382
58 | 2505226.5501 | 1118707.7719 | 2505231.6078 | 1118700.4166
59 | 2504793.6087 | 1118430.5779 | 2504788.9473 | 1118429.7154
60 | 2504762.7268 | 1118424.8638 | 2504788.9473 | 1118429.7154
61 | 2504762.7268 | 1118424.8638 | 2504755.2146 | 1118441.3496
62 | 2504750.7733 | 1118459.4109 | 2504748.2756 | 1118456.5774 | 2504755.2146 | 1118441.3496
63 | 2504778.4562 | 1118486.8516 | 2504760.0877 | 1118469.9774 | 2504750.7733 | 1118459.4109
64 | 2504778.4562 | 1118486.8516 | 2504789.4413 | 1118496.9429 | 2504793.5347 | 1118500.1174
65 | 2505051.4292 | 1118641.9153 | 2505060.4657 | 1118646.7052
66 | 2505039.4274 | 1118635.5536 | 2505051.4292 | 1118641.9153
67 | 2505060.4657 | 1118646.7052 | 2505084.71 | 1118659.5562
68 | 2505039.4274 | 1118635.5536 | 2505050.6923 | 1118615.2341
69 | 2505013.7275 | 1118621.9266 | 2505039.4274 | 1118635.5536
70 | 2505089.5813 | 1118662.1383 | 2505084.71 | 1118659.5562
71 | 2505013.7275 | 1118621.9266 | 2505010.6355 | 1118627.4246
72 | 2505013.7275 | 1118621.9266 | 2505022.3355 | 1118606.1208
73 | 2505089.5813 | 1118662.1383 | 2505116.4074 | 1118676.3554
74 | 2505089.5813 | 1118662.1383 | 2505081.3213 | 1118676.8782
75 | 2504997.4266 | 1118650.9114 | 2505010.6355 | 1118627.4246
76 | 2505129.5157 | 1118683.3025 | 2505116.4074 | 1118676.3554
77 | 2504997.4266 | 1118650.9114 | 2504995.2095 | 1118649.3585
78 | 2504997.4266 | 1118650.9114 | 2505011.4413 | 1118666.0339 | 2505017.4538 | 1118673.6739
79 | 2505077.7205 | 1118573.8989 | 2505067.3315 | 1118568.2622
80 | 2505077.7205 | 1118573.8989 | 2505095.0093 | 1118583.2792
81 | 2505067.3315 | 1118568.2622 | 2505054.863 | 1118561.4972
82 | 2505100.8424 | 1118586.4441 | 2505095.0093 | 1118583.2792
83 | 2505048.514 | 1118558.0525 | 2505054.863 | 1118561.4972
84 | 2505100.8424 | 1118586.4441 | 2505118.6392 | 1118596.1
85 | 2505048.514 | 1118558.0525 | 2505048.514 | 1118558.0525 | 2505039.058 | 1118575.4153
86 | 2505127.4971 | 1118600.906 | 2505118.6392 | 1118596.1
87 | 2505131.1091 | 1118602.8617 | 2505127.4971 | 1118600.906
88 | 2505127.4971 | 1118600.906 | 2505124.3324 | 1118610.2391 | 2505118.3459 | 1118621.4336
89 | 2505197.4467 | 1118587.6018 | 2505208.0617 | 1118593.3474
90 | 2505164.0612 | 1118620.7447 | 2505161.8396 | 1118624.7598
91 | 2505164.0612 | 1118620.7447 | 2505147.914 | 1118611.9817
92 | 2505161.8396 | 1118624.7598 | 2505155.509 | 1118636.2238
93 | 2505161.8396 | 1118624.7598 | 2505184.9995 | 1118638.0297
94 | 2505131.1091 | 1118602.8617 | 2505147.914 | 1118611.9817
95 | 2505145.2235 | 1118654.8499 | 2505155.509 | 1118636.2238
96 | 2505131.1091 | 1118602.8617 | 2505146.9731 | 1118570.0928 | 2505136.0574 | 1118563.0819 | 2505140.1982 | 1118552.4994
97 | 2505129.5157 | 1118683.3025 | 2505145.2235 | 1118654.8499
98 | 2505129.5157 | 1118683.3025 | 2505127.817 | 1118686.2087
99 | 2505145.2235 | 1118654.8499 | 2505158.8117 | 1118662.5503
100 | 2505127.817 | 1118686.2087 | 2505140.39 | 1118693.2058
101 | 2505127.817 | 1118686.2087 | 2505121.4382 | 1118697.1014
102 | 2505187.7425 | 1118678.9454 | 2505158.8117 | 1118662.5503
103 | 2505097.8182 | 1118737.4551 | 2505106.8103 | 1118722.0888
104 | 2505113.5052 | 1118710.6482 | 2505106.8103 | 1118722.0888
105 | 2505097.8182 | 1118737.4551 | 2505083.2333 | 1118762.3673
106 | 2505097.8182 | 1118737.4551 | 2505110.9993 | 1118744.7192
107 | 2505113.5052 | 1118710.6482 | 2505126.7155 | 1118718.4526
108 | 2505113.5052 | 1118710.6482 | 2505121.4382 | 1118697.1014
109 | 2505074.1487 | 1118777.8846 | 2505083.2333 | 1118762.3673
110 | 2505134.9272 | 1118757.9058 | 2505110.9993 | 1118744.7192
111 | 2505126.7155 | 1118718.4526 | 2505151.5537 | 1118733.1268
112 | 2505074.1487 | 1118777.8846 | 2505068.4843 | 1118771.0471 | 2505063.777 | 1118764.706
113 | 2505135.2159 | 1118758.0649 | 2505134.9272 | 1118757.9058
114 | 2505063.777 | 1118764.706 | 2505060.8369 | 1118759.8269 | 2505057.2467 | 1118753.3497
115 | 2505131.3925 | 1118780.2657 | 2505142.6002 | 1118762.1344 | 2505135.2159 | 1118758.0649
116 | 2505140.39 | 1118693.2058 | 2505167.4053 | 1118708.2402
117 | 2505054.8878 | 1118749.094 | 2505057.2467 | 1118753.3497
118 | 2505031.6908 | 1118698.7471 | 2505037.2892 | 1118711.3287
119 | 2505031.6908 | 1118698.7471 | 2505024.8876 | 1118684.7676 | 2505018.4505 | 1118674.9404 | 2505017.4538 | 1118673.6739
120 | 2505031.6908 | 1118698.7471 | 2505014.4427 | 1118706.9852
121 | 2504993.5406 | 1118716.9685 | 2505014.4427 | 1118706.9852
122 | 2504980.4418 | 1118698.2405 | 2504993.5406 | 1118716.9685
123 | 2504993.5406 | 1118716.9685 | 2504995.589 | 1118723.5514 | 2504996.8468 | 1118729.4242 | 2504997.5916 | 1118735.0715 | 2504997.5261 | 1118737.5632
124 | 2504995.2095 | 1118649.3585 | 2504960.8718 | 1118625.3076
125 | 2504980.4418 | 1118698.2405 | 2504971.0421 | 1118708.0229
126 | 2504997.5261 | 1118737.5632 | 2504997.4805 | 1118739.298 | 2504996.882 | 1118743.9436 | 2504995.8101 | 1118748.4187 | 2504994.1257 | 1118753.704 | 2504991.3078 | 1118759.5518 | 2504982.885 | 1118773.4489
127 | 2505219.9117 | 1118717.4257 | 2505226.5501 | 1118707.7719
128 | 2505219.9117 | 1118717.4257 | 2505213.9614 | 1118726.079
129 | 2505213.9614 | 1118726.079 | 2505208.5645 | 1118733.9275 | 2505201.8851 | 1118743.6323
130 | 2504950.7652 | 1118618.2287 | 2504960.8718 | 1118625.3076
131 | 2504950.7652 | 1118618.2287 | 2504936.2195 | 1118608.0406
132 | 2505194.6871 | 1118754.0906 | 2505201.8851 | 1118743.6323
133 | 2505131.3925 | 1118780.2657 | 2505158.1679 | 1118797.0783
134 | 2504920.6319 | 1118597.1227 | 2504936.2195 | 1118608.0406
135 | 2504894.8709 | 1118579.0791 | 2504920.6319 | 1118597.1227
136 | 2504894.8709 | 1118579.0791 | 2504899.2577 | 1118574.8409 | 2504916.1726 | 1118552.0276 | 2504918.2283 | 1118548.2708
137 | 2504894.8709 | 1118579.0791 | 2504874.4369 | 1118590.7218
138 | 2504918.2283 | 1118548.2708 | 2504925.9781 | 1118534.1098
139 | 2504918.2283 | 1118548.2708 | 2504906.284 | 1118541.9566
140 | 2504868.9465 | 1118593.85 | 2504874.4369 | 1118590.7218
141 | 2504906.284 | 1118541.9566 | 2504899.1495 | 1118538.185
142 | 2504868.9465 | 1118593.85 | 2504864.6697 | 1118596.2868 | 2504847.7578 | 1118610.7484
143 | 2504855.4018 | 1118548.1702 | 2504856.0456 | 1118548.6743
144 | 2504855.4018 | 1118548.1702 | 2504845.701 | 1118540.5733 | 2504830.0748 | 1118528.4549
145 | 2504793.5347 | 1118500.1174 | 2504821.8752 | 1118522.096
146 | 2504793.5347 | 1118500.1174 | 2504745.7897 | 1118547.1609
147 | 2504830.0748 | 1118528.4549 | 2504821.8752 | 1118522.096
148 | 2504837.8362 | 1118619.2326 | 2504847.7578 | 1118610.7484
149 | 2504815.1729 | 1118641.9268 | 2504816.3327 | 1118639.6071 | 2504819.8729 | 1118635.5267 | 2504833.0793 | 1118623.3003 | 2504837.8362 | 1118619.2326
150 | 2504815.1729 | 1118641.9268 | 2504798.5876 | 1118634.1368
151 | 2504811.8421 | 1118651.952 | 2504812.5319 | 1118648.2166 | 2504814.4622 | 1118643.361 | 2504815.1729 | 1118641.9268
152 | 2504798.5876 | 1118634.1368 | 2504789.1784 | 1118629.7173 | 2504789.1784 | 1118629.7173
153 | 2504811.8421 | 1118651.952 | 2504827.9225 | 1118665.8295
154 | 2504774.623 | 1118647.3464 | 2504789.1784 | 1118629.7173
155 | 2504774.623 | 1118647.3464 | 2504772.157 | 1118650.3331
156 | 2504771.7587 | 1118650.8155 | 2504772.157 | 1118650.3331
157 | 2504981.8478 | 1118775.1602 | 2504982.885 | 1118773.4489
158 | 2504981.8478 | 1118775.1602 | 2504968.1973 | 1118797.6827 | 2504968.0013 | 1118797.9692
159 | 2504957.0313 | 1118814.0125 | 2504968.0013 | 1118797.9692
160 | 2504957.0313 | 1118814.0125 | 2504942.8338 | 1118806.3976 | 2504938.2191 | 1118802.4851
161 | 2504910.0815 | 1118778.6288 | 2504938.2191 | 1118802.4851
162 | 2504899.1495 | 1118538.185 | 2504882.5894 | 1118529.4307 | 2504887.9749 | 1118517.2184
163 | 2504827.9225 | 1118665.8295 | 2504851.1159 | 1118685.8457
164 | 2504851.8461 | 1118686.4758 | 2504851.1159 | 1118685.8457
165 | 2504852.2405 | 1118686.8162 | 2504851.8461 | 1118686.4758
166 | 2504864.2031 | 1118697.14 | 2504852.2405 | 1118686.8162
167 | 2504865.5497 | 1118698.3021 | 2504864.2031 | 1118697.14
168 | 2504890.0494 | 1118512.5141 | 2504887.9749 | 1118517.2184
169 | 2504971.0421 | 1118708.0229 | 2504963.4339 | 1118715.941
170 | 2504960.2343 | 1118719.2709 | 2504963.4339 | 1118715.941

## bus_geodata
| x | y | coords
0 | 2504944.9169 | 1118482.6546
1 | 2504924.861 | 1118472.86
2 | 2504952.1399 | 1118486.2221
3 | 2504911.1936 | 1118466.2815
4 | 2504950.3629 | 1118489.552
5 | 2504960.376 | 1118490.184
6 | 2504901.5833 | 1118461.6247
7 | 2504938.2086 | 1118511.7614
8 | 2504966.6944 | 1118488.517
9 | 2504986.9792 | 1118501.3284
10 | 2504885.0583 | 1118453.7477
11 | 2504934.2631 | 1118518.9709
12 | 2504979.0176 | 1118517.5267
13 | 2505007.1791 | 1118507.8858
14 | 2505031.1257 | 1118513.4203
15 | 2505039.4327 | 1118515.038
16 | 2505016.7796 | 1118538.0374
17 | 2505040.86 | 1118515.2866
18 | 2505012.0055 | 1118546.2295
19 | 2505072.107 | 1118519.8998
20 | 2504866.658 | 1118446.5971
21 | 2504852.6445 | 1118442.3039
22 | 2504850.9896 | 1118441.8129
23 | 2504839.3367 | 1118469.3583
24 | 2504819.8462 | 1118435.4326
25 | 2504839.3312 | 1118469.3695
26 | 2504802.2048 | 1118432.1684
27 | 2505147.8564 | 1118530.3078
28 | 2505144.5273 | 1118529.742
29 | 2505168.9697 | 1118535.6046
30 | 2505126.3571 | 1118526.9509
31 | 2505179.7518 | 1118528.4679
32 | 2505202.9101 | 1118550.0481
33 | 2505096.4743 | 1118523.0669
34 | 2505202.7115 | 1118534.201
35 | 2505191.59 | 1118570.6416
36 | 2505088.9052 | 1118522.0831
37 | 2505222.792 | 1118548.8672
38 | 2505238.3754 | 1118574.1293
39 | 2505268.1228 | 1118601.7692
40 | 2505238.8527 | 1118564.5408
41 | 2505185.7479 | 1118581.2695
42 | 2505285.5344 | 1118581.2094
43 | 2505281.6725 | 1118586.02
44 | 2505288.9635 | 1118568.8449
45 | 2505284.6869 | 1118618.0642
46 | 2505263.4568 | 1118651.7943
47 | 2505307.4857 | 1118637.7081
48 | 2505315.325 | 1118642.868
49 | 2505328.6249 | 1118651.4412
50 | 2505281.0138 | 1118677.0573
51 | 2505332.5509 | 1118653.7367
52 | 2505313.2497 | 1118679.7248
53 | 2505368.7827 | 1118671.0999
54 | 2505360.0247 | 1118610.7382
55 | 2505231.6078 | 1118700.4166
56 | 2504793.6087 | 1118430.5779
57 | 2504788.9473 | 1118429.7154
58 | 2504762.7268 | 1118424.8638
59 | 2504755.2146 | 1118441.3496
60 | 2504750.7733 | 1118459.4109
61 | 2504778.4562 | 1118486.8516
62 | 2505051.4292 | 1118641.9153
63 | 2505060.4657 | 1118646.7052
64 | 2505039.4274 | 1118635.5536
65 | 2505084.71 | 1118659.5562
66 | 2505050.6923 | 1118615.2341
67 | 2505013.7275 | 1118621.9266
68 | 2505089.5813 | 1118662.1383
69 | 2505010.6355 | 1118627.4246
70 | 2505022.3355 | 1118606.1208
71 | 2505116.4074 | 1118676.3554
72 | 2505081.3213 | 1118676.8782
73 | 2504997.4266 | 1118650.9114
74 | 2505077.7205 | 1118573.8989
75 | 2505067.3315 | 1118568.2622
76 | 2505095.0093 | 1118583.2792
77 | 2505054.863 | 1118561.4972
78 | 2505100.8424 | 1118586.4441
79 | 2505048.514 | 1118558.0525
80 | 2505118.6392 | 1118596.1
81 | 2505039.058 | 1118575.4153
82 | 2505127.4971 | 1118600.906
83 | 2505208.0617 | 1118593.3474
84 | 2505197.4467 | 1118587.6018
85 | 2505164.0612 | 1118620.7447
86 | 2505161.8396 | 1118624.7598
87 | 2505147.914 | 1118611.9817
88 | 2505155.509 | 1118636.2238
89 | 2505184.9995 | 1118638.0297
90 | 2505131.1091 | 1118602.8617
91 | 2505129.5157 | 1118683.3025
92 | 2505145.2235 | 1118654.8499
93 | 2505127.817 | 1118686.2087
94 | 2505118.3459 | 1118621.4336
95 | 2505140.1982 | 1118552.4994
96 | 2505187.7425 | 1118678.9454
97 | 2505158.8117 | 1118662.5503
98 | 2505106.8103 | 1118722.0888
99 | 2505097.8182 | 1118737.4551
100 | 2505113.5052 | 1118710.6482
101 | 2505083.2333 | 1118762.3673
102 | 2505110.9993 | 1118744.7192
103 | 2505126.7155 | 1118718.4526
104 | 2505121.4382 | 1118697.1014
105 | 2505074.1487 | 1118777.8846
106 | 2505134.9272 | 1118757.9058
107 | 2505151.5537 | 1118733.1268
108 | 2505063.777 | 1118764.706
109 | 2505135.2159 | 1118758.0649
110 | 2505140.39 | 1118693.2058
111 | 2505167.4053 | 1118708.2402
112 | 2505057.2467 | 1118753.3497
113 | 2505054.8878 | 1118749.094
114 | 2505037.2892 | 1118711.3287
115 | 2505031.6908 | 1118698.7471
116 | 2505017.4538 | 1118673.6739
117 | 2505014.4427 | 1118706.9852
118 | 2504993.5406 | 1118716.9685
119 | 2504995.2095 | 1118649.3585
120 | 2504980.4418 | 1118698.2405
121 | 2504997.5261 | 1118737.5632
122 | 2505226.5501 | 1118707.7719
123 | 2505219.9117 | 1118717.4257
124 | 2505213.9614 | 1118726.079
125 | 2504960.8718 | 1118625.3076
126 | 2504950.7652 | 1118618.2287
127 | 2505201.8851 | 1118743.6323
128 | 2505194.6871 | 1118754.0906
129 | 2505131.3925 | 1118780.2657
130 | 2505158.1679 | 1118797.0783
131 | 2504936.2195 | 1118608.0406
132 | 2504920.6319 | 1118597.1227
133 | 2504894.8709 | 1118579.0791
134 | 2504918.2283 | 1118548.2708
135 | 2504874.4369 | 1118590.7218
136 | 2504925.9781 | 1118534.1098
137 | 2504906.284 | 1118541.9566
138 | 2504868.9465 | 1118593.85
139 | 2504856.0456 | 1118548.6743
140 | 2504855.4018 | 1118548.1702
141 | 2504793.5347 | 1118500.1174
142 | 2504821.8752 | 1118522.096
143 | 2504745.7897 | 1118547.1609
144 | 2504830.0748 | 1118528.4549
145 | 2504847.7578 | 1118610.7484
146 | 2504837.8362 | 1118619.2326
147 | 2504815.1729 | 1118641.9268
148 | 2504798.5876 | 1118634.1368
149 | 2504811.8421 | 1118651.952
150 | 2504774.623 | 1118647.3464
151 | 2504789.1784 | 1118629.7173
152 | 2504772.157 | 1118650.3331
153 | 2504771.7587 | 1118650.8155
154 | 2504981.8478 | 1118775.1602
155 | 2504982.885 | 1118773.4489
156 | 2504968.0013 | 1118797.9692
157 | 2504957.0313 | 1118814.0125
158 | 2504938.2191 | 1118802.4851
159 | 2504910.0815 | 1118778.6288
160 | 2504899.1495 | 1118538.185
161 | 2504827.9225 | 1118665.8295
162 | 2504851.1159 | 1118685.8457
163 | 2504851.8461 | 1118686.4758
164 | 2504852.2405 | 1118686.8162
165 | 2504864.2031 | 1118697.14
166 | 2504865.5497 | 1118698.3021
167 | 2504887.9749 | 1118517.2184
168 | 2504890.0494 | 1118512.5142
169 | 2504971.0421 | 1118708.0229
170 | 2504963.4339 | 1118715.941
171 | 2504960.2343 | 1118719.2709
172 | 2505013.7275 | 1118621.9266

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1