## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6644-4_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6644-4_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6644-4_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6644-4_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6644-4_0_5_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_6644-4_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_6644-4_0_5_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_6644-4_0_5_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_6644-4_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_6644-4_0_5_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_6644-4_0_5_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_6644-4_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_6644-4_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_6644-4_0_5_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_6644-4_0_5_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_6644-4_0_5_node_51 | 0.4 | n |  | TRUE
16 | bus_LV_6644-4_0_5_node_47 | 0.4 | n |  | TRUE
17 | bus_LV_6644-4_0_5_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_6644-4_0_5_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_6644-4_0_5_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_6644-4_0_5_node_61 | 0.4 | n |  | TRUE
21 | bus_LV_6644-4_0_5_node_53 | 0.4 | n |  | TRUE
22 | bus_LV_6644-4_0_5_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_6644-4_0_5_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_6644-4_0_5_node_49 | 0.4 | n |  | TRUE
25 | bus_LV_6644-4_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_6644-4_0_5_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_6644-4_0_5_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_6644-4_0_5_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_6644-4_0_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_6644-4_0_5_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_6644-4_0_5_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_6644-4_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_6644-4_0_5_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_6644-4_0_5_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_6644-4_0_5_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_6644-4_0_5_node_153 | 0.4 | n |  | TRUE
37 | bus_LV_6644-4_0_5_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_6644-4_0_5_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_6644-4_0_5_node_156 | 0.4 | n |  | TRUE
40 | bus_LV_6644-4_0_5_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_6644-4_0_5_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_6644-4_0_5_node_62 | 0.4 | n |  | TRUE
43 | bus_LV_6644-4_0_5_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_6644-4_0_5_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_6644-4_0_5_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_6644-4_0_5_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_6644-4_0_5_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_6644-4_0_5_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_6644-4_0_5_node_73 | 0.4 | n |  | TRUE
50 | bus_LV_6644-4_0_5_node_74 | 0.4 | n |  | TRUE
51 | bus_LV_6644-4_0_5_node_63 | 0.4 | n |  | TRUE
52 | bus_LV_6644-4_0_5_node_152 | 0.4 | n |  | TRUE
53 | bus_LV_6644-4_0_5_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_6644-4_0_5_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_6644-4_0_5_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_6644-4_0_5_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_6644-4_0_5_node_76 | 0.4 | n |  | TRUE
58 | bus_LV_6644-4_0_5_node_77 | 0.4 | n |  | TRUE
59 | bus_LV_6644-4_0_5_node_75 | 0.4 | n |  | TRUE
60 | bus_LV_6644-4_0_5_node_139 | 0.4 | n |  | TRUE
61 | bus_LV_6644-4_0_5_node_138 | 0.4 | n |  | TRUE
62 | bus_LV_6644-4_0_5_node_80 | 0.4 | n |  | TRUE
63 | bus_LV_6644-4_0_5_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_6644-4_0_5_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_6644-4_0_5_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_6644-4_0_5_node_78 | 0.4 | n |  | TRUE
67 | bus_LV_6644-4_0_5_node_50 | 0.4 | n |  | TRUE
68 | bus_LV_6644-4_0_5_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_6644-4_0_5_node_64 | 0.4 | n |  | TRUE
70 | bus_LV_6644-4_0_5_node_54 | 0.4 | n |  | TRUE
71 | bus_LV_6644-4_0_5_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_6644-4_0_5_node_55 | 0.4 | n |  | TRUE
73 | bus_LV_6644-4_0_5_node_159 | 0.4 | n |  | TRUE
74 | bus_LV_6644-4_0_5_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_6644-4_0_5_node_110 | 0.4 | n |  | TRUE
76 | bus_LV_6644-4_0_5_node_120 | 0.4 | n |  | TRUE
77 | bus_LV_6644-4_0_5_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_6644-4_0_5_node_123 | 0.4 | n |  | TRUE
79 | bus_LV_6644-4_0_5_node_58 | 0.4 | n |  | TRUE
80 | bus_LV_6644-4_0_5_node_59 | 0.4 | n |  | TRUE
81 | bus_LV_6644-4_0_5_node_124 | 0.4 | n |  | TRUE
82 | bus_LV_6644-4_0_5_node_133 | 0.4 | n |  | TRUE
83 | bus_LV_6644-4_0_5_node_88 | 0.4 | n |  | TRUE
84 | bus_LV_6644-4_0_5_node_83 | 0.4 | n |  | TRUE
85 | bus_LV_6644-4_0_5_node_105 | 0.4 | n |  | TRUE
86 | bus_LV_6644-4_0_5_node_115 | 0.4 | n |  | TRUE
87 | bus_LV_6644-4_0_5_node_85 | 0.4 | n |  | TRUE
88 | bus_LV_6644-4_0_5_node_119 | 0.4 | n |  | TRUE
89 | bus_LV_6644-4_0_5_node_117 | 0.4 | n |  | TRUE
90 | bus_LV_6644-4_0_5_node_131 | 0.4 | n |  | TRUE
91 | bus_LV_6644-4_0_5_node_128 | 0.4 | n |  | TRUE
92 | bus_LV_6644-4_0_5_node_125 | 0.4 | n |  | TRUE
93 | bus_LV_6644-4_0_5_node_160 | 0.4 | n |  | TRUE
94 | bus_LV_6644-4_0_5_node_161 | 0.4 | n |  | TRUE
95 | bus_LV_6644-4_0_5_node_126 | 0.4 | n |  | TRUE
96 | bus_LV_6644-4_0_5_node_114 | 0.4 | n |  | TRUE
97 | bus_LV_6644-4_0_5_node_132 | 0.4 | n |  | TRUE
98 | bus_LV_6644-4_0_5_node_82 | 0.4 | n |  | TRUE
99 | bus_LV_6644-4_0_5_node_116 | 0.4 | n |  | TRUE
100 | bus_LV_6644-4_0_5_node_65 | 0.4 | n |  | TRUE
101 | bus_LV_6644-4_0_5_node_66 | 0.4 | n |  | TRUE
102 | bus_LV_6644-4_0_5_node_67 | 0.4 | n |  | TRUE
103 | bus_LV_6644-4_0_5_node_68 | 0.4 | n |  | TRUE
104 | bus_LV_6644-4_0_5_node_69 | 0.4 | n |  | TRUE
105 | bus_LV_6644-4_0_5_node_70 | 0.4 | n |  | TRUE
106 | bus_LV_6644-4_0_5_node_71 | 0.4 | n |  | TRUE
107 | bus_LV_6644-4_0_5_node_79 | 0.4 | n |  | TRUE
108 | bus_LV_6644-4_0_5_node_81 | 0.4 | n |  | TRUE
109 | bus_LV_6644-4_0_5_node_144 | 0.4 | n |  | TRUE
110 | bus_LV_6644-4_0_5_node_143 | 0.4 | n |  | TRUE
111 | bus_LV_6644-4_0_5_node_136 | 0.4 | n |  | TRUE
112 | bus_LV_6644-4_0_5_node_95 | 0.4 | n |  | TRUE
113 | bus_LV_6644-4_0_5_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_6644-4_0_5_node_135 | 0.4 | n |  | TRUE
115 | bus_LV_6644-4_0_5_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_6644-4_0_5_node_84 | 0.4 | n |  | TRUE
117 | bus_LV_6644-4_0_5_node_86 | 0.4 | n |  | TRUE
118 | bus_LV_6644-4_0_5_node_87 | 0.4 | n |  | TRUE
119 | bus_LV_6644-4_0_5_node_89 | 0.4 | n |  | TRUE
120 | bus_LV_6644-4_0_5_node_92 | 0.4 | n |  | TRUE
121 | bus_LV_6644-4_0_5_node_91 | 0.4 | n |  | TRUE
122 | bus_LV_6644-4_0_5_node_129 | 0.4 | n |  | TRUE
123 | bus_LV_6644-4_0_5_node_127 | 0.4 | n |  | TRUE
124 | bus_LV_6644-4_0_5_node_157 | 0.4 | n |  | TRUE
125 | bus_LV_6644-4_0_5_node_93 | 0.4 | n |  | TRUE
126 | bus_LV_6644-4_0_5_node_158 | 0.4 | n |  | TRUE
127 | bus_LV_6644-4_0_5_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_6644-4_0_5_node_122 | 0.4 | n |  | TRUE
129 | bus_LV_6644-4_0_5_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_6644-4_0_5_node_106 | 0.4 | n |  | TRUE
131 | bus_LV_6644-4_0_5_node_97 | 0.4 | n |  | TRUE
132 | bus_LV_6644-4_0_5_node_98 | 0.4 | n |  | TRUE
133 | bus_LV_6644-4_0_5_node_99 | 0.4 | n |  | TRUE
134 | bus_LV_6644-4_0_5_node_100 | 0.4 | n |  | TRUE
135 | bus_LV_6644-4_0_5_node_101 | 0.4 | n |  | TRUE
136 | bus_LV_6644-4_0_5_node_102 | 0.4 | n |  | TRUE
137 | bus_LV_6644-4_0_5_node_103 | 0.4 | n |  | TRUE
138 | bus_LV_6644-4_0_5_node_104 | 0.4 | n |  | TRUE
139 | bus_LV_6644-4_0_5_node_140 | 0.4 | n |  | TRUE
140 | bus_LV_6644-4_0_5_node_141 | 0.4 | n |  | TRUE
141 | bus_LV_6644-4_0_5_node_118 | 0.4 | n |  | TRUE
142 | bus_LV_6644-4_0_5_node_142 | 0.4 | n |  | TRUE
143 | bus_LV_6644-4_0_5_node_107 | 0.4 | n |  | TRUE
144 | bus_LV_6644-4_0_5_node_109 | 0.4 | n |  | TRUE
145 | bus_LV_6644-4_0_5_node_112 | 0.4 | n |  | TRUE
146 | bus_LV_6644-4_0_5_node_113 | 0.4 | n |  | TRUE
147 | bus_LV_6644-4_0_5_node_121 | 0.4 | n |  | TRUE
148 | bus_LV_6644-4_0_5_node_154 | 0.4 | n |  | TRUE
149 | bus_LV_6644-4_0_5_node_130 | 0.4 | n |  | TRUE
150 | bus_LV_6644-4_0_5_node_155 | 0.4 | n |  | TRUE
151 | bus_LV_6644-4_0_5_node_162 | 0.4 | n |  | TRUE
152 | bus_LV_6644-4_0_5_node_134 | 0.4 | n |  | TRUE
153 | bus_LV_6644-4_0_5_node_145 | 0.4 | n |  | TRUE
154 | bus_LV_6644-4_0_5_node_146 | 0.4 | n |  | TRUE
155 | bus_LV_6644-4_0_5_node_147 | 0.4 | n |  | TRUE
156 | bus_LV_6644-4_0_5_node_148 | 0.4 | n |  | TRUE
157 | bus_LV_6644-4_0_5_node_149 | 0.4 | n |  | TRUE
158 | bus_LV_6644-4_0_5_node_151 | 0.4 | n |  | TRUE
159 | bus_MV_461_0_node_134 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6644-4_0_5_load_0 | 0 | 0.0049821 | 0.0012486 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6644-4_0_5_load_1 | 1 | 0.0049822 | 0.0012487 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6644-4_0_5_load_2 | 2 | 0.0059133 | 0.001482 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6644-4_0_5_load_14 | 6 | 0.00055751 | 0.00013972 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6644-4_0_5_load_4 | 9 | 0.0098437 | 0.0024671 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6644-4_0_5_load_8 | 11 | 0.00034546 | 8.6582e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6644-4_0_5_load_11 | 12 | 0.0010039 | 0.00025159 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6644-4_0_5_load_51 | 15 | 0.018275 | 0.0045803 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6644-4_0_5_load_25 | 17 | 0.00046683 | 0.000117 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6644-4_0_5_load_15 | 18 | 0.00063293 | 0.00015863 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6644-4_0_5_load_61 | 20 | 0.024012 | 0.0060179 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6644-4_0_5_load_46 | 22 | 0.00017713 | 4.4392e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6644-4_0_5_load_27 | 23 | 0.0065372 | 0.0016384 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6644-4_0_5_load_49 | 24 | 0.041886 | 0.010498 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6644-4_0_5_load_26 | 28 | 0.077255 | 0.019362 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6644-4_0_5_load_28 | 30 | 0.007279 | 0.0018243 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6644-4_0_5_load_31 | 33 | 0.00070713 | 0.00017722 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6644-4_0_5_load_153 | 36 | 0.0013382 | 0.00033538 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6644-4_0_5_load_30 | 38 | 0.0016777 | 0.00042047 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6644-4_0_5_load_156 | 39 | 0.0064287 | 0.0016112 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6644-4_0_5_load_38 | 40 | 0.00065623 | 0.00016447 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6644-4_0_5_load_29 | 41 | 0.005657 | 0.0014178 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6644-4_0_5_load_62 | 42 | 0.01143 | 0.0028647 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6644-4_0_5_load_40 | 43 | 0.0006196 | 0.00015529 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6644-4_0_5_load_39 | 44 | 0.0019238 | 0.00048216 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6644-4_0_5_load_41 | 48 | 0.0067602 | 0.0016943 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6644-4_0_5_load_63 | 51 | 0.011985 | 0.0030038 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6644-4_0_5_load_152 | 52 | 0.00085368 | 0.00021395 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6644-4_0_5_load_36 | 53 | 0.0010466 | 0.00026229 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6644-4_0_5_load_45 | 55 | 0.00039995 | 0.00010024 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6644-4_0_5_load_42 | 56 | 0.0078553 | 0.0019687 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6644-4_0_5_load_77 | 58 | 0.00060574 | 0.00015181 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6644-4_0_5_load_139 | 60 | 0.00040114 | 0.00010054 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6644-4_0_5_load_138 | 61 | 0.0029942 | 0.00075042 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6644-4_0_5_load_35 | 63 | 0.0007799 | 0.00019546 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6644-4_0_5_load_37 | 64 | 0.00048813 | 0.00012234 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6644-4_0_5_load_72 | 65 | 0.00089799 | 0.00022506 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6644-4_0_5_load_78 | 66 | 0.00038797 | 9.7235e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6644-4_0_5_load_50 | 67 | 0.016077 | 0.0040293 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6644-4_0_5_load_52 | 68 | 0.024859 | 0.0062303 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6644-4_0_5_load_64 | 69 | 0.0078119 | 0.0019578 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6644-4_0_5_load_159 | 73 | 0.0013618 | 0.0003413 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6644-4_0_5_load_124 | 81 | 0.00083081 | 0.00020822 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6644-4_0_5_load_133 | 82 | 0.0021377 | 0.00053575 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6644-4_0_5_load_88 | 83 | 0.0018102 | 0.00045369 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6644-4_0_5_load_105 | 85 | 0.00045007 | 0.0001128 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6644-4_0_5_load_85 | 87 | 0.00032126 | 8.0515e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6644-4_0_5_load_119 | 88 | 0.000633 | 0.00015864 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6644-4_0_5_load_131 | 90 | 0.00048981 | 0.00012276 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6644-4_0_5_load_160 | 93 | 0.00013315 | 3.3371e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6644-4_0_5_load_126 | 95 | 0.0004124 | 0.00010336 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6644-4_0_5_load_132 | 97 | 0.00072443 | 0.00018156 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6644-4_0_5_load_82 | 98 | 0.0013033 | 0.00032663 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6644-4_0_5_load_116 | 99 | 0.00091157 | 0.00022846 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6644-4_0_5_load_65 | 100 | 0.00059069 | 0.00014804 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6644-4_0_5_load_66 | 101 | 0.00034703 | 8.6973e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6644-4_0_5_load_67 | 102 | 0.00041669 | 0.00010443 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6644-4_0_5_load_69 | 104 | 0.00026809 | 6.7189e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6644-4_0_5_load_70 | 105 | 0.00028511 | 7.1456e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6644-4_0_5_load_71 | 106 | 0.00038857 | 9.7384e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6644-4_0_5_load_144 | 109 | 0.00027114 | 6.7955e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6644-4_0_5_load_143 | 110 | 0.0018686 | 0.00046832 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6644-4_0_5_load_136 | 111 | 0.00014106 | 3.5354e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6644-4_0_5_load_95 | 112 | 0.00015975 | 4.0038e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6644-4_0_5_load_94 | 113 | 0.00049451 | 0.00012394 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6644-4_0_5_load_87 | 118 | 0.000532 | 0.00013333 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6644-4_0_5_load_89 | 119 | 0.0010634 | 0.0002665 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6644-4_0_5_load_129 | 122 | 0.00089075 | 0.00022324 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6644-4_0_5_load_127 | 123 | 0.00070826 | 0.00017751 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6644-4_0_5_load_157 | 124 | 0.00113 | 0.00028321 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6644-4_0_5_load_158 | 126 | 0.00084675 | 0.00021222 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6644-4_0_5_load_122 | 128 | 0.00034611 | 8.6744e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6644-4_0_5_load_106 | 130 | 0.00012543 | 3.1435e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6644-4_0_5_load_97 | 131 | 0.00014042 | 3.5192e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6644-4_0_5_load_98 | 132 | 0.0001722 | 4.3157e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6644-4_0_5_load_101 | 135 | 0.00021357 | 5.3526e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6644-4_0_5_load_102 | 136 | 0.00025467 | 6.3825e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6644-4_0_5_load_103 | 137 | 0.00010508 | 2.6337e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6644-4_0_5_load_140 | 139 | 0.00024564 | 6.1564e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6644-4_0_5_load_142 | 142 | 0.00014069 | 3.526e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6644-4_0_5_load_109 | 144 | 0.0009957 | 0.00024955 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6644-4_0_5_load_112 | 145 | 0.0003604 | 9.0325e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6644-4_0_5_load_113 | 146 | 0.00042219 | 0.00010581 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6644-4_0_5_load_121 | 147 | 6.1772e-05 | 1.5481e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6644-4_0_5_load_130 | 149 | 0.00057272 | 0.00014354 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6644-4_0_5_load_155 | 150 | 6.6994e-05 | 1.679e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6644-4_0_5_load_162 | 151 | 0.00018735 | 4.6954e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6644-4_0_5_load_134 | 152 | 0.00014294 | 3.5824e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_6644-4_0_5_load_145 | 153 | 0.00071508 | 0.00017922 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_6644-4_0_5_load_146 | 154 | 0.0018543 | 0.00046474 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_6644-4_0_5_load_149 | 157 | 0.0015464 | 0.00038755 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_6644-4_0_5_load_151 | 158 | 0.00063029 | 0.00015796 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 102 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6644-4_0_5_line_0 |  | 0 | 1 | 0.021021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6644-4_0_5_line_1 |  | 1 | 2 | 0.014618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6644-4_0_5_line_2 |  | 2 | 3 | 0.051641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6644-4_0_5_line_3 |  | 3 | 4 | 0.11044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6644-4_0_5_line_4 |  | 3 | 5 | 0.023408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6644-4_0_5_line_5 |  | 4 | 6 | 0.14574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6644-4_0_5_line_6 |  | 4 | 7 | 0.067375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6644-4_0_5_line_7 |  | 5 | 8 | 0.035808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6644-4_0_5_line_8 |  | 7 | 10 | 0.014784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6644-4_0_5_line_9 |  | 7 | 11 | 0.012397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6644-4_0_5_line_10 |  | 8 | 9 | 0.032052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6644-4_0_5_line_11 |  | 10 | 12 | 0.029553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6644-4_0_5_line_12 |  | 10 | 13 | 0.090392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_6644-4_0_5_line_13 |  | 12 | 14 | 0.043411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6644-4_0_5_line_14 |  | 13 | 15 | 0.081002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_6644-4_0_5_line_15 |  | 13 | 16 | 0.003126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_6644-4_0_5_line_16 |  | 14 | 17 | 0.020696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6644-4_0_5_line_17 |  | 14 | 18 | 0.011216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6644-4_0_5_line_18 |  | 15 | 23 | 0.031293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_6644-4_0_5_line_19 |  | 16 | 24 | 0.12817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_6644-4_0_5_line_20 |  | 16 | 22 | 0.020869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6644-4_0_5_line_21 |  | 17 | 41 | 0.0087203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6644-4_0_5_line_22 |  | 19 | 20 | 0.02821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6644-4_0_5_line_23 |  | 19 | 21 | 0.064062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6644-4_0_5_line_24 |  | 21 | 68 | 0.031282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6644-4_0_5_line_25 |  | 23 | 27 | 0.024145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_6644-4_0_5_line_26 |  | 24 | 67 | 0.0022887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6644-4_0_5_line_27 |  | 25 | 26 | 0.004309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_6644-4_0_5_line_28 |  | 25 | 27 | 0.13597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_6644-4_0_5_line_29 |  | 26 | 28 | 0.00369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6644-4_0_5_line_30 |  | 26 | 29 | 0.10326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_6644-4_0_5_line_31 |  | 27 | 30 | 0.02688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_6644-4_0_5_line_32 |  | 29 | 31 | 0.13361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6644-4_0_5_line_33 |  | 29 | 32 | 0.15481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6644-4_0_5_line_34 |  | 29 | 33 | 0.0495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_6644-4_0_5_line_35 |  | 30 | 42 | 0.035094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_6644-4_0_5_line_36 |  | 31 | 40 | 0.01911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6644-4_0_5_line_37 |  | 32 | 39 | 0.1779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6644-4_0_5_line_38 |  | 33 | 38 | 0.025292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6644-4_0_5_line_39 |  | 34 | 35 | 0.069708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6644-4_0_5_line_40 |  | 34 | 36 | 0.092396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6644-4_0_5_line_41 |  | 35 | 37 | 0.0094961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6644-4_0_5_line_42 |  | 35 | 38 | 0.046533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6644-4_0_5_line_43 |  | 36 | 52 | 0.014851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6644-4_0_5_line_44 |  | 37 | 43 | 0.074679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6644-4_0_5_line_45 |  | 37 | 44 | 0.019239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6644-4_0_5_line_46 |  | 40 | 53 | 0.028549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6644-4_0_5_line_47 |  | 42 | 51 | 0.028872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_6644-4_0_5_line_48 |  | 45 | 46 | 0.04177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6644-4_0_5_line_49 |  | 45 | 47 | 0.073712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6644-4_0_5_line_50 |  | 45 | 48 | 0.058731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6644-4_0_5_line_51 |  | 46 | 54 | 0.04719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6644-4_0_5_line_52 |  | 46 | 55 | 0.019738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6644-4_0_5_line_53 |  | 47 | 49 | 0.044044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6644-4_0_5_line_54 |  | 47 | 50 | 0.053053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_6644-4_0_5_line_55 |  | 47 | 51 | 0.080227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_6644-4_0_5_line_56 |  | 48 | 56 | 0.010226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6644-4_0_5_line_57 |  | 49 | 57 | 0.051767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6644-4_0_5_line_58 |  | 49 | 58 | 0.017981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6644-4_0_5_line_59 |  | 50 | 59 | 0.034122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_6644-4_0_5_line_60 |  | 50 | 60 | 0.010796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6644-4_0_5_line_61 |  | 52 | 158 | 0.014608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6644-4_0_5_line_62 |  | 53 | 63 | 0.02479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6644-4_0_5_line_63 |  | 54 | 65 | 0.008132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6644-4_0_5_line_64 |  | 57 | 109 | 0.044023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6644-4_0_5_line_65 |  | 58 | 110 | 0.01495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6644-4_0_5_line_66 |  | 59 | 61 | 0.031401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6644-4_0_5_line_67 |  | 59 | 62 | 0.033607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_6644-4_0_5_line_68 |  | 62 | 111 | 0.068704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6644-4_0_5_line_69 |  | 62 | 107 | 0.018354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_6644-4_0_5_line_70 |  | 63 | 64 | 0.0080284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6644-4_0_5_line_71 |  | 65 | 66 | 0.0074192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6644-4_0_5_line_72 |  | 67 | 69 | 0.10143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6644-4_0_5_line_73 |  | 68 | 70 | 0.033673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6644-4_0_5_line_74 |  | 70 | 71 | 0.10206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6644-4_0_5_line_75 |  | 71 | 86 | 0.001645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6644-4_0_5_line_76 |  | 71 | 87 | 0.0483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6644-4_0_5_line_77 |  | 72 | 73 | 0.025748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_6644-4_0_5_line_78 |  | 72 | 74 | 0.030031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6644-4_0_5_line_79 |  | 72 | 75 | 0.14951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6644-4_0_5_line_80 |  | 72 | 76 | 0.10594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_6644-4_0_5_line_81 |  | 74 | 80 | 0.081285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6644-4_0_5_line_82 |  | 74 | 82 | 0.019385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6644-4_0_5_line_83 |  | 75 | 88 | 0.03628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_6644-4_0_5_line_84 |  | 75 | 89 | 0.031596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_6644-4_0_5_line_85 |  | 76 | 90 | 0.01579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6644-4_0_5_line_86 |  | 76 | 91 | 0.018553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6644-4_0_5_line_87 |  | 77 | 78 | 0.089895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_6644-4_0_5_line_88 |  | 77 | 79 | 0.080167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_6644-4_0_5_line_89 |  | 77 | 80 | 0.063829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_6644-4_0_5_line_90 |  | 77 | 81 | 0.030795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_6644-4_0_5_line_91 |  | 78 | 95 | 0.05929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_6644-4_0_5_line_92 |  | 78 | 96 | 0.080873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_6644-4_0_5_line_93 |  | 78 | 92 | 0.097007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_6644-4_0_5_line_94 |  | 79 | 83 | 0.018976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_6644-4_0_5_line_95 |  | 79 | 84 | 0.049023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_6644-4_0_5_line_96 |  | 80 | 85 | 0.0047936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_6644-4_0_5_line_97 |  | 82 | 97 | 0.010471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_6644-4_0_5_line_98 |  | 84 | 87 | 0.04805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_6644-4_0_5_line_99 |  | 84 | 98 | 0.0063805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_6644-4_0_5_line_100 |  | 86 | 99 | 0.03179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_6644-4_0_5_line_101 |  | 89 | 141 | 0.093069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_6644-4_0_5_line_102 |  | 89 | 137 | 0.097559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_6644-4_0_5_line_103 |  | 91 | 149 | 0.071011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_6644-4_0_5_line_104 |  | 91 | 123 | 0.035299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_6644-4_0_5_line_105 |  | 92 | 93 | 0.014213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_6644-4_0_5_line_106 |  | 92 | 94 | 0.005367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_6644-4_0_5_line_107 |  | 94 | 151 | 0.01542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_6644-4_0_5_line_108 |  | 96 | 128 | 0.025748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_6644-4_0_5_line_109 |  | 96 | 115 | 0.003688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_6644-4_0_5_line_110 |  | 98 | 116 | 0.00098052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_6644-4_0_5_line_111 |  | 100 | 101 | 0.011202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_6644-4_0_5_line_112 |  | 100 | 102 | 0.011212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_6644-4_0_5_line_113 |  | 101 | 103 | 0.0013914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_6644-4_0_5_line_114 |  | 103 | 104 | 0.021908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_6644-4_0_5_line_115 |  | 103 | 105 | 0.015096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_6644-4_0_5_line_116 |  | 105 | 106 | 0.0083451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_6644-4_0_5_line_117 |  | 106 | 107 | 0.044081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_6644-4_0_5_line_118 |  | 107 | 108 | 0.034496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_6644-4_0_5_line_119 |  | 108 | 112 | 0.043354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_6644-4_0_5_line_120 |  | 108 | 113 | 0.038933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_6644-4_0_5_line_121 |  | 111 | 114 | 0.0080442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_6644-4_0_5_line_122 |  | 112 | 115 | 0.015711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_6644-4_0_5_line_123 |  | 114 | 152 | 0.015882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_6644-4_0_5_line_124 |  | 115 | 127 | 0.092928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_6644-4_0_5_line_125 |  | 116 | 117 | 0.062327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_6644-4_0_5_line_126 |  | 116 | 118 | 0.013961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_6644-4_0_5_line_127 |  | 117 | 119 | 0.014995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_6644-4_0_5_line_128 |  | 117 | 120 | 0.066946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_6644-4_0_5_line_129 |  | 120 | 124 | 0.00602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_6644-4_0_5_line_130 |  | 120 | 125 | 0.10157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_6644-4_0_5_line_131 |  | 121 | 122 | 0.008818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_6644-4_0_5_line_132 |  | 121 | 123 | 0.021576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_6644-4_0_5_line_133 |  | 125 | 126 | 0.015751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_6644-4_0_5_line_134 |  | 127 | 129 | 0.067004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_6644-4_0_5_line_135 |  | 127 | 130 | 0.12479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_6644-4_0_5_line_136 |  | 129 | 145 | 0.012795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_6644-4_0_5_line_137 |  | 129 | 146 | 0.014931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_6644-4_0_5_line_138 |  | 130 | 143 | 0.020092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_6644-4_0_5_line_139 |  | 131 | 132 | 0.0031576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_6644-4_0_5_line_140 |  | 131 | 133 | 0.034529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_6644-4_0_5_line_141 |  | 133 | 134 | 0.007433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_6644-4_0_5_line_142 |  | 133 | 135 | 0.026692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_6644-4_0_5_line_143 |  | 134 | 136 | 0.014093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_6644-4_0_5_line_144 |  | 134 | 137 | 0.0056106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_6644-4_0_5_line_145 |  | 135 | 138 | 0.042198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_6644-4_0_5_line_146 |  | 138 | 139 | 0.005886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_6644-4_0_5_line_147 |  | 138 | 140 | 0.028505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_6644-4_0_5_line_148 |  | 140 | 142 | 0.009157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_6644-4_0_5_line_149 |  | 141 | 147 | 0.020744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_6644-4_0_5_line_150 |  | 143 | 144 | 0.022679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_6644-4_0_5_line_151 |  | 147 | 148 | 0.02244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_6644-4_0_5_line_152 |  | 148 | 150 | 0.035802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_6644-4_0_5_line_153 |  | 153 | 154 | 0.0039151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_6644-4_0_5_line_154 |  | 153 | 155 | 0.022449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_6644-4_0_5_line_155 |  | 154 | 156 | 0.0045815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_6644-4_0_5_line_156 |  | 155 | 157 | 0.011039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_6644-4_0_5_line_157 |  | 156 | 158 | 0.0095674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6644-4_0_5_trafo_67 | 0.63 MVA 20/0.4 kV | 159 | 102 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2500012.7656 | 1126318.5098 | 2499991.9534 | 1126315.556
1 | 2499991.9534 | 1126315.556 | 2499977.4799 | 1126313.5018
2 | 2499941.5362 | 1126284.1956 | 2499944.7176 | 1126287.7785 | 2499947.9738 | 1126292.6165 | 2499950.6123 | 1126297.398 | 2499956.5421 | 1126310.5302 | 2499977.4799 | 1126313.5018
3 | 2499866.589 | 1126318.4143 | 2499868.4969 | 1126318.1825 | 2499872.1469 | 1126318.411 | 2499880.4534 | 1126319.1294 | 2499883.8532 | 1126280.5601 | 2499923.3658 | 1126283.2071 | 2499928.7694 | 1126283.6623 | 2499941.5362 | 1126284.1956
4 | 2499922.7359 | 1126270.3206 | 2499932.8895 | 1126276.901 | 2499937.2577 | 1126279.9972 | 2499941.5362 | 1126284.1956
5 | 2499866.589 | 1126318.4143 | 2499864.7492 | 1126317.1773 | 2499859.0225 | 1126312.5805 | 2499851.7808 | 1126311.4554 | 2499850.8862 | 1126310.5029 | 2499850.1574 | 1126306.0678 | 2499849.2587 | 1126303.9369 | 2499847.4601 | 1126301.4652 | 2499844.4315 | 1126298.269 | 2499839.551 | 1126294.9589 | 2499831.9733 | 1126287.9913 | 2499803.2926 | 1126253.8234 | 2499786.5695 | 1126233.2213 | 2499778.0977 | 1126224.4119 | 2499778.942 | 1126210.7226
6 | 2499866.589 | 1126318.4143 | 2499863.8391 | 1126319.4716 | 2499862.0999 | 1126321.0459 | 2499860.9827 | 1126323.3992 | 2499857.7784 | 1126337.4944 | 2499855.988 | 1126343.8836 | 2499852.6172 | 1126351.1885 | 2499849.2493 | 1126356.3475 | 2499841.3389 | 1126368.3528 | 2499835.2698 | 1126376.1027
7 | 2499907.0325 | 1126238.1941 | 2499918.6846 | 1126259.8367 | 2499922.7359 | 1126270.3206
8 | 2499826.7208 | 1126388.1742 | 2499833.2013 | 1126378.7387 | 2499835.2698 | 1126376.1027
9 | 2499835.2698 | 1126376.1027 | 2499843.7947 | 1126383.9552 | 2499844.438 | 1126384.4424
10 | 2499907.0325 | 1126238.1941 | 2499897.2147 | 1126243.0375 | 2499878.2904 | 1126252.3792
11 | 2499826.7208 | 1126388.1742 | 2499847.7495 | 1126403.0237 | 2499850.9646 | 1126405.0668
12 | 2499826.7208 | 1126388.1742 | 2499821.8315 | 1126384.7976 | 2499815.0353 | 1126390.0803 | 2499820.32 | 1126394.5177 | 2499826.1254 | 1126395.4998 | 2499831.4274 | 1126397.2685 | 2499847.2091 | 1126407.6244 | 2499856.1296 | 1126412.8354 | 2499867.2223 | 1126417.4877 | 2499876.512 | 1126419.8686 | 2499883.1143 | 1126420.5596
13 | 2499892.1102 | 1126416.8416 | 2499885.1929 | 1126416.6783 | 2499880.016 | 1126415.9414 | 2499874.41 | 1126414.9003 | 2499866.7815 | 1126412.7588 | 2499860.381 | 1126410.2855 | 2499854.0755 | 1126407.0436 | 2499850.9646 | 1126405.0668
14 | 2499883.1143 | 1126420.5596 | 2499885.4154 | 1126420.7994 | 2499886.549 | 1126423.6157 | 2499888.2365 | 1126424.4994 | 2499896.025 | 1126425.1374 | 2499919.8784 | 1126425.3312 | 2499933.1498 | 1126425.1668 | 2499941.6203 | 1126424.6262 | 2499953.2294 | 1126424.167 | 2499961.9265 | 1126423.9301
15 | 2499883.1143 | 1126420.5596 | 2499879.9888 | 1126420.8116
16 | 2499892.1102 | 1126416.8416 | 2499891.2175 | 1126413.2096 | 2499889.1038 | 1126404.2835 | 2499887.573 | 1126396.653
17 | 2499892.1102 | 1126416.8416 | 2499895.588 | 1126416.9173 | 2499903.3247 | 1126416.8193
18 | 2499961.9265 | 1126423.9301 | 2499964.6946 | 1126423.8547 | 2499976.3116 | 1126422.0057 | 2499979.6301 | 1126421.3058 | 2499991.3608 | 1126418.8768 | 2499992.7472 | 1126418.7785
19 | 2499879.9888 | 1126420.8116 | 2499880.7658 | 1126422.1106 | 2499882.684 | 1126425.2919 | 2499884.2252 | 1126430.8365 | 2499879.791 | 1126437.7031 | 2499865.5644 | 1126452.7817 | 2499849.4986 | 1126468.5022 | 2499840.1528 | 1126478.5412 | 2499829.9418 | 1126486.1375 | 2499817.4572 | 1126493.7603 | 2499805.9848 | 1126500.1323 | 2499799.7416 | 1126509.9198
20 | 2499879.9888 | 1126420.8116 | 2499875.2697 | 1126421.19 | 2499863.954 | 1126424.9354 | 2499860.0739 | 1126426.5837
21 | 2499886.2444 | 1126388.043 | 2499886.7341 | 1126392.471 | 2499887.573 | 1126396.653
22 | 2499669.3373 | 1126558.1364 | 2499648.2907 | 1126576.9866
23 | 2499667.559 | 1126638.0602 | 2499661.8739 | 1126618.3312 | 2499651.1999 | 1126584.5986 | 2499648.2907 | 1126576.9866
24 | 2499667.559 | 1126638.0602 | 2499643.5941 | 1126658.1664
25 | 2500016.2999 | 1126422.255 | 2500012.5142 | 1126420.8056 | 2500005.1405 | 1126418.6819 | 2499998.9294 | 1126418.3401 | 2499992.7472 | 1126418.7785
26 | 2499799.7416 | 1126509.9198 | 2499799.7416 | 1126509.9198 | 2499797.4684 | 1126510.186
27 | 2500140.6846 | 1126432.4819 | 2500141.4625 | 1126428.2441
28 | 2500016.2999 | 1126422.255 | 2500018.9198 | 1126422.6563 | 2500027.8746 | 1126421.5741 | 2500034.8996 | 1126422.6586 | 2500041.6175 | 1126424.2817 | 2500057.7552 | 1126425.4377 | 2500068.0176 | 1126427.9028 | 2500077.6685 | 1126429.7554 | 2500088.984 | 1126431.1136 | 2500101.1402 | 1126432.9693 | 2500110.3227 | 1126435.3967 | 2500115.4205 | 1126436.4798 | 2500122.1331 | 1126438.7146 | 2500130.9745 | 1126441.9594 | 2500137.7327 | 1126444.1601 | 2500139.0025 | 1126440.3034 | 2500140.2981 | 1126434.2782 | 2500140.6846 | 1126432.4819
29 | 2500137.8494 | 1126427.4478 | 2500141.4625 | 1126428.2441
30 | 2500141.4625 | 1126428.2441 | 2500142.2052 | 1126428.4097 | 2500175.2293 | 1126434.0453 | 2500199.9578 | 1126438.684 | 2500216.3945 | 1126441.1474 | 2500235.0612 | 1126444.6746 | 2500238.216 | 1126445.2674 | 2500243.0335 | 1126446.6442
31 | 2500016.2999 | 1126422.255 | 2500023.9911 | 1126448.0106
32 | 2500352.5683 | 1126434.7847 | 2500342.3698 | 1126434.7751 | 2500336.619 | 1126433.825 | 2500309.6028 | 1126431.6249 | 2500281.1048 | 1126430.2499 | 2500257.8828 | 1126431.4118 | 2500248.5021 | 1126433.3123 | 2500234.6526 | 1126438.6109 | 2500235.0612 | 1126444.6746 | 2500238.216 | 1126445.2674 | 2500243.0335 | 1126446.6442
33 | 2500173.369 | 1126360.697 | 2500174.4074 | 1126363.3593 | 2500175.8592 | 1126365.381 | 2500177.8233 | 1126366.6827 | 2500180.0059 | 1126367.6806 | 2500182.3383 | 1126367.9422 | 2500211.6605 | 1126359.9306 | 2500217.7086 | 1126359.2747 | 2500229.5764 | 1126359.0675 | 2500229.91 | 1126368.0565 | 2500233.3688 | 1126416.8964 | 2500233.8497 | 1126425.0046 | 2500234.6526 | 1126438.6109 | 2500235.0612 | 1126444.6746 | 2500238.216 | 1126445.2674 | 2500243.0335 | 1126446.6442
34 | 2500243.0335 | 1126446.6442 | 2500250.7632 | 1126448.8624 | 2500251.4647 | 1126449.3289 | 2500253.4392 | 1126449.8633 | 2500269.3959 | 1126455.47 | 2500287.2963 | 1126462.5456 | 2500289.5253 | 1126463.4612
35 | 2500023.9911 | 1126448.0106 | 2500024.9425 | 1126451.1967 | 2500035.3222 | 1126481.2221
36 | 2500352.5683 | 1126434.7847 | 2500354.5017 | 1126439.3668 | 2500357.96 | 1126442.9342 | 2500364.6763 | 1126445.8697 | 2500366.4242 | 1126446.4399
37 | 2500173.369 | 1126360.697 | 2500166.4405 | 1126361.7232 | 2500163.6269 | 1126362.1922 | 2500153.6396 | 1126363.3136 | 2500140.9533 | 1126363.4344 | 2500134.4436 | 1126362.7527 | 2500128.8323 | 1126361.856 | 2500120.9749 | 1126359.3844 | 2500112.0012 | 1126354.6743 | 2500098.9802 | 1126347.1515 | 2500086.9721 | 1126337.9555 | 2500078.8921 | 1126330.8847 | 2500069.9415 | 1126317.7913 | 2500066.8167 | 1126311.1055 | 2500063.4009 | 1126303.6017 | 2500058.2331 | 1126292.7138 | 2500056.6673 | 1126291.261 | 2500054.8715 | 1126287.5551 | 2500053.9746 | 1126282.7336 | 2500052.4742 | 1126263.6816
38 | 2500312.891 | 1126473.1429 | 2500302.4925 | 1126468.7876 | 2500289.5253 | 1126463.4612
39 | 2500355.4793 | 1126491.5942 | 2500359.3321 | 1126494.3102 | 2500365.1992 | 1126498.1046 | 2500374.8592 | 1126504.7272 | 2500386.3615 | 1126516.0224 | 2500396.464 | 1126527.9743 | 2500394.8616 | 1126534.1046 | 2500397.599 | 1126537.8951 | 2500399.7644 | 1126540.6611
40 | 2500399.7644 | 1126540.6611 | 2500410.9126 | 1126555.7312 | 2500427.6522 | 1126577.0463 | 2500447.7978 | 1126603.9199 | 2500455.9098 | 1126614.0295
41 | 2500355.4793 | 1126491.5942 | 2500357.4943 | 1126489.9155 | 2500360.4373 | 1126488.4105 | 2500362.1765 | 1126487.3033 | 2500362.9336 | 1126486.0011
42 | 2500355.4793 | 1126491.5942 | 2500347.4776 | 1126486.9011 | 2500341.9279 | 1126484.1242 | 2500325.2869 | 1126478.1506 | 2500317.6365 | 1126475.1305 | 2500312.891 | 1126473.1429
43 | 2500465.2043 | 1126625.613 | 2500455.9098 | 1126614.0295
44 | 2500362.9336 | 1126486.0011 | 2500364.6455 | 1126483.2379 | 2500365.8317 | 1126479.9162 | 2500366.7973 | 1126475.8311 | 2500367.332 | 1126473.6654 | 2500367.9879 | 1126472.7762 | 2500370.1595 | 1126472.6403 | 2500387.919 | 1126474.4597 | 2500395.6732 | 1126474.8988 | 2500398.1194 | 1126475.5255 | 2500399.27 | 1126476.585 | 2500400.837 | 1126477.6487 | 2500402.3953 | 1126478.19 | 2500405.3417 | 1126477.8301 | 2500408.7148 | 1126475.7621 | 2500411.7487 | 1126474.6336 | 2500414.1702 | 1126474.2268 | 2500426.6398 | 1126474.9995
45 | 2500362.9336 | 1126486.0011 | 2500362.9165 | 1126484.9675 | 2500361.3514 | 1126484.0149 | 2500345.3421 | 1126480.5826
46 | 2500366.4242 | 1126446.4399 | 2500387.772 | 1126453.4046 | 2500393.7369 | 1126454.6507
47 | 2500044.7647 | 1126508.5063 | 2500038.4633 | 1126490.3084 | 2500036.755 | 1126485.3669 | 2500035.3222 | 1126481.2221
48 | 2500138.9728 | 1126561.5461 | 2500178.8687 | 1126548.801
49 | 2500069.0984 | 1126584.9494 | 2500103.1915 | 1126574.1788 | 2500124.2428 | 1126566.2481 | 2500138.9728 | 1126561.5461
50 | 2500138.9728 | 1126561.5461 | 2500137.5097 | 1126554.1768 | 2500122.6823 | 1126507.3261 | 2500122.2298 | 1126505.2992
51 | 2500178.8687 | 1126548.801 | 2500175.0992 | 1126532.9423 | 2500169.4965 | 1126506.4517 | 2500168.6029 | 1126502.7531
52 | 2500178.8687 | 1126548.801 | 2500197.6711 | 1126542.797
53 | 2500069.0984 | 1126584.9494 | 2500070.1143 | 1126588.5793 | 2500073.1395 | 1126599.5027 | 2500080.0794 | 1126627.5943
54 | 2500069.0984 | 1126584.9494 | 2500048.8434 | 1126591.622 | 2500030.0562 | 1126597.5476 | 2500030.8288 | 1126604.1723 | 2500032.3456 | 1126608.2609 | 2500032.9675 | 1126609.04
55 | 2500069.0984 | 1126584.9494 | 2500067.9596 | 1126581.3438 | 2500048.2345 | 1126518.5198 | 2500047.7651 | 1126517.1712 | 2500044.7647 | 1126508.5063
56 | 2500120.0015 | 1126495.3184 | 2500122.2298 | 1126505.2992
57 | 2500092.5042 | 1126677.8423 | 2500080.0794 | 1126627.5943
58 | 2500080.0794 | 1126627.5943 | 2500062.7108 | 1126632.2482
59 | 2500008.9837 | 1126604.1894 | 2500030.0562 | 1126597.5476 | 2500030.8288 | 1126604.1723 | 2500032.3456 | 1126608.2609 | 2500032.9675 | 1126609.04
60 | 2500032.9675 | 1126609.04 | 2500035.1951 | 1126611.8271 | 2500036.963 | 1126618.8351
61 | 2500465.2043 | 1126625.613 | 2500466.4812 | 1126627.2043 | 2500472.6703 | 1126634.1844 | 2500474.8773 | 1126636.555
62 | 2500418.2365 | 1126458.0093 | 2500405.9728 | 1126457.2069 | 2500393.7369 | 1126454.6507
63 | 2500168.6029 | 1126502.7531 | 2500166.0043 | 1126501.7732 | 2500163.533 | 1126502.4255 | 2500160.943 | 1126503.4863
64 | 2500051.2922 | 1126691.1101 | 2500055.1463 | 1126686.9215 | 2500063.0776 | 1126685.0336 | 2500092.5042 | 1126677.8423
65 | 2500053.1145 | 1126641.9493 | 2500054.3974 | 1126638.4259 | 2500055.6888 | 1126635.4138 | 2500057.5248 | 1126633.6378 | 2500062.7108 | 1126632.2482
66 | 2500008.9837 | 1126604.1894 | 2500018.3045 | 1126634.1751
67 | 2500008.9837 | 1126604.1894 | 2499989.5381 | 1126609.926 | 2499976.7075 | 1126613.8742
68 | 2499976.7075 | 1126613.8742 | 2499995.8226 | 1126679.8655
69 | 2499959.0489 | 1126619.0587 | 2499976.2705 | 1126614.0149 | 2499976.7075 | 1126613.8742
70 | 2500426.2275 | 1126458.7582 | 2500421.7151 | 1126458.2369 | 2500418.2365 | 1126458.0093
71 | 2500156.6105 | 1126508.9329 | 2500157.4037 | 1126506.5516 | 2500158.8089 | 1126504.3604 | 2500160.943 | 1126503.4863
72 | 2499797.4684 | 1126510.186 | 2499793.5483 | 1126510.6452 | 2499777.2673 | 1126513.3836 | 2499765.621 | 1126521.8154 | 2499758.8121 | 1126528.6327 | 2499747.8111 | 1126539.711 | 2499742.9021 | 1126546.2855 | 2499739.3701 | 1126548.5121 | 2499731.6791 | 1126549.0957 | 2499722.006 | 1126548.6893 | 2499710.9654 | 1126545.224
73 | 2499616.9364 | 1126678.7154 | 2499634.9225 | 1126665.4416 | 2499643.5941 | 1126658.1664
74 | 2499558.2071 | 1126758.3969 | 2499559.4347 | 1126753.4178 | 2499563.7476 | 1126738.37 | 2499567.8349 | 1126728.2958 | 2499574.1163 | 1126718.9856 | 2499576.0946 | 1126716.0397 | 2499584.6433 | 1126704.9351 | 2499609.0093 | 1126684.5619 | 2499616.9364 | 1126678.7154
75 | 2499557.8097 | 1126759.9934 | 2499558.2071 | 1126758.3969
76 | 2499558.2071 | 1126758.3969 | 2499576.5524 | 1126757.0021 | 2499579.7521 | 1126757.049 | 2499583.5358 | 1126760.6995 | 2499594.4582 | 1126779.154
77 | 2499742.0719 | 1126872.7362 | 2499766.4176 | 1126864.149
78 | 2499742.0719 | 1126872.7362 | 2499737.3744 | 1126857.6825 | 2499723.7308 | 1126861.8338
79 | 2499742.0719 | 1126872.7362 | 2499753.0061 | 1126907.8099 | 2499756.1237 | 1126914.0621 | 2499786.0804 | 1126952.3556 | 2499821.2441 | 1126997.4338
80 | 2499684.1523 | 1126900.9264 | 2499753.0061 | 1126907.8099 | 2499742.0719 | 1126872.7362
81 | 2499721.6392 | 1126796.2387 | 2499718.404 | 1126796.8372 | 2499732.6278 | 1126842.4629 | 2499737.3744 | 1126857.6825 | 2499723.7308 | 1126861.8338
82 | 2499723.7308 | 1126861.8338 | 2499717.6877 | 1126843.415
83 | 2499821.2441 | 1126997.4338 | 2499804.6588 | 1127003.5905 | 2499787.5344 | 1127010.8222
84 | 2499830.9462 | 1127027.5027 | 2499823.1048 | 1127003.1954 | 2499821.2441 | 1126997.4338
85 | 2499684.1523 | 1126900.9264 | 2499682.7332 | 1126916.6487
86 | 2499684.1523 | 1126900.9264 | 2499665.6379 | 1126899.0772
87 | 2499726.0192 | 1126748.0804 | 2499773.1431 | 1126715.8227 | 2499784.3391 | 1126708.1544 | 2499800.3579 | 1126697.5376
88 | 2499659.4619 | 1126792.7579 | 2499695.4817 | 1126769.0894 | 2499707.0265 | 1126761.0816 | 2499726.0192 | 1126748.0804
89 | 2499721.6392 | 1126796.2387 | 2499718.404 | 1126796.8372 | 2499718.1844 | 1126796.1404 | 2499707.0265 | 1126761.0816 | 2499726.0192 | 1126748.0804
90 | 2499726.0192 | 1126748.0804 | 2499739.3175 | 1126772.7862 | 2499739.0222 | 1126774.0363 | 2499738.3548 | 1126775.3275
91 | 2499800.3579 | 1126697.5376 | 2499811.6778 | 1126732.1715 | 2499812.4782 | 1126737.2058 | 2499811.7188 | 1126741.1431 | 2499809.9419 | 1126744.1522 | 2499809.399 | 1126745.8067 | 2499809.4633 | 1126746.8952 | 2499810.0719 | 1126749.1976 | 2499811.1701 | 1126754.1148
92 | 2499800.3579 | 1126697.5376 | 2499867.9181 | 1126652.7895
93 | 2499800.3579 | 1126697.5376 | 2499784.3391 | 1126708.1544 | 2499773.1431 | 1126715.8227 | 2499803.5503 | 1126772.3869
94 | 2499659.4619 | 1126792.7579 | 2499658.7099 | 1126783.6869 | 2499657.4461 | 1126779.0717 | 2499655.5094 | 1126777.5585 | 2499652.8714 | 1126777.4467
95 | 2499618.9316 | 1126820.5041 | 2499653.9415 | 1126796.3852 | 2499659.4619 | 1126792.7579
96 | 2499721.6392 | 1126796.2387 | 2499723.2313 | 1126797.4241 | 2499724.9258 | 1126799.6641
97 | 2499714.4234 | 1126833.4653 | 2499717.6877 | 1126843.415
98 | 2499618.9316 | 1126820.5041 | 2499594.4582 | 1126779.154
99 | 2499618.9316 | 1126820.5041 | 2499613.6802 | 1126824.1282
100 | 2499557.8097 | 1126759.9934 | 2499551.889 | 1126784.029 | 2499550.2364 | 1126790.8676
101 | 2499830.9462 | 1127027.5027 | 2499860.6046 | 1127115.7215
102 | 2499830.9462 | 1127027.5027 | 2499768.0963 | 1127102.1188
103 | 2499665.6379 | 1126899.0772 | 2499658.7971 | 1126960.0622 | 2499658.024 | 1126969.6588
104 | 2499665.6379 | 1126899.0772 | 2499630.5133 | 1126895.5691
105 | 2499803.5503 | 1126772.3869 | 2499804.9871 | 1126773.0413 | 2499807.0591 | 1126772.9513 | 2499816.8586 | 1126768.9196
106 | 2499806.0953 | 1126777.1143 | 2499803.5503 | 1126772.3869
107 | 2499806.0953 | 1126777.1143 | 2499807.0856 | 1126777.7983 | 2499808.4846 | 1126778.0308 | 2499809.9247 | 1126777.4844 | 2499820.1268 | 1126772.6344
108 | 2499862.9173 | 1126677.5323 | 2499866.2023 | 1126666.4598 | 2499868.224 | 1126660.5449 | 2499868.9408 | 1126657.2865 | 2499867.9181 | 1126652.7895
109 | 2499870.9984 | 1126650.7483 | 2499867.9181 | 1126652.7895
110 | 2499613.6802 | 1126824.1282 | 2499612.8732 | 1126824.6851
111 | 2499934.5336 | 1126542.7863 | 2499937.6151 | 1126552.7279 | 2499937.8601 | 1126553.4834
112 | 2499931.214 | 1126532.0766 | 2499934.5336 | 1126542.7863
113 | 2499938.2893 | 1126554.8069 | 2499937.8601 | 1126553.4834
114 | 2499938.2893 | 1126554.8069 | 2499933.5579 | 1126554.8965 | 2499917.0517 | 1126559.8619
115 | 2499938.2893 | 1126554.8069 | 2499942.9305 | 1126569.1715
116 | 2499942.9305 | 1126569.1715 | 2499945.4962 | 1126577.1124
117 | 2499959.0489 | 1126619.0587 | 2499945.4962 | 1126577.1124
118 | 2499959.0489 | 1126619.0587 | 2499926.2631 | 1126630.0753
119 | 2499926.2631 | 1126630.0753 | 2499890.1354 | 1126642.2259 | 2499885.3503 | 1126644.3569
120 | 2499926.2631 | 1126630.0753 | 2499921.2628 | 1126658.12 | 2499921.4378 | 1126662.1641 | 2499923.0905 | 1126668.3447
121 | 2500002.4776 | 1126683.7578 | 2499998.6583 | 1126682.5981 | 2499997.1497 | 1126681.8003 | 2499995.8226 | 1126679.8655
122 | 2499870.9984 | 1126650.7483 | 2499885.3503 | 1126644.3569
123 | 2500002.4776 | 1126683.7578 | 2500001.4016 | 1126684.4093 | 2499996.6309 | 1126689.5693 | 2499991.0781 | 1126694.7537
124 | 2499870.9984 | 1126650.7483 | 2499923.4998 | 1126727.504
125 | 2499612.8732 | 1126824.6851 | 2499596.6791 | 1126835.839 | 2499566.8016 | 1126856.1594 | 2499561.2907 | 1126859.8867
126 | 2499599.7423 | 1126824.4365 | 2499606.8396 | 1126822.4729 | 2499610.0511 | 1126822.7753 | 2499612.8732 | 1126824.6851
127 | 2499561.2907 | 1126859.8867 | 2499556.0621 | 1126845.8316
128 | 2499504.9335 | 1126876.779 | 2499517.0069 | 1126881.57 | 2499528.2464 | 1126885.3521 | 2499532.5856 | 1126879.3095 | 2499561.2907 | 1126859.8867
129 | 2499504.9335 | 1126876.779 | 2499502.9702 | 1126882.4708
130 | 2499504.9335 | 1126876.779 | 2499517.0069 | 1126881.57 | 2499528.2464 | 1126885.3521 | 2499527.6732 | 1126912.045 | 2499528.4329 | 1126933.6125 | 2499529.0888 | 1126952.1798 | 2499529.4378 | 1126962.0357
131 | 2499609.0446 | 1126893.425 | 2499610.3023 | 1126884.6986
132 | 2499609.0446 | 1126893.425 | 2499630.5133 | 1126895.5691
133 | 2499514.2284 | 1126966.1024 | 2499519.1652 | 1126964.4748 | 2499525.5455 | 1126962.5119 | 2499529.4378 | 1126962.0357
134 | 2499923.4998 | 1126727.504 | 2499868.3192 | 1126765.7422
135 | 2499923.4998 | 1126727.504 | 2499948.2728 | 1126763.7162 | 2499947.7442 | 1126772.7528 | 2499942.0295 | 1126784.666 | 2499930.045 | 1126805.6887 | 2499912.9762 | 1126835.6192
136 | 2499868.3192 | 1126765.7422 | 2499867.5496 | 1126766.2775 | 2499858.9822 | 1126767.4536 | 2499855.775 | 1126767.3344
137 | 2499868.3192 | 1126765.7422 | 2499874.0924 | 1126779.5116
138 | 2499902.8098 | 1126852.9472 | 2499906.9824 | 1126846.1293 | 2499912.9762 | 1126835.6192
139 | 2499724.9064 | 1127121.9432 | 2499726.6197 | 1127119.2908
140 | 2499760.376 | 1127112.5931 | 2499731.2893 | 1127117.3566 | 2499726.6197 | 1127119.2908
141 | 2499760.376 | 1127112.5931 | 2499763.2648 | 1127107.8533 | 2499764.4818 | 1127106.41
142 | 2499760.376 | 1127112.5931 | 2499746.4615 | 1127135.371
143 | 2499764.4818 | 1127106.41 | 2499769.05 | 1127113.2273 | 2499769.0747 | 1127114.7167 | 2499765.4001 | 1127117.157
144 | 2499764.4818 | 1127106.41 | 2499768.0963 | 1127102.1188
145 | 2499724.4636 | 1127171.3813 | 2499746.4615 | 1127135.371
146 | 2499719.0746 | 1127168.9804 | 2499724.4636 | 1127171.3813
147 | 2499709.5915 | 1127195.7212 | 2499724.4636 | 1127171.3813
148 | 2499709.5915 | 1127195.7212 | 2499701.6608 | 1127191.1055
149 | 2499860.6046 | 1127115.7215 | 2499854.8425 | 1127118.2409 | 2499847.511 | 1127121.8647 | 2499842.0178 | 1127124.9023
150 | 2499884.6771 | 1126839.2613 | 2499902.8098 | 1126852.9472
151 | 2499822.7165 | 1127136.3293 | 2499832.1518 | 1127130.358 | 2499842.0178 | 1127124.9023
152 | 2499792.3574 | 1127155.4447 | 2499810.0015 | 1127144.3785 | 2499822.7165 | 1127136.3293
153 | 2500486.7892 | 1126650.0968 | 2500485.3672 | 1126648.7621 | 2500484.1754 | 1126647.2
154 | 2500501.3426 | 1126666.7768 | 2500499.5004 | 1126662.5712 | 2500496.5333 | 1126658.8622 | 2500490.2214 | 1126653.3183 | 2500486.7892 | 1126650.0968
155 | 2500481.3964 | 1126643.5576 | 2500484.1754 | 1126647.2
156 | 2500501.3426 | 1126666.7768 | 2500500.9251 | 1126669.5076 | 2500501.0862 | 1126672.2622 | 2500501.816 | 1126674.9185 | 2500503.0973 | 1126677.3656
157 | 2500481.3964 | 1126643.5576 | 2500474.8773 | 1126636.555

## bus_geodata
| x | y | coords
0 | 2500012.7656 | 1126318.5098
1 | 2499991.9534 | 1126315.556
2 | 2499977.4799 | 1126313.5018
3 | 2499941.5362 | 1126284.1956
4 | 2499866.589 | 1126318.4143
5 | 2499922.7359 | 1126270.3206
6 | 2499778.942 | 1126210.7226
7 | 2499835.2698 | 1126376.1027
8 | 2499907.0325 | 1126238.1941
9 | 2499878.2904 | 1126252.3792
10 | 2499826.7208 | 1126388.1742
11 | 2499844.438 | 1126384.4424
12 | 2499850.9646 | 1126405.0668
13 | 2499883.1143 | 1126420.5596
14 | 2499892.1102 | 1126416.8415
15 | 2499961.9265 | 1126423.9301
16 | 2499879.9888 | 1126420.8116
17 | 2499887.573 | 1126396.653
18 | 2499903.3247 | 1126416.8193
19 | 2499648.2907 | 1126576.9866
20 | 2499669.3373 | 1126558.1364
21 | 2499667.559 | 1126638.0602
22 | 2499860.0739 | 1126426.5837
23 | 2499992.7472 | 1126418.7785
24 | 2499799.7416 | 1126509.9198
25 | 2500140.6846 | 1126432.4819
26 | 2500141.4625 | 1126428.2441
27 | 2500016.2999 | 1126422.255
28 | 2500137.8494 | 1126427.4478
29 | 2500243.0335 | 1126446.6442
30 | 2500023.9911 | 1126448.0106
31 | 2500352.5683 | 1126434.7847
32 | 2500173.369 | 1126360.697
33 | 2500289.5253 | 1126463.4612
34 | 2500399.7644 | 1126540.6611
35 | 2500355.4793 | 1126491.5942
36 | 2500455.9098 | 1126614.0295
37 | 2500362.9336 | 1126486.0011
38 | 2500312.891 | 1126473.1429
39 | 2500052.4742 | 1126263.6816
40 | 2500366.4242 | 1126446.4399
41 | 2499886.2444 | 1126388.043
42 | 2500035.3222 | 1126481.2221
43 | 2500426.6398 | 1126474.9995
44 | 2500345.3421 | 1126480.5826
45 | 2500138.9728 | 1126561.5461
46 | 2500178.8687 | 1126548.801
47 | 2500069.0984 | 1126584.9494
48 | 2500122.2298 | 1126505.2992
49 | 2500080.0794 | 1126627.5943
50 | 2500032.9675 | 1126609.04
51 | 2500044.7647 | 1126508.5063
52 | 2500465.2043 | 1126625.613
53 | 2500393.7369 | 1126454.6507
54 | 2500168.6029 | 1126502.7531
55 | 2500197.6711 | 1126542.797
56 | 2500120.0015 | 1126495.3185
57 | 2500092.5042 | 1126677.8423
58 | 2500062.7108 | 1126632.2482
59 | 2500008.9837 | 1126604.1894
60 | 2500036.963 | 1126618.8351
61 | 2500018.3045 | 1126634.1751
62 | 2499976.7075 | 1126613.8742
63 | 2500418.2365 | 1126458.0093
64 | 2500426.2275 | 1126458.7582
65 | 2500160.943 | 1126503.4863
66 | 2500156.6105 | 1126508.9329
67 | 2499797.4684 | 1126510.186
68 | 2499643.5941 | 1126658.1664
69 | 2499710.9654 | 1126545.224
70 | 2499616.9364 | 1126678.7154
71 | 2499558.2071 | 1126758.3969
72 | 2499742.0719 | 1126872.7362
73 | 2499766.4176 | 1126864.149
74 | 2499723.7308 | 1126861.8338
75 | 2499821.2441 | 1126997.4338
76 | 2499684.1523 | 1126900.9264
77 | 2499726.0192 | 1126748.0804
78 | 2499800.3579 | 1126697.5376
79 | 2499659.4619 | 1126792.7579
80 | 2499721.6392 | 1126796.2387
81 | 2499738.3548 | 1126775.3275
82 | 2499717.6877 | 1126843.415
83 | 2499652.8714 | 1126777.4467
84 | 2499618.9316 | 1126820.5041
85 | 2499724.9258 | 1126799.6641
86 | 2499557.8097 | 1126759.9934
87 | 2499594.4582 | 1126779.154
88 | 2499787.5344 | 1127010.8222
89 | 2499830.9462 | 1127027.5027
90 | 2499682.7332 | 1126916.6487
91 | 2499665.6379 | 1126899.0772
92 | 2499803.5503 | 1126772.3869
93 | 2499816.8586 | 1126768.9196
94 | 2499806.0953 | 1126777.1143
95 | 2499811.1701 | 1126754.1148
96 | 2499867.9181 | 1126652.7895
97 | 2499714.4234 | 1126833.4653
98 | 2499613.6802 | 1126824.1282
99 | 2499550.2364 | 1126790.8676
100 | 2499934.5336 | 1126542.7863
101 | 2499937.8601 | 1126553.4834
102 | 2499931.214 | 1126532.0766
103 | 2499938.2893 | 1126554.8069
104 | 2499917.0517 | 1126559.8619
105 | 2499942.9305 | 1126569.1715
106 | 2499945.4962 | 1126577.1124
107 | 2499959.0489 | 1126619.0587
108 | 2499926.2631 | 1126630.0753
109 | 2500051.2922 | 1126691.1101
110 | 2500053.1145 | 1126641.9493
111 | 2499995.8226 | 1126679.8655
112 | 2499885.3503 | 1126644.3569
113 | 2499923.0905 | 1126668.3447
114 | 2500002.4776 | 1126683.7578
115 | 2499870.9984 | 1126650.7483
116 | 2499612.8732 | 1126824.6851
117 | 2499561.2907 | 1126859.8867
118 | 2499599.7423 | 1126824.4365
119 | 2499556.0621 | 1126845.8316
120 | 2499504.9335 | 1126876.779
121 | 2499609.0446 | 1126893.425
122 | 2499610.3023 | 1126884.6986
123 | 2499630.5133 | 1126895.5691
124 | 2499502.9702 | 1126882.4708
125 | 2499529.4378 | 1126962.0357
126 | 2499514.2284 | 1126966.1024
127 | 2499923.4998 | 1126727.504
128 | 2499862.9173 | 1126677.5323
129 | 2499868.3192 | 1126765.7422
130 | 2499912.9762 | 1126835.6192
131 | 2499726.6197 | 1127119.2908
132 | 2499724.9064 | 1127121.9432
133 | 2499760.376 | 1127112.5931
134 | 2499764.4818 | 1127106.41
135 | 2499746.4615 | 1127135.371
136 | 2499765.4001 | 1127117.157
137 | 2499768.0963 | 1127102.1188
138 | 2499724.4636 | 1127171.3813
139 | 2499719.0746 | 1127168.9804
140 | 2499709.5915 | 1127195.7212
141 | 2499860.6046 | 1127115.7215
142 | 2499701.6608 | 1127191.1055
143 | 2499902.8098 | 1126852.9472
144 | 2499884.6771 | 1126839.2613
145 | 2499855.775 | 1126767.3344
146 | 2499874.0924 | 1126779.5116
147 | 2499842.0178 | 1127124.9023
148 | 2499822.7165 | 1127136.3293
149 | 2499658.024 | 1126969.6588
150 | 2499792.3574 | 1127155.4447
151 | 2499820.1268 | 1126772.6344
152 | 2499991.0781 | 1126694.7537
153 | 2500486.7892 | 1126650.0968
154 | 2500484.1754 | 1126647.2
155 | 2500501.3426 | 1126666.7768
156 | 2500481.3964 | 1126643.5576
157 | 2500503.0973 | 1126677.3656
158 | 2500474.8773 | 1126636.555
159 | 2499938.2893 | 1126554.8069

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1