## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6644-7_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6644-7_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6644-7_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6644-7_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6644-7_0_8_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_6644-7_0_8_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_6644-7_0_8_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_6644-7_0_8_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_6644-7_0_8_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_6644-7_0_8_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_6644-7_0_8_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_6644-7_0_8_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_6644-7_0_8_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_6644-7_0_8_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_6644-7_0_8_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_6644-7_0_8_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_6644-7_0_8_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_6644-7_0_8_node_84 | 0.4 | n |  | TRUE
18 | bus_LV_6644-7_0_8_node_85 | 0.4 | n |  | TRUE
19 | bus_LV_6644-7_0_8_node_86 | 0.4 | n |  | TRUE
20 | bus_LV_6644-7_0_8_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_6644-7_0_8_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_6644-7_0_8_node_72 | 0.4 | n |  | TRUE
23 | bus_LV_6644-7_0_8_node_68 | 0.4 | n |  | TRUE
24 | bus_LV_6644-7_0_8_node_87 | 0.4 | n |  | TRUE
25 | bus_LV_6644-7_0_8_node_163 | 0.4 | n |  | TRUE
26 | bus_LV_6644-7_0_8_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_6644-7_0_8_node_45 | 0.4 | n |  | TRUE
28 | bus_LV_6644-7_0_8_node_175 | 0.4 | n |  | TRUE
29 | bus_LV_6644-7_0_8_node_176 | 0.4 | n |  | TRUE
30 | bus_LV_6644-7_0_8_node_153 | 0.4 | n |  | TRUE
31 | bus_LV_6644-7_0_8_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_6644-7_0_8_node_77 | 0.4 | n |  | TRUE
33 | bus_LV_6644-7_0_8_node_88 | 0.4 | n |  | TRUE
34 | bus_LV_6644-7_0_8_node_47 | 0.4 | n |  | TRUE
35 | bus_LV_6644-7_0_8_node_161 | 0.4 | n |  | TRUE
36 | bus_LV_6644-7_0_8_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_6644-7_0_8_node_62 | 0.4 | n |  | TRUE
38 | bus_LV_6644-7_0_8_node_173 | 0.4 | n |  | TRUE
39 | bus_LV_6644-7_0_8_node_168 | 0.4 | n |  | TRUE
40 | bus_LV_6644-7_0_8_node_61 | 0.4 | n |  | TRUE
41 | bus_LV_6644-7_0_8_node_55 | 0.4 | n |  | TRUE
42 | bus_LV_6644-7_0_8_node_170 | 0.4 | n |  | TRUE
43 | bus_LV_6644-7_0_8_node_64 | 0.4 | n |  | TRUE
44 | bus_LV_6644-7_0_8_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_6644-7_0_8_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_6644-7_0_8_node_52 | 0.4 | n |  | TRUE
47 | bus_LV_6644-7_0_8_node_174 | 0.4 | n |  | TRUE
48 | bus_LV_6644-7_0_8_node_56 | 0.4 | n |  | TRUE
49 | bus_LV_6644-7_0_8_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_6644-7_0_8_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_6644-7_0_8_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_6644-7_0_8_node_75 | 0.4 | n |  | TRUE
53 | bus_LV_6644-7_0_8_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_6644-7_0_8_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_6644-7_0_8_node_66 | 0.4 | n |  | TRUE
56 | bus_LV_6644-7_0_8_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_6644-7_0_8_node_33 | 0.4 | n |  | TRUE
58 | bus_LV_6644-7_0_8_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_6644-7_0_8_node_96 | 0.4 | n |  | TRUE
60 | bus_LV_6644-7_0_8_node_94 | 0.4 | n |  | TRUE
61 | bus_LV_6644-7_0_8_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_6644-7_0_8_node_112 | 0.4 | n |  | TRUE
63 | bus_LV_6644-7_0_8_node_109 | 0.4 | n |  | TRUE
64 | bus_LV_6644-7_0_8_node_90 | 0.4 | n |  | TRUE
65 | bus_LV_6644-7_0_8_node_39 | 0.4 | n |  | TRUE
66 | bus_LV_6644-7_0_8_node_79 | 0.4 | n |  | TRUE
67 | bus_LV_6644-7_0_8_node_111 | 0.4 | n |  | TRUE
68 | bus_LV_6644-7_0_8_node_116 | 0.4 | n |  | TRUE
69 | bus_LV_6644-7_0_8_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_6644-7_0_8_node_91 | 0.4 | n |  | TRUE
71 | bus_LV_6644-7_0_8_node_140 | 0.4 | n |  | TRUE
72 | bus_LV_6644-7_0_8_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_6644-7_0_8_node_113 | 0.4 | n |  | TRUE
74 | bus_LV_6644-7_0_8_node_46 | 0.4 | n |  | TRUE
75 | bus_LV_6644-7_0_8_node_162 | 0.4 | n |  | TRUE
76 | bus_LV_6644-7_0_8_node_127 | 0.4 | n |  | TRUE
77 | bus_LV_6644-7_0_8_node_50 | 0.4 | n |  | TRUE
78 | bus_LV_6644-7_0_8_node_160 | 0.4 | n |  | TRUE
79 | bus_LV_6644-7_0_8_node_58 | 0.4 | n |  | TRUE
80 | bus_LV_6644-7_0_8_node_136 | 0.4 | n |  | TRUE
81 | bus_LV_6644-7_0_8_node_150 | 0.4 | n |  | TRUE
82 | bus_LV_6644-7_0_8_node_59 | 0.4 | n |  | TRUE
83 | bus_LV_6644-7_0_8_node_108 | 0.4 | n |  | TRUE
84 | bus_LV_6644-7_0_8_node_126 | 0.4 | n |  | TRUE
85 | bus_LV_6644-7_0_8_node_100 | 0.4 | n |  | TRUE
86 | bus_LV_6644-7_0_8_node_97 | 0.4 | n |  | TRUE
87 | bus_LV_6644-7_0_8_node_143 | 0.4 | n |  | TRUE
88 | bus_LV_6644-7_0_8_node_63 | 0.4 | n |  | TRUE
89 | bus_LV_6644-7_0_8_node_128 | 0.4 | n |  | TRUE
90 | bus_LV_6644-7_0_8_node_51 | 0.4 | n |  | TRUE
91 | bus_LV_6644-7_0_8_node_106 | 0.4 | n |  | TRUE
92 | bus_LV_6644-7_0_8_node_107 | 0.4 | n |  | TRUE
93 | bus_LV_6644-7_0_8_node_65 | 0.4 | n |  | TRUE
94 | bus_LV_6644-7_0_8_node_103 | 0.4 | n |  | TRUE
95 | bus_LV_6644-7_0_8_node_149 | 0.4 | n |  | TRUE
96 | bus_LV_6644-7_0_8_node_29 | 0.4 | n |  | TRUE
97 | bus_LV_6644-7_0_8_node_21 | 0.4 | n |  | TRUE
98 | bus_LV_6644-7_0_8_node_23 | 0.4 | n |  | TRUE
99 | bus_LV_6644-7_0_8_node_22 | 0.4 | n |  | TRUE
100 | bus_LV_6644-7_0_8_node_24 | 0.4 | n |  | TRUE
101 | bus_LV_6644-7_0_8_node_25 | 0.4 | n |  | TRUE
102 | bus_LV_6644-7_0_8_node_26 | 0.4 | n |  | TRUE
103 | bus_LV_6644-7_0_8_node_164 | 0.4 | n |  | TRUE
104 | bus_LV_6644-7_0_8_node_165 | 0.4 | n |  | TRUE
105 | bus_LV_6644-7_0_8_node_27 | 0.4 | n |  | TRUE
106 | bus_LV_6644-7_0_8_node_28 | 0.4 | n |  | TRUE
107 | bus_LV_6644-7_0_8_node_139 | 0.4 | n |  | TRUE
108 | bus_LV_6644-7_0_8_node_125 | 0.4 | n |  | TRUE
109 | bus_LV_6644-7_0_8_node_110 | 0.4 | n |  | TRUE
110 | bus_LV_6644-7_0_8_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_6644-7_0_8_node_78 | 0.4 | n |  | TRUE
112 | bus_LV_6644-7_0_8_node_114 | 0.4 | n |  | TRUE
113 | bus_LV_6644-7_0_8_node_92 | 0.4 | n |  | TRUE
114 | bus_LV_6644-7_0_8_node_141 | 0.4 | n |  | TRUE
115 | bus_LV_6644-7_0_8_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_6644-7_0_8_node_95 | 0.4 | n |  | TRUE
117 | bus_LV_6644-7_0_8_node_93 | 0.4 | n |  | TRUE
118 | bus_LV_6644-7_0_8_node_159 | 0.4 | n |  | TRUE
119 | bus_LV_6644-7_0_8_node_144 | 0.4 | n |  | TRUE
120 | bus_LV_6644-7_0_8_node_145 | 0.4 | n |  | TRUE
121 | bus_LV_6644-7_0_8_node_135 | 0.4 | n |  | TRUE
122 | bus_LV_6644-7_0_8_node_104 | 0.4 | n |  | TRUE
123 | bus_LV_6644-7_0_8_node_74 | 0.4 | n |  | TRUE
124 | bus_LV_6644-7_0_8_node_70 | 0.4 | n |  | TRUE
125 | bus_LV_6644-7_0_8_node_71 | 0.4 | n |  | TRUE
126 | bus_LV_6644-7_0_8_node_69 | 0.4 | n |  | TRUE
127 | bus_LV_6644-7_0_8_node_169 | 0.4 | n |  | TRUE
128 | bus_LV_6644-7_0_8_node_105 | 0.4 | n |  | TRUE
129 | bus_LV_6644-7_0_8_node_158 | 0.4 | n |  | TRUE
130 | bus_LV_6644-7_0_8_node_154 | 0.4 | n |  | TRUE
131 | bus_LV_6644-7_0_8_node_102 | 0.4 | n |  | TRUE
132 | bus_LV_6644-7_0_8_node_98 | 0.4 | n |  | TRUE
133 | bus_LV_6644-7_0_8_node_142 | 0.4 | n |  | TRUE
134 | bus_LV_6644-7_0_8_node_166 | 0.4 | n |  | TRUE
135 | bus_LV_6644-7_0_8_node_129 | 0.4 | n |  | TRUE
136 | bus_LV_6644-7_0_8_node_148 | 0.4 | n |  | TRUE
137 | bus_LV_6644-7_0_8_node_123 | 0.4 | n |  | TRUE
138 | bus_LV_6644-7_0_8_node_67 | 0.4 | n |  | TRUE
139 | bus_LV_6644-7_0_8_node_73 | 0.4 | n |  | TRUE
140 | bus_LV_6644-7_0_8_node_80 | 0.4 | n |  | TRUE
141 | bus_LV_6644-7_0_8_node_76 | 0.4 | n |  | TRUE
142 | bus_LV_6644-7_0_8_node_81 | 0.4 | n |  | TRUE
143 | bus_LV_6644-7_0_8_node_82 | 0.4 | n |  | TRUE
144 | bus_LV_6644-7_0_8_node_83 | 0.4 | n |  | TRUE
145 | bus_LV_6644-7_0_8_node_151 | 0.4 | n |  | TRUE
146 | bus_LV_6644-7_0_8_node_152 | 0.4 | n |  | TRUE
147 | bus_LV_6644-7_0_8_node_156 | 0.4 | n |  | TRUE
148 | bus_LV_6644-7_0_8_node_157 | 0.4 | n |  | TRUE
149 | bus_LV_6644-7_0_8_node_99 | 0.4 | n |  | TRUE
150 | bus_LV_6644-7_0_8_node_101 | 0.4 | n |  | TRUE
151 | bus_LV_6644-7_0_8_node_124 | 0.4 | n |  | TRUE
152 | bus_LV_6644-7_0_8_node_119 | 0.4 | n |  | TRUE
153 | bus_LV_6644-7_0_8_node_115 | 0.4 | n |  | TRUE
154 | bus_LV_6644-7_0_8_node_117 | 0.4 | n |  | TRUE
155 | bus_LV_6644-7_0_8_node_118 | 0.4 | n |  | TRUE
156 | bus_LV_6644-7_0_8_node_120 | 0.4 | n |  | TRUE
157 | bus_LV_6644-7_0_8_node_122 | 0.4 | n |  | TRUE
158 | bus_LV_6644-7_0_8_node_130 | 0.4 | n |  | TRUE
159 | bus_LV_6644-7_0_8_node_131 | 0.4 | n |  | TRUE
160 | bus_LV_6644-7_0_8_node_132 | 0.4 | n |  | TRUE
161 | bus_LV_6644-7_0_8_node_133 | 0.4 | n |  | TRUE
162 | bus_LV_6644-7_0_8_node_134 | 0.4 | n |  | TRUE
163 | bus_LV_6644-7_0_8_node_137 | 0.4 | n |  | TRUE
164 | bus_LV_6644-7_0_8_node_138 | 0.4 | n |  | TRUE
165 | bus_LV_6644-7_0_8_node_146 | 0.4 | n |  | TRUE
166 | bus_LV_6644-7_0_8_node_147 | 0.4 | n |  | TRUE
167 | bus_LV_6644-7_0_8_node_155 | 0.4 | n |  | TRUE
168 | bus_LV_6644-7_0_8_node_171 | 0.4 | n |  | TRUE
169 | bus_LV_6644-7_0_8_node_172 | 0.4 | n |  | TRUE
170 | bus_LV_6644-7_0_8_node_167 | 0.4 | n |  | TRUE
171 | bus_MV_461_0_node_135 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6644-7_0_8_load_0 | 0 | 0.0052452 | 0.0013146 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6644-7_0_8_load_5 | 4 | 0.0052437 | 0.0013142 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6644-7_0_8_load_6 | 5 | 0.0058643 | 0.0014697 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6644-7_0_8_load_7 | 6 | 0.013159 | 0.003298 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6644-7_0_8_load_10 | 8 | 0.0075067 | 0.0018813 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6644-7_0_8_load_11 | 9 | 0.011459 | 0.002872 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6644-7_0_8_load_12 | 11 | 0.007818 | 0.0019594 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6644-7_0_8_load_14 | 12 | 0.0079936 | 0.0020034 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6644-7_0_8_load_18 | 16 | 0.0035351 | 0.00088599 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6644-7_0_8_load_84 | 17 | 0.0031678 | 0.00079392 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6644-7_0_8_load_86 | 19 | 0.0063188 | 0.0015836 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6644-7_0_8_load_72 | 22 | 0.002739 | 0.00068647 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6644-7_0_8_load_68 | 23 | 0.0016695 | 0.00041842 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6644-7_0_8_load_87 | 24 | 0.0020027 | 0.00050191 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6644-7_0_8_load_163 | 25 | 0.0066608 | 0.0016693 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6644-7_0_8_load_30 | 26 | 0.0055789 | 0.0013982 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6644-7_0_8_load_175 | 28 | 0.0032697 | 0.00081945 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6644-7_0_8_load_176 | 29 | 0.0064632 | 0.0016198 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6644-7_0_8_load_19 | 31 | 0.0078179 | 0.0019593 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6644-7_0_8_load_77 | 32 | 0.0024751 | 0.00062033 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6644-7_0_8_load_88 | 33 | 0.0022418 | 0.00056184 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6644-7_0_8_load_161 | 35 | 0.012171 | 0.0030502 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6644-7_0_8_load_173 | 38 | 0.0036232 | 0.00090805 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6644-7_0_8_load_174 | 47 | 0.013688 | 0.0034305 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6644-7_0_8_load_31 | 51 | 0.0055587 | 0.0013931 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6644-7_0_8_load_75 | 52 | 0.0064274 | 0.0016109 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6644-7_0_8_load_66 | 55 | 0.0019548 | 0.00048993 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6644-7_0_8_load_96 | 59 | 0.0026448 | 0.00066284 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6644-7_0_8_load_94 | 60 | 0.004751 | 0.0011907 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6644-7_0_8_load_109 | 63 | 0.0046405 | 0.001163 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6644-7_0_8_load_90 | 64 | 0.0082229 | 0.0020608 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6644-7_0_8_load_79 | 66 | 0.0024935 | 0.00062493 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6644-7_0_8_load_111 | 67 | 0.0027461 | 0.00068824 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6644-7_0_8_load_116 | 68 | 0.0019735 | 0.0004946 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6644-7_0_8_load_91 | 70 | 0.0026907 | 0.00067435 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6644-7_0_8_load_140 | 71 | 0.0079075 | 0.0019818 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6644-7_0_8_load_113 | 73 | 0.0017687 | 0.00044328 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6644-7_0_8_load_162 | 75 | 0.0038981 | 0.00097694 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6644-7_0_8_load_127 | 76 | 0.0029149 | 0.00073055 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6644-7_0_8_load_160 | 78 | 0.0012133 | 0.00030407 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6644-7_0_8_load_136 | 80 | 0.0011784 | 0.00029534 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6644-7_0_8_load_150 | 81 | 0.0017727 | 0.00044428 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6644-7_0_8_load_108 | 83 | 0.00798 | 0.002 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6644-7_0_8_load_126 | 84 | 0.0011358 | 0.00028466 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6644-7_0_8_load_100 | 85 | 0.023088 | 0.0057865 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6644-7_0_8_load_97 | 86 | 0.001276 | 0.00031979 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6644-7_0_8_load_143 | 87 | 0.002853 | 0.00071502 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6644-7_0_8_load_128 | 89 | 0.0033369 | 0.0008363 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6644-7_0_8_load_106 | 91 | 0.012582 | 0.0031532 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6644-7_0_8_load_107 | 92 | 0.00024456 | 6.1292e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6644-7_0_8_load_103 | 94 | 0.00027516 | 6.8961e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6644-7_0_8_load_149 | 95 | 0.00036489 | 9.1449e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6644-7_0_8_load_29 | 96 | 0.0057771 | 0.0014479 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6644-7_0_8_load_23 | 98 | 0.0037487 | 0.00093952 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6644-7_0_8_load_24 | 100 | 0.0078039 | 0.0019559 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6644-7_0_8_load_25 | 101 | 0.0064856 | 0.0016254 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6644-7_0_8_load_164 | 103 | 0.0066737 | 0.0016726 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6644-7_0_8_load_165 | 104 | 0.0084527 | 0.0021185 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6644-7_0_8_load_27 | 105 | 0.0056855 | 0.0014249 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6644-7_0_8_load_28 | 106 | 0.0054633 | 0.0013692 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6644-7_0_8_load_139 | 107 | 0.0020893 | 0.00052363 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6644-7_0_8_load_125 | 108 | 0.0017245 | 0.00043221 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6644-7_0_8_load_110 | 109 | 0.0045584 | 0.0011425 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6644-7_0_8_load_89 | 110 | 0.0017503 | 0.00043867 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6644-7_0_8_load_78 | 111 | 0.0024161 | 0.00060552 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6644-7_0_8_load_114 | 112 | 0.0040727 | 0.0010207 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6644-7_0_8_load_92 | 113 | 0.0020875 | 0.00052316 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6644-7_0_8_load_141 | 114 | 0.013163 | 0.0032989 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6644-7_0_8_load_121 | 115 | 0.0051609 | 0.0012934 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6644-7_0_8_load_93 | 117 | 0.0023352 | 0.00058527 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6644-7_0_8_load_159 | 118 | 0.001171 | 0.00029349 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6644-7_0_8_load_144 | 119 | 0.00047711 | 0.00011958 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6644-7_0_8_load_145 | 120 | 0.00045212 | 0.00011331 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6644-7_0_8_load_135 | 121 | 0.0011558 | 0.00028966 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6644-7_0_8_load_104 | 122 | 0.00097841 | 0.00024521 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6644-7_0_8_load_74 | 123 | 0.021518 | 0.0053929 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6644-7_0_8_load_71 | 125 | 0.055068 | 0.013801 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6644-7_0_8_load_169 | 127 | 0.008692 | 0.0021784 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6644-7_0_8_load_105 | 128 | 0.005893 | 0.0014769 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6644-7_0_8_load_158 | 129 | 0.0022342 | 0.00055995 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6644-7_0_8_load_154 | 130 | 0.0025199 | 0.00063154 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6644-7_0_8_load_102 | 131 | 0.0010779 | 0.00027014 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6644-7_0_8_load_98 | 132 | 0.0020031 | 0.00050203 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6644-7_0_8_load_142 | 133 | 0.0032838 | 0.000823 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6644-7_0_8_load_166 | 134 | 0.0016792 | 0.00042086 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6644-7_0_8_load_129 | 135 | 0.0044013 | 0.0011031 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6644-7_0_8_load_148 | 136 | 0.00037384 | 9.3692e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6644-7_0_8_load_123 | 137 | 0.0056725 | 0.0014217 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_6644-7_0_8_load_67 | 138 | 0.0072957 | 0.0018285 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_6644-7_0_8_load_73 | 139 | 0.0078234 | 0.0019607 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_6644-7_0_8_load_80 | 140 | 0.001831 | 0.00045889 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_6644-7_0_8_load_76 | 141 | 0.020254 | 0.0050761 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_6644-7_0_8_load_81 | 142 | 0.0017888 | 0.00044832 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_6644-7_0_8_load_82 | 143 | 0.0078079 | 0.0019568 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_6644-7_0_8_load_83 | 144 | 0.0017733 | 0.00044443 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_6644-7_0_8_load_151 | 145 | 0.0074448 | 0.0018659 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_6644-7_0_8_load_156 | 147 | 0.0062405 | 0.001564 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_6644-7_0_8_load_157 | 148 | 0.0032393 | 0.00081185 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_6644-7_0_8_load_99 | 149 | 0.0011778 | 0.00029519 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_6644-7_0_8_load_101 | 150 | 0.0014134 | 0.00035423 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_6644-7_0_8_load_124 | 151 | 0.001311 | 0.00032856 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_6644-7_0_8_load_119 | 152 | 0.0035145 | 0.00088083 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_6644-7_0_8_load_115 | 153 | 0.0023336 | 0.00058485 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_6644-7_0_8_load_117 | 154 | 0.0047548 | 0.0011917 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_6644-7_0_8_load_118 | 155 | 0.0015903 | 0.00039856 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_6644-7_0_8_load_120 | 156 | 0.0031412 | 0.00078727 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_6644-7_0_8_load_122 | 157 | 0.0052777 | 0.0013227 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_6644-7_0_8_load_130 | 158 | 0.0010936 | 0.00027409 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_6644-7_0_8_load_131 | 159 | 0.0005419 | 0.00013581 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_6644-7_0_8_load_132 | 160 | 0.014528 | 0.003641 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_6644-7_0_8_load_133 | 161 | 0.0010908 | 0.00027339 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_6644-7_0_8_load_134 | 162 | 0.0010896 | 0.00027308 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_6644-7_0_8_load_137 | 163 | 0.0010042 | 0.00025168 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_6644-7_0_8_load_138 | 164 | 0.004273 | 0.0010709 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_6644-7_0_8_load_146 | 165 | 0.00042437 | 0.00010636 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_6644-7_0_8_load_147 | 166 | 0.00018007 | 4.5129e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_6644-7_0_8_load_155 | 167 | 0.0024047 | 0.00060268 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_6644-7_0_8_load_172 | 169 | 0.00089635 | 0.00022465 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_6644-7_0_8_load_167 | 170 | 0.0014275 | 0.00035775 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6644-7_0_8_line_0 |  | 0 | 1 | 0.035399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6644-7_0_8_line_1 |  | 0 | 2 | 0.053288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6644-7_0_8_line_2 |  | 1 | 3 | 0.026456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6644-7_0_8_line_3 |  | 1 | 4 | 0.020486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6644-7_0_8_line_4 |  | 2 | 5 | 0.014746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6644-7_0_8_line_5 |  | 2 | 6 | 0.014362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6644-7_0_8_line_6 |  | 3 | 7 | 0.024346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_6644-7_0_8_line_7 |  | 3 | 8 | 0.017242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6644-7_0_8_line_8 |  | 3 | 9 | 0.016584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_6644-7_0_8_line_9 |  | 7 | 17 | 0.010128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6644-7_0_8_line_10 |  | 7 | 18 | 0.015729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_6644-7_0_8_line_11 |  | 7 | 19 | 0.009375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6644-7_0_8_line_12 |  | 9 | 20 | 0.020521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_6644-7_0_8_line_13 |  | 10 | 11 | 0.01718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6644-7_0_8_line_14 |  | 10 | 12 | 0.017638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6644-7_0_8_line_15 |  | 11 | 21 | 0.014225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6644-7_0_8_line_16 |  | 12 | 24 | 0.012969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6644-7_0_8_line_17 |  | 13 | 14 | 0.023742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6644-7_0_8_line_18 |  | 13 | 15 | 0.039931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6644-7_0_8_line_19 |  | 13 | 16 | 0.036914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6644-7_0_8_line_20 |  | 14 | 25 | 0.011727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6644-7_0_8_line_21 |  | 15 | 26 | 0.011801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6644-7_0_8_line_22 |  | 16 | 27 | 0.010001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6644-7_0_8_line_23 |  | 18 | 28 | 0.009913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6644-7_0_8_line_24 |  | 18 | 29 | 0.00959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6644-7_0_8_line_25 |  | 18 | 30 | 0.012281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_6644-7_0_8_line_26 |  | 20 | 22 | 0.025619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_6644-7_0_8_line_27 |  | 20 | 23 | 0.032629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6644-7_0_8_line_28 |  | 21 | 31 | 0.002687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6644-7_0_8_line_29 |  | 22 | 32 | 0.013244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_6644-7_0_8_line_30 |  | 24 | 33 | 0.0062901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6644-7_0_8_line_31 |  | 26 | 96 | 0.016937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6644-7_0_8_line_32 |  | 27 | 75 | 0.020263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6644-7_0_8_line_33 |  | 30 | 147 | 0.009306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6644-7_0_8_line_34 |  | 30 | 148 | 0.010197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6644-7_0_8_line_35 |  | 30 | 146 | 0.030527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_6644-7_0_8_line_36 |  | 31 | 97 | 0.019307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6644-7_0_8_line_37 |  | 32 | 141 | 0.0020502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_6644-7_0_8_line_38 |  | 33 | 110 | 0.0059137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6644-7_0_8_line_39 |  | 34 | 35 | 0.031526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6644-7_0_8_line_40 |  | 34 | 36 | 0.029064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6644-7_0_8_line_41 |  | 35 | 116 | 0.02903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6644-7_0_8_line_42 |  | 36 | 67 | 0.011339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6644-7_0_8_line_43 |  | 37 | 38 | 0.019126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6644-7_0_8_line_44 |  | 37 | 39 | 0.16347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6644-7_0_8_line_45 |  | 37 | 40 | 0.091455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6644-7_0_8_line_46 |  | 39 | 134 | 0.032477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6644-7_0_8_line_47 |  | 40 | 87 | 0.01547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6644-7_0_8_line_48 |  | 41 | 42 | 0.00769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6644-7_0_8_line_49 |  | 41 | 43 | 0.023557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_6644-7_0_8_line_50 |  | 41 | 44 | 0.026265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6644-7_0_8_line_51 |  | 41 | 45 | 0.11122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_6644-7_0_8_line_52 |  | 42 | 127 | 0.041452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6644-7_0_8_line_53 |  | 43 | 52 | 0.026172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_6644-7_0_8_line_54 |  | 44 | 71 | 0.028362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6644-7_0_8_line_55 |  | 45 | 77 | 0.020403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6644-7_0_8_line_56 |  | 45 | 78 | 0.021851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6644-7_0_8_line_57 |  | 46 | 47 | 0.005594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6644-7_0_8_line_58 |  | 46 | 48 | 0.10603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6644-7_0_8_line_59 |  | 48 | 81 | 0.006308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6644-7_0_8_line_60 |  | 48 | 82 | 0.062838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6644-7_0_8_line_61 |  | 48 | 83 | 0.018682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6644-7_0_8_line_62 |  | 49 | 50 | 0.030815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_6644-7_0_8_line_63 |  | 49 | 51 | 0.045167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_6644-7_0_8_line_64 |  | 50 | 52 | 0.01739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_6644-7_0_8_line_65 |  | 51 | 57 | 0.004095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_6644-7_0_8_line_66 |  | 53 | 54 | 0.01306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6644-7_0_8_line_67 |  | 53 | 55 | 0.012363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6644-7_0_8_line_68 |  | 53 | 56 | 0.011292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_6644-7_0_8_line_69 |  | 53 | 57 | 0.015997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_6644-7_0_8_line_70 |  | 54 | 68 | 0.0036755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6644-7_0_8_line_71 |  | 55 | 107 | 0.044453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6644-7_0_8_line_72 |  | 56 | 64 | 0.021454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6644-7_0_8_line_73 |  | 56 | 65 | 0.014183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_6644-7_0_8_line_74 |  | 58 | 59 | 0.01197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6644-7_0_8_line_75 |  | 58 | 60 | 0.0080938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6644-7_0_8_line_76 |  | 59 | 101 | 0.0082412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6644-7_0_8_line_77 |  | 60 | 69 | 0.017254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_6644-7_0_8_line_78 |  | 61 | 62 | 0.023808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6644-7_0_8_line_79 |  | 61 | 63 | 0.0094764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6644-7_0_8_line_80 |  | 62 | 108 | 0.005314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_6644-7_0_8_line_81 |  | 63 | 109 | 0.010144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6644-7_0_8_line_82 |  | 64 | 110 | 0.012668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6644-7_0_8_line_83 |  | 65 | 66 | 0.025221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_6644-7_0_8_line_84 |  | 66 | 111 | 0.012998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_6644-7_0_8_line_85 |  | 67 | 109 | 0.010108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6644-7_0_8_line_86 |  | 68 | 112 | 0.0081759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6644-7_0_8_line_87 |  | 69 | 70 | 0.0067389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_6644-7_0_8_line_88 |  | 70 | 113 | 0.01005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_6644-7_0_8_line_89 |  | 71 | 114 | 0.0025012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_6644-7_0_8_line_90 |  | 72 | 73 | 0.031643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_6644-7_0_8_line_91 |  | 72 | 74 | 0.040937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_6644-7_0_8_line_92 |  | 73 | 115 | 0.01051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_6644-7_0_8_line_93 |  | 74 | 76 | 0.013815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_6644-7_0_8_line_94 |  | 75 | 102 | 0.014003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_6644-7_0_8_line_95 |  | 76 | 88 | 0.031128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_6644-7_0_8_line_96 |  | 77 | 79 | 0.035875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_6644-7_0_8_line_97 |  | 77 | 80 | 0.0096773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_6644-7_0_8_line_98 |  | 78 | 118 | 0.0075465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_6644-7_0_8_line_99 |  | 79 | 84 | 0.02273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_6644-7_0_8_line_100 |  | 80 | 121 | 0.0014841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_6644-7_0_8_line_101 |  | 82 | 85 | 0.008304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_6644-7_0_8_line_102 |  | 82 | 86 | 0.057213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_6644-7_0_8_line_103 |  | 83 | 128 | 0.014029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_6644-7_0_8_line_104 |  | 84 | 131 | 0.0040962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_6644-7_0_8_line_105 |  | 86 | 132 | 0.0067646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_6644-7_0_8_line_106 |  | 87 | 133 | 0.012261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_6644-7_0_8_line_107 |  | 88 | 89 | 0.0054315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_6644-7_0_8_line_108 |  | 89 | 135 | 0.0093367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_6644-7_0_8_line_109 |  | 90 | 91 | 0.004034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_6644-7_0_8_line_110 |  | 90 | 92 | 0.034572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_6644-7_0_8_line_111 |  | 90 | 93 | 0.048892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_6644-7_0_8_line_112 |  | 90 | 94 | 0.019066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_6644-7_0_8_line_113 |  | 93 | 95 | 0.021251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_6644-7_0_8_line_114 |  | 94 | 122 | 0.011141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_6644-7_0_8_line_115 |  | 95 | 136 | 0.01572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_6644-7_0_8_line_116 |  | 96 | 106 | 0.016731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_6644-7_0_8_line_117 |  | 97 | 98 | 0.058186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_6644-7_0_8_line_118 |  | 98 | 102 | 0.003421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_6644-7_0_8_line_119 |  | 99 | 100 | 0.020695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_6644-7_0_8_line_120 |  | 99 | 101 | 0.015982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_6644-7_0_8_line_121 |  | 102 | 103 | 0.018081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_6644-7_0_8_line_122 |  | 103 | 104 | 7.4985e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_6644-7_0_8_line_123 |  | 104 | 168 | 0.020548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_6644-7_0_8_line_124 |  | 105 | 106 | 0.036229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_6644-7_0_8_line_125 |  | 107 | 137 | 0.015364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_6644-7_0_8_line_126 |  | 108 | 151 | 0.0071444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_6644-7_0_8_line_127 |  | 111 | 141 | 0.010956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_6644-7_0_8_line_128 |  | 112 | 153 | 0.0097362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_6644-7_0_8_line_129 |  | 113 | 117 | 0.011933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_6644-7_0_8_line_130 |  | 115 | 152 | 0.0035018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_6644-7_0_8_line_131 |  | 116 | 117 | 0.013813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_6644-7_0_8_line_132 |  | 118 | 162 | 0.0059545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_6644-7_0_8_line_133 |  | 119 | 120 | 0.0042709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_6644-7_0_8_line_134 |  | 120 | 165 | 0.034226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_6644-7_0_8_line_135 |  | 121 | 163 | 5.2067e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_6644-7_0_8_line_136 |  | 122 | 128 | 0.048863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_6644-7_0_8_line_137 |  | 123 | 124 | 0.014029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_6644-7_0_8_line_138 |  | 124 | 139 | 0.02703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_6644-7_0_8_line_139 |  | 124 | 126 | 0.008504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_6644-7_0_8_line_140 |  | 125 | 126 | 0.023774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_6644-7_0_8_line_141 |  | 126 | 138 | 0.024182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_6644-7_0_8_line_142 |  | 129 | 130 | 0.00024063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_6644-7_0_8_line_143 |  | 130 | 146 | 0.015477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_6644-7_0_8_line_144 |  | 131 | 150 | 0.0034081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_6644-7_0_8_line_145 |  | 132 | 149 | 0.068735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_6644-7_0_8_line_146 |  | 133 | 135 | 0.010391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_6644-7_0_8_line_147 |  | 134 | 170 | 0.0070417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_6644-7_0_8_line_148 |  | 136 | 166 | 0.022713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_6644-7_0_8_line_149 |  | 137 | 157 | 0.022893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_6644-7_0_8_line_150 |  | 139 | 140 | 0.023618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_6644-7_0_8_line_151 |  | 140 | 142 | 0.0058028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_6644-7_0_8_line_152 |  | 142 | 143 | 0.00065453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_6644-7_0_8_line_153 |  | 143 | 144 | 0.0050563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_6644-7_0_8_line_154 |  | 144 | 145 | 0.00067734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_6644-7_0_8_line_155 |  | 145 | 146 | 0.017142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
156 | LV_6644-7_0_8_line_156 |  | 146 | 167 | 0.013086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_6644-7_0_8_line_157 |  | 149 | 150 | 0.001122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_6644-7_0_8_line_158 |  | 151 | 155 | 0.0061953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_6644-7_0_8_line_159 |  | 152 | 156 | 0.010932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_6644-7_0_8_line_160 |  | 153 | 154 | 0.0045867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_6644-7_0_8_line_161 |  | 154 | 155 | 0.0092973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_6644-7_0_8_line_162 |  | 156 | 157 | 0.019649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_6644-7_0_8_line_163 |  | 158 | 159 | 0.0020472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_6644-7_0_8_line_164 |  | 158 | 160 | 0.0016427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_6644-7_0_8_line_165 |  | 159 | 161 | 0.0034671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_6644-7_0_8_line_166 |  | 161 | 162 | 0.01727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_6644-7_0_8_line_167 |  | 163 | 164 | 0.0036728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_6644-7_0_8_line_168 |  | 165 | 166 | 0.0072552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_6644-7_0_8_line_169 |  | 168 | 169 | 0.010891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6644-7_0_8_trafo_34 | 0.63 MVA 20/0.4 kV | 171 | 50 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30
0 | 2501789.177 | 1127275.3679 | 2501789.9445 | 1127239.9769
1 | 2501790.3472 | 1127186.694 | 2501790.3704 | 1127220.3367 | 2501789.9445 | 1127239.9769
2 | 2501789.177 | 1127275.3679 | 2501788.7594 | 1127301.8132
3 | 2501789.177 | 1127275.3679 | 2501768.6938 | 1127275.0024
4 | 2501775.5577 | 1127186.7679 | 2501788.983 | 1127186.694 | 2501790.3472 | 1127186.694
5 | 2501804.7516 | 1127186.6376 | 2501790.3472 | 1127186.694
6 | 2501788.7594 | 1127301.8132 | 2501787.2002 | 1127320.6169 | 2501787.135 | 1127326.088
7 | 2501788.7594 | 1127301.8132 | 2501771.5325 | 1127301.0946
8 | 2501788.7594 | 1127301.8132 | 2501805.3425 | 1127301.9878
9 | 2501787.135 | 1127326.088 | 2501797.2933 | 1127326.0895
10 | 2501786.9515 | 1127341.8118 | 2501787.135 | 1127326.088
11 | 2501777.7322 | 1127326.0964 | 2501787.135 | 1127326.088
12 | 2501824.375 | 1127307.4933 | 2501815.3158 | 1127302.0928 | 2501805.3425 | 1127301.9878
13 | 2501826.2517 | 1127275.9767 | 2501826.7943 | 1127263.3712 | 2501826.9358 | 1127258.8106
14 | 2501826.2517 | 1127275.9767 | 2501841.9349 | 1127276.3665 | 2501843.8843 | 1127276.3789
15 | 2501827.545 | 1127244.6029 | 2501827.2899 | 1127247.3977 | 2501826.9358 | 1127258.8106
16 | 2501843.8843 | 1127276.3789 | 2501856.8528 | 1127276.4613
17 | 2501790.309 | 1127114.2276 | 2501790.1926 | 1127090.4926
18 | 2501790.309 | 1127114.2276 | 2501754.5578 | 1127114.4981 | 2501752.981 | 1127118.4817
19 | 2501790.309 | 1127114.2276 | 2501819.3741 | 1127113.7437 | 2501822.3116 | 1127116.1642 | 2501824.2247 | 1127119.1127 | 2501824.5801 | 1127119.4975
20 | 2501778.4312 | 1127090.5172 | 2501790.1926 | 1127090.4926
21 | 2501752.981 | 1127118.4817 | 2501753.0042 | 1127130.2831
22 | 2501831.3644 | 1127126.8459 | 2501824.5801 | 1127119.4975
23 | 2501786.9515 | 1127341.8118 | 2501796.8939 | 1127341.8057
24 | 2501777.3328 | 1127341.8126 | 2501786.9515 | 1127341.8118
25 | 2501786.8121 | 1127354.0883 | 2501786.9515 | 1127341.8118
26 | 2501824.375 | 1127307.4933 | 2501832.4182 | 1127299.2353 | 2501846.5078 | 1127299.4322
27 | 2501824.375 | 1127307.4933 | 2501824.48 | 1127336.6985 | 2501824.3954 | 1127340.1211
28 | 2501827.545 | 1127244.6029 | 2501827.7878 | 1127241.9269
29 | 2501859.7509 | 1127299.6173 | 2501846.5078 | 1127299.4322
30 | 2501863.1427 | 1127276.5013 | 2501856.8528 | 1127276.4613
31 | 2501753.0042 | 1127130.2831 | 2501753.0374 | 1127147.2198
32 | 2501831.3644 | 1127126.8459 | 2501831.3521 | 1127147.1089
33 | 2501777.4787 | 1127354.0956 | 2501786.8121 | 1127354.0883
34 | 2501797.0395 | 1127354.0776 | 2501786.8121 | 1127354.0883
35 | 2501786.3683 | 1127384.6033 | 2501786.6644 | 1127366.7986 | 2501786.8121 | 1127354.0883
36 | 2501829.2696 | 1127222.6836 | 2501829.1725 | 1127226.6654 | 2501827.7878 | 1127241.9269
37 | 2501861.8009 | 1127299.646 | 2501859.7509 | 1127299.6173
38 | 2501863.1427 | 1127276.5013 | 2501869.0563 | 1127276.539
39 | 2501902.8465 | 1127130.7648 | 2501892.8352 | 1127130.8163 | 2501892.7242 | 1127152.3309
40 | 2501902.8465 | 1127130.7648 | 2501903.4223 | 1127127.3088 | 2501908.3492 | 1127127.4178 | 2501913.2277 | 1127127.3941 | 2501913.3441 | 1127133.6072 | 2501913.3141 | 1127143.1469
41 | 2501902.8513 | 1127171.3787 | 2501892.6271 | 1127171.1335 | 2501892.7242 | 1127152.3309
42 | 2501913.3141 | 1127143.1469 | 2501913.16 | 1127154.485
43 | 2502208.9429 | 1127169.6811 | 2502209.1216 | 1127188.8011
44 | 2502208.9429 | 1127169.6811 | 2502210.9532 | 1127170.071 | 2502212.368 | 1127170.3372 | 2502219.2234 | 1127171.5047 | 2502224.3089 | 1127172.3674 | 2502228.7495 | 1127172.9069 | 2502233.2616 | 1127173.5788 | 2502249.7361 | 1127176.6585 | 2502261.628 | 1127176.6105 | 2502261.2733 | 1127188.9794 | 2502260.9572 | 1127196.5892 | 2502261.0107 | 1127197.9892 | 2502267.1698 | 1127197.089 | 2502272.9019 | 1127196.9517 | 2502279.0667 | 1127197.8303 | 2502281.5383 | 1127200.0584 | 2502283.3021 | 1127203.7877 | 2502285.404 | 1127209.3682 | 2502285.9278 | 1127214.1071 | 2502284.8654 | 1127217.5153 | 2502280.6873 | 1127227.4779 | 2502277.5207 | 1127237.5465 | 2502275.8716 | 1127242.7986 | 2502273.8036 | 1127255.5066 | 2502272.8945 | 1127264.5713
45 | 2502117.5343 | 1127168.4053 | 2502196.6772 | 1127169.0126 | 2502206.6931 | 1127169.2506 | 2502208.9429 | 1127169.6811
46 | 2502272.8945 | 1127264.5713 | 2502272.6497 | 1127267.0657 | 2502273.5397 | 1127277.769 | 2502272.2279 | 1127286.2399 | 2502270.9579 | 1127296.8225
47 | 2502117.5343 | 1127168.4053 | 2502115.7694 | 1127168.4117 | 2502102.0647 | 1127168.4132
48 | 2501925.9235 | 1127401.2127 | 2501930.4562 | 1127407.4318
49 | 2501902.9462 | 1127397.7614 | 2501911.6573 | 1127398.8317 | 2501919.9856 | 1127399.1078 | 2501922.6715 | 1127399.3421 | 2501925.9235 | 1127401.2127
50 | 2501925.9235 | 1127401.2127 | 2501922.6715 | 1127399.3421 | 2501919.9856 | 1127399.1078 | 2501920.0114 | 1127395.0048 | 2501923.3245 | 1127394.9399 | 2501925.6977 | 1127394.9013 | 2501930.2437 | 1127394.8275 | 2501935.7237 | 1127394.8385
51 | 2501925.9235 | 1127401.2127 | 2501922.6715 | 1127399.3421 | 2501919.9856 | 1127399.1078 | 2501920.0778 | 1127425.1779 | 2501920.1985 | 1127461.5429 | 2501919.9985 | 1127477.2225 | 2501919.7974 | 1127495.2035 | 2501928.4606 | 1127494.7515
52 | 2501930.4562 | 1127407.4318 | 2501937.0125 | 1127416.7644 | 2501939.0097 | 1127419.2002 | 2501941.6205 | 1127420.5031 | 2501944.9343 | 1127420.9607 | 2501954.9603 | 1127420.8979 | 2501957.7413 | 1127420.3413 | 2501960.3057 | 1127419.2656 | 2501961.4245 | 1127417.9133 | 2501961.5082 | 1127414.6793
53 | 2501902.9462 | 1127397.7614 | 2501903.271 | 1127371.5917
54 | 2501935.7237 | 1127394.8385 | 2501939.0594 | 1127396.641 | 2501942.5965 | 1127398.0289 | 2501946.0283 | 1127399.1072 | 2501949.7572 | 1127399.9694 | 2501963.0973 | 1127400.3753
55 | 2501928.4606 | 1127494.7515 | 2501924.9848 | 1127503.3021 | 2501925.2049 | 1127514.4721
56 | 2501928.4606 | 1127494.7515 | 2501948.9872 | 1127487.2587
57 | 2501911.8401 | 1127733.5466 | 2501912.0542 | 1127739.1355
58 | 2501911.8401 | 1127733.5466 | 2501922.2983 | 1127733.5546 | 2501922.695 | 1127731.4023 | 2501923.1622 | 1127729.8049 | 2501923.7606 | 1127728.6834 | 2501924.6036 | 1127727.4467 | 2501925.5123 | 1127726.4535 | 2501926.7849 | 1127725.5657 | 2501928.0088 | 1127725.001 | 2501928.9911 | 1127724.7404 | 2501929.9079 | 1127724.7255 | 2501930.9598 | 1127724.9531 | 2501932.1428 | 1127725.6676 | 2501933.2056 | 1127726.5731 | 2501934.2139 | 1127728.3912 | 2501935.0631 | 1127731.3237 | 2501936.3498 | 1127738.4183 | 2501936.5268 | 1127739.8274 | 2501937.649 | 1127741.0655 | 2501938.4814 | 1127740.1181 | 2501940.5893 | 1127736.0925 | 2501942.0399 | 1127734.7792 | 2501943.3219 | 1127735.8924 | 2501944.644 | 1127737.572 | 2501946.7819 | 1127740.1389 | 2501948.8654 | 1127739.8271 | 2501950.2624 | 1127739.482 | 2501954.1816 | 1127737.8396 | 2501958.1605 | 1127736.0739 | 2501969.8256 | 1127762.4675 | 2501976.7997 | 1127759.5859
59 | 2501982.6566 | 1127757.2005 | 2501976.7997 | 1127759.5859
60 | 2501952.4533 | 1127701.6564 | 2501958.9916 | 1127717.4934 | 2501965.5303 | 1127732.8856 | 2501976.7997 | 1127759.5859
61 | 2501976.7997 | 1127759.5859 | 2501984.1822 | 1127776.7476
62 | 2501903.4869 | 1127354.2035 | 2501911.1337 | 1127354.2794 | 2501911.4295 | 1127339.7545 | 2501920.0695 | 1127339.7586
63 | 2501920.0695 | 1127339.7586 | 2501919.3356 | 1127328.7415 | 2501918.7702 | 1127309.1275 | 2501918.4685 | 1127294.6275
64 | 2501903.4869 | 1127354.2035 | 2501903.271 | 1127371.5917
65 | 2501918.3833 | 1127290.5334 | 2501918.4685 | 1127294.6275
66 | 2501914.2094 | 1127275.0916 | 2501913.3504 | 1127271.0809 | 2501912.8428 | 1127262.1392
67 | 2501914.2094 | 1127275.0916 | 2501920.1361 | 1127274.1281 | 2501926.4943 | 1127274.1355
68 | 2501914.2094 | 1127275.0916 | 2501908.8571 | 1127276.7796 | 2501903.1768 | 1127276.7829
69 | 2501914.2094 | 1127275.0916 | 2501918.3833 | 1127290.5334
70 | 2501912.8428 | 1127262.1392 | 2501912.8427 | 1127258.4637
71 | 2501970.9472 | 1127274.1836 | 2501941.2239 | 1127274.1524 | 2501926.4943 | 1127274.1355
72 | 2501903.1768 | 1127276.7829 | 2501896.9944 | 1127276.7166 | 2501881.7237 | 1127276.6195
73 | 2501902.991 | 1127290.9614 | 2501903.1768 | 1127276.7829
74 | 2501903.1297 | 1127239.2605 | 2501891.1599 | 1127239.2549 | 2501891.1599 | 1127239.2549
75 | 2501903.1297 | 1127239.2605 | 2501903.0941 | 1127231.1668
76 | 2501891.1599 | 1127239.2549 | 2501891.1381 | 1127237.91 | 2501886.6989 | 1127237.9266 | 2501884.242 | 1127237.9234
77 | 2501903.0184 | 1127213.9133 | 2501903.0941 | 1127231.1668
78 | 2501912.9023 | 1127184.2123 | 2501912.887 | 1127188.9599 | 2501912.6957 | 1127208.0192
79 | 2501912.9023 | 1127184.2123 | 2501912.9785 | 1127174.7362
80 | 2501912.6957 | 1127208.0192 | 2501912.8061 | 1127213.3321
81 | 2501913.06 | 1127164.592 | 2501912.9785 | 1127174.7362
82 | 2501869.0563 | 1127276.539 | 2501881.7237 | 1127276.6195
83 | 2501902.991 | 1127290.9614 | 2501898.6989 | 1127291.02 | 2501898.6111 | 1127295.1017 | 2501896.0603 | 1127295.121 | 2501893.7326 | 1127295.1143 | 2501893.6222 | 1127298.2847 | 2501892.3565 | 1127300.0731 | 2501885.753 | 1127299.9808
84 | 2501872.7559 | 1127299.7991 | 2501885.753 | 1127299.9808
85 | 2501913.16 | 1127154.485 | 2501913.114 | 1127157.8703 | 2501913.06 | 1127164.592
86 | 2501912.8427 | 1127258.4637 | 2501912.8425 | 1127250.7321 | 2501912.8469 | 1127250.2878
87 | 2501903.0184 | 1127213.9133 | 2501902.9875 | 1127207.1745
88 | 2501902.9875 | 1127207.1745 | 2501902.9415 | 1127197.1246
89 | 2501963.0643 | 1127397.8743 | 2501963.0973 | 1127400.3753
90 | 2501985.585 | 1127174.3041 | 2501986.5848 | 1127205.9309
91 | 2501985.585 | 1127174.3041 | 2501985.552 | 1127167.5227 | 2501995.9609 | 1127167.7539 | 2502012.4569 | 1127167.8753 | 2502019.7037 | 1127167.98
92 | 2501986.7617 | 1127216.4383 | 2501986.7259 | 1127210.3968 | 2501986.5848 | 1127205.9309
93 | 2502019.7037 | 1127167.98 | 2502033.5176 | 1127168.1754
94 | 2501831.3436 | 1127161.1118 | 2501831.3521 | 1127147.1089
95 | 2502064.6449 | 1127168.3737 | 2502041.6674 | 1127168.2907 | 2502033.5176 | 1127168.1754
96 | 2501919.9031 | 1127541.5526 | 2501919.7209 | 1127524.6452 | 2501919.6361 | 1127511.8386 | 2501925.2049 | 1127514.4721
97 | 2501925.2049 | 1127514.4721 | 2501926.7251 | 1127520.2843 | 2501928.1719 | 1127523.6565
98 | 2501948.9872 | 1127487.2587 | 2501956.0762 | 1127484.671
99 | 2501919.9031 | 1127541.5526 | 2501920.7499 | 1127555.7254 | 2501921.5635 | 1127564.2186
100 | 2501928.757 | 1127525.0204 | 2501928.1719 | 1127523.6565
101 | 2501960.2837 | 1127698.8275 | 2501952.4533 | 1127701.6564
102 | 2501952.4533 | 1127701.6564 | 2501946.999 | 1127687.0804 | 2501939.2541 | 1127661.9684 | 2501935.3964 | 1127647.0891
103 | 2501984.1822 | 1127776.7476 | 2501989.7261 | 1127789.6349
104 | 2501921.954 | 1127568.2962 | 2501921.5635 | 1127564.2186
105 | 2501935.3964 | 1127647.0891 | 2501933.6986 | 1127640.541
106 | 2502089.8035 | 1127168.4145 | 2502102.0647 | 1127168.4132
107 | 2502064.6449 | 1127168.3737 | 2502070.0763 | 1127168.3932
108 | 2502079.4129 | 1127168.4156 | 2502076.4303 | 1127168.416 | 2502070.0763 | 1127168.3932
109 | 2502025.2363 | 1127862.1188 | 2502021.1912 | 1127862.1734
110 | 2502034.571 | 1127894.0538 | 2502030.8255 | 1127884.5531 | 2502021.1912 | 1127862.1734
111 | 2501993.5226 | 1127884.8474 | 2501997.8038 | 1127884.6222 | 2502002.4718 | 1127883.5347 | 2502011.4087 | 1127880.0431 | 2502018.0928 | 1127874.4979 | 2502012.8636 | 1127862.3753 | 2502021.1912 | 1127862.1734
112 | 2502021.1912 | 1127862.1734 | 2502013.6686 | 1127844.6537
113 | 2501993.5226 | 1127884.8474 | 2501992.5832 | 1127884.896 | 2501972.2754 | 1127885.2441
114 | 2502013.6686 | 1127844.6537 | 2502009.2731 | 1127834.4168
115 | 2501956.5579 | 1127885.5134 | 2501972.2754 | 1127885.2441
116 | 2501753.0374 | 1127147.2198 | 2501753.0703 | 1127163.9506
117 | 2501829.2696 | 1127222.6836 | 2501829.4627 | 1127215.1313 | 2501831.2245 | 1127164.5307
118 | 2501831.3436 | 1127161.1118 | 2501831.2245 | 1127164.5307
119 | 2501868.2607 | 1127237.8038 | 2501868.3231 | 1127229.7867 | 2501863.5446 | 1127225.5284 | 2501857.2416 | 1127225.6308
120 | 2501868.2607 | 1127237.8038 | 2501884.1631 | 1127237.9233 | 2501884.242 | 1127237.9234
121 | 2501831.3436 | 1127161.1118 | 2501849.4242 | 1127161.2178
122 | 2501849.4992 | 1127161.2182 | 2501849.4242 | 1127161.2178
123 | 2501870.0468 | 1127161.3386 | 2501849.4992 | 1127161.2182
124 | 2501753.0703 | 1127163.9506 | 2501753.1415 | 1127200.1799
125 | 2501970.9472 | 1127274.1836 | 2501983.6692 | 1127274.1969 | 2501986.1115 | 1127273.19 | 2501986.1115 | 1127273.19
126 | 2501912.8061 | 1127213.3321 | 2501912.9547 | 1127220.4749
127 | 2501872.7559 | 1127299.7991 | 2501861.8009 | 1127299.646
128 | 2501912.9444 | 1127240.5521 | 2501912.8469 | 1127250.2878
129 | 2501902.8869 | 1127185.1917 | 2501902.9415 | 1127197.1246
130 | 2501986.7617 | 1127216.4383 | 2501986.7824 | 1127219.94
131 | 2501902.8513 | 1127171.3787 | 2501902.8491 | 1127176.9377 | 2501902.8869 | 1127185.1917
132 | 2501956.0762 | 1127484.671 | 2501961.6698 | 1127482.6292
133 | 2501888.1035 | 1127886.7333 | 2501892.3736 | 1127886.6467
134 | 2501926.5936 | 1127886.027 | 2501918.1042 | 1127886.1725 | 2501903.535 | 1127886.4204 | 2501892.3736 | 1127886.6467
135 | 2501928.7776 | 1127525.0683 | 2501928.757 | 1127525.0204
136 | 2502009.2731 | 1127834.4168 | 2502006.3336 | 1127827.5708 | 2501992.8578 | 1127796.915 | 2501989.7261 | 1127789.6349
137 | 2501828.2581 | 1127423.9911 | 2501830.0303 | 1127429.1766 | 2501833.0228 | 1127437.1844
138 | 2501828.2581 | 1127423.9911 | 2501801.2277 | 1127424.0135
139 | 2501825.2845 | 1127416.0234 | 2501827.0646 | 1127420.7418 | 2501828.2581 | 1127423.9911
140 | 2501825.2845 | 1127416.0234 | 2501849.0559 | 1127415.6924
141 | 2501825.2845 | 1127416.0234 | 2501821.7008 | 1127405.1304 | 2501820.0582 | 1127398.9088 | 2501819.3595 | 1127392.6681
142 | 2501770.8976 | 1127385.0264 | 2501770.6571 | 1127385.033
143 | 2501786.3683 | 1127384.6033 | 2501770.8976 | 1127385.0264
144 | 2501922.279 | 1127571.6887 | 2501921.954 | 1127568.2962
145 | 2501922.386 | 1127572.8056 | 2501922.532 | 1127574.3302 | 2501925.5652 | 1127599.7411 | 2501928.5122 | 1127616.5258 | 2501933.252 | 1127638.8182 | 2501933.6986 | 1127640.541
146 | 2502079.4129 | 1127168.4156 | 2502089.8035 | 1127168.4145
147 | 2502272.3326 | 1127303.6601 | 2502271.3603 | 1127301.2076 | 2502270.9579 | 1127296.8225
148 | 2501933.8477 | 1127885.9027 | 2501956.5579 | 1127885.5134
149 | 2501986.9632 | 1127250.5214 | 2501987.0039 | 1127257.4213 | 2501987.1314 | 1127270.9721 | 2501986.1115 | 1127273.19
150 | 2501801.2277 | 1127424.0135 | 2501789.3681 | 1127424.0233 | 2501789.1903 | 1127419.2566 | 2501785.8108 | 1127416.6544 | 2501785.8595 | 1127413.9317
151 | 2501785.8595 | 1127413.9317 | 2501785.9632 | 1127408.1298
152 | 2501785.9749 | 1127407.4754 | 2501785.9632 | 1127408.1298
153 | 2501785.9749 | 1127407.4754 | 2501786.0652 | 1127402.4199
154 | 2501786.0773 | 1127401.7427 | 2501786.0652 | 1127402.4199
155 | 2501786.3683 | 1127384.6033 | 2501786.3272 | 1127387.7614 | 2501786.0773 | 1127401.7427
156 | 2501799.4879 | 1127384.2453 | 2501786.3683 | 1127384.6033
157 | 2501922.279 | 1127571.6887 | 2501922.386 | 1127572.8056
158 | 2501913.0835 | 1127226.6689 | 2501913.0835 | 1127226.6689 | 2501912.9547 | 1127220.4749
159 | 2501986.8471 | 1127230.8722 | 2501986.7824 | 1127219.94
160 | 2501912.9444 | 1127240.5521 | 2501912.9904 | 1127235.9657
161 | 2501912.9904 | 1127235.9657 | 2501913.0835 | 1127226.6689
162 | 2501986.9632 | 1127250.5214 | 2501986.9291 | 1127244.748 | 2501986.8471 | 1127230.8722
163 | 2501982.6598 | 1127473.8669 | 2501980.8342 | 1127474.7933
164 | 2501984.1246 | 1127473.1235 | 2501982.6598 | 1127473.8669
165 | 2501977.7425 | 1127476.3624 | 2501980.8342 | 1127474.7933
166 | 2501961.6698 | 1127482.6292 | 2501974.9363 | 1127477.7866 | 2501977.7425 | 1127476.3624
167 | 2501930.2257 | 1127528.4436 | 2501928.7776 | 1127525.0683
168 | 2501926.5936 | 1127886.027 | 2501933.8477 | 1127885.9027
169 | 2501870.0468 | 1127161.3386 | 2501869.9077 | 1127172.2254

## bus_geodata
| x | y | coords
0 | 2501789.9445 | 1127239.9769
1 | 2501789.177 | 1127275.3679
2 | 2501790.3472 | 1127186.694
3 | 2501788.7594 | 1127301.8132
4 | 2501768.6938 | 1127275.0024
5 | 2501775.5577 | 1127186.7679
6 | 2501804.7516 | 1127186.6376
7 | 2501787.135 | 1127326.088
8 | 2501771.5325 | 1127301.0946
9 | 2501805.3425 | 1127301.9878
10 | 2501826.2517 | 1127275.9767
11 | 2501826.9358 | 1127258.8106
12 | 2501843.8843 | 1127276.3789
13 | 2501790.309 | 1127114.2276
14 | 2501790.1926 | 1127090.4926
15 | 2501752.981 | 1127118.4817
16 | 2501824.5801 | 1127119.4975
17 | 2501797.2933 | 1127326.0895
18 | 2501786.9515 | 1127341.8118
19 | 2501777.7322 | 1127326.0964
20 | 2501824.375 | 1127307.4933
21 | 2501827.545 | 1127244.6029
22 | 2501846.5078 | 1127299.4322
23 | 2501824.3954 | 1127340.1211
24 | 2501856.8528 | 1127276.4613
25 | 2501778.4312 | 1127090.5172
26 | 2501753.0042 | 1127130.2831
27 | 2501831.3644 | 1127126.8459
28 | 2501796.8939 | 1127341.8057
29 | 2501777.3328 | 1127341.8126
30 | 2501786.8121 | 1127354.0883
31 | 2501827.7878 | 1127241.9269
32 | 2501859.7509 | 1127299.6173
33 | 2501863.1427 | 1127276.5013
34 | 2501902.8465 | 1127130.7648
35 | 2501892.7242 | 1127152.3309
36 | 2501913.3141 | 1127143.1469
37 | 2502208.9429 | 1127169.6811
38 | 2502209.1216 | 1127188.8011
39 | 2502272.8945 | 1127264.5713
40 | 2502117.5343 | 1127168.4053
41 | 2501925.9235 | 1127401.2127
42 | 2501930.4562 | 1127407.4318
43 | 2501902.9462 | 1127397.7614
44 | 2501935.7237 | 1127394.8385
45 | 2501928.4606 | 1127494.7515
46 | 2501911.8401 | 1127733.5466
47 | 2501912.0542 | 1127739.1355
48 | 2501976.7997 | 1127759.5859
49 | 2501920.0695 | 1127339.7586
50 | 2501903.4869 | 1127354.2035
51 | 2501918.4685 | 1127294.6275
52 | 2501903.271 | 1127371.5917
53 | 2501914.2094 | 1127275.0916
54 | 2501912.8428 | 1127262.1392
55 | 2501926.4943 | 1127274.1355
56 | 2501903.1768 | 1127276.7829
57 | 2501918.3833 | 1127290.5334
58 | 2501903.1297 | 1127239.2605
59 | 2501891.1599 | 1127239.2549
60 | 2501903.0941 | 1127231.1668
61 | 2501912.9023 | 1127184.2123
62 | 2501912.6957 | 1127208.0192
63 | 2501912.9785 | 1127174.7362
64 | 2501881.7237 | 1127276.6195
65 | 2501902.991 | 1127290.9614
66 | 2501885.753 | 1127299.9808
67 | 2501913.16 | 1127154.485
68 | 2501912.8427 | 1127258.4637
69 | 2501903.0184 | 1127213.9133
70 | 2501902.9875 | 1127207.1745
71 | 2501963.0973 | 1127400.3753
72 | 2501985.585 | 1127174.3041
73 | 2501986.5848 | 1127205.9309
74 | 2502019.7037 | 1127167.98
75 | 2501831.3521 | 1127147.1089
76 | 2502033.5176 | 1127168.1754
77 | 2501925.2049 | 1127514.4721
78 | 2501948.9872 | 1127487.2587
79 | 2501919.9031 | 1127541.5526
80 | 2501928.1719 | 1127523.6565
81 | 2501982.6566 | 1127757.2005
82 | 2501952.4533 | 1127701.6564
83 | 2501984.1822 | 1127776.7476
84 | 2501921.5635 | 1127564.2186
85 | 2501960.2837 | 1127698.8275
86 | 2501935.3964 | 1127647.0891
87 | 2502102.0647 | 1127168.4132
88 | 2502064.6449 | 1127168.3737
89 | 2502070.0763 | 1127168.3932
90 | 2502021.1912 | 1127862.1734
91 | 2502025.2363 | 1127862.1188
92 | 2502034.571 | 1127894.0538
93 | 2501993.5226 | 1127884.8474
94 | 2502013.6686 | 1127844.6537
95 | 2501972.2754 | 1127885.2441
96 | 2501753.0374 | 1127147.2198
97 | 2501829.2696 | 1127222.6836
98 | 2501831.2245 | 1127164.5307
99 | 2501868.2607 | 1127237.8038
100 | 2501857.2416 | 1127225.6308
101 | 2501884.242 | 1127237.9234
102 | 2501831.3436 | 1127161.1118
103 | 2501849.4242 | 1127161.2178
104 | 2501849.4992 | 1127161.2182
105 | 2501753.1415 | 1127200.1799
106 | 2501753.0703 | 1127163.9506
107 | 2501970.9472 | 1127274.1836
108 | 2501912.8061 | 1127213.3321
109 | 2501913.06 | 1127164.592
110 | 2501869.0563 | 1127276.539
111 | 2501872.7559 | 1127299.7991
112 | 2501912.8469 | 1127250.2878
113 | 2501902.9415 | 1127197.1246
114 | 2501963.0643 | 1127397.8743
115 | 2501986.7617 | 1127216.4383
116 | 2501902.8513 | 1127171.3787
117 | 2501902.8869 | 1127185.1917
118 | 2501956.0762 | 1127484.671
119 | 2501888.1035 | 1127886.7333
120 | 2501892.3736 | 1127886.6467
121 | 2501928.757 | 1127525.0204
122 | 2502009.2731 | 1127834.4168
123 | 2501833.0228 | 1127437.1844
124 | 2501828.2581 | 1127423.9911
125 | 2501849.0559 | 1127415.6924
126 | 2501825.2845 | 1127416.0234
127 | 2501961.5082 | 1127414.6793
128 | 2501989.7261 | 1127789.6349
129 | 2501770.6571 | 1127385.033
130 | 2501770.8976 | 1127385.0264
131 | 2501921.954 | 1127568.2962
132 | 2501933.6986 | 1127640.541
133 | 2502089.8035 | 1127168.4145
134 | 2502270.9579 | 1127296.8225
135 | 2502079.4129 | 1127168.4156
136 | 2501956.5579 | 1127885.5134
137 | 2501986.1115 | 1127273.19
138 | 2501819.3595 | 1127392.6681
139 | 2501801.2277 | 1127424.0135
140 | 2501785.8595 | 1127413.9317
141 | 2501861.8009 | 1127299.646
142 | 2501785.9632 | 1127408.1298
143 | 2501785.9749 | 1127407.4754
144 | 2501786.0652 | 1127402.4199
145 | 2501786.0773 | 1127401.7427
146 | 2501786.3683 | 1127384.6033
147 | 2501777.4787 | 1127354.0956
148 | 2501797.0395 | 1127354.0776
149 | 2501922.386 | 1127572.8056
150 | 2501922.279 | 1127571.6887
151 | 2501912.9547 | 1127220.4749
152 | 2501986.7824 | 1127219.94
153 | 2501912.9444 | 1127240.5521
154 | 2501912.9904 | 1127235.9657
155 | 2501913.0835 | 1127226.6689
156 | 2501986.8471 | 1127230.8722
157 | 2501986.9632 | 1127250.5214
158 | 2501982.6598 | 1127473.8669
159 | 2501980.8342 | 1127474.7933
160 | 2501984.1246 | 1127473.1235
161 | 2501977.7425 | 1127476.3624
162 | 2501961.6698 | 1127482.6292
163 | 2501928.7776 | 1127525.0683
164 | 2501930.2257 | 1127528.4436
165 | 2501926.5936 | 1127886.027
166 | 2501933.8477 | 1127885.9027
167 | 2501799.4879 | 1127384.2453
168 | 2501870.0468 | 1127161.3386
169 | 2501869.9077 | 1127172.2254
170 | 2502272.3326 | 1127303.6601
171 | 2501911.1337 | 1127354.2794

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1