## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6644-8_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6644-8_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6644-8_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6644-8_0_3_node_13 | 0.4 | n |  | TRUE
4 | bus_LV_6644-8_0_3_node_18 | 0.4 | n |  | TRUE
5 | bus_LV_6644-8_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6644-8_0_3_node_52 | 0.4 | n |  | TRUE
7 | bus_LV_6644-8_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_6644-8_0_3_node_48 | 0.4 | n |  | TRUE
9 | bus_LV_6644-8_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_6644-8_0_3_node_59 | 0.4 | n |  | TRUE
11 | bus_LV_6644-8_0_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_6644-8_0_3_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_6644-8_0_3_node_63 | 0.4 | n |  | TRUE
14 | bus_LV_6644-8_0_3_node_61 | 0.4 | n |  | TRUE
15 | bus_LV_6644-8_0_3_node_65 | 0.4 | n |  | TRUE
16 | bus_LV_6644-8_0_3_node_55 | 0.4 | n |  | TRUE
17 | bus_LV_6644-8_0_3_node_58 | 0.4 | n |  | TRUE
18 | bus_LV_6644-8_0_3_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_6644-8_0_3_node_56 | 0.4 | n |  | TRUE
20 | bus_LV_6644-8_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_6644-8_0_3_node_50 | 0.4 | n |  | TRUE
22 | bus_LV_6644-8_0_3_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_6644-8_0_3_node_64 | 0.4 | n |  | TRUE
24 | bus_LV_6644-8_0_3_node_60 | 0.4 | n |  | TRUE
25 | bus_LV_6644-8_0_3_node_57 | 0.4 | n |  | TRUE
26 | bus_LV_6644-8_0_3_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_6644-8_0_3_node_49 | 0.4 | n |  | TRUE
28 | bus_LV_6644-8_0_3_node_51 | 0.4 | n |  | TRUE
29 | bus_LV_6644-8_0_3_node_53 | 0.4 | n |  | TRUE
30 | bus_LV_6644-8_0_3_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_6644-8_0_3_node_67 | 0.4 | n |  | TRUE
32 | bus_LV_6644-8_0_3_node_62 | 0.4 | n |  | TRUE
33 | bus_LV_6644-8_0_3_node_66 | 0.4 | n |  | TRUE
34 | bus_MV_461_0_node_85 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6644-8_0_3_load_0 | 0 | 0.00050729 | 0.00012714 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6644-8_0_3_load_52 | 6 | 7.0879e-05 | 1.7764e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6644-8_0_3_load_59 | 10 | 0.0020917 | 0.00052423 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6644-8_0_3_load_61 | 14 | 0.00017248 | 4.3228e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6644-8_0_3_load_65 | 15 | 0.01254 | 0.0031428 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6644-8_0_3_load_55 | 16 | 0.0018347 | 0.00045981 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6644-8_0_3_load_58 | 17 | 0.00039184 | 9.8203e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6644-8_0_3_load_19 | 20 | 0.00013528 | 3.3905e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6644-8_0_3_load_46 | 22 | 0.0097707 | 0.0024488 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6644-8_0_3_load_64 | 23 | 0.00010203 | 2.5572e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6644-8_0_3_load_60 | 24 | 0.00047933 | 0.00012013 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6644-8_0_3_load_57 | 25 | 0.00050236 | 0.0001259 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6644-8_0_3_load_47 | 26 | 0.016988 | 0.0042577 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6644-8_0_3_load_49 | 27 | 5.9934e-05 | 1.5021e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6644-8_0_3_load_51 | 28 | 0.00013769 | 3.4509e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6644-8_0_3_load_53 | 29 | 0.028371 | 0.0071105 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6644-8_0_3_load_54 | 30 | 0.012392 | 0.0031059 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6644-8_0_3_load_67 | 31 | 0.011753 | 0.0029456 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6644-8_0_3_load_62 | 32 | 0.00026599 | 6.6662e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6644-8_0_3_load_66 | 33 | 8.0966e-05 | 2.0292e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6644-8_0_3_line_0 |  | 0 | 1 | 0.020881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_6644-8_0_3_line_1 |  | 0 | 2 | 0.02623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_6644-8_0_3_line_2 |  | 1 | 3 | 0.53744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_6644-8_0_3_line_3 |  | 2 | 4 | 0.19488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_6644-8_0_3_line_4 |  | 3 | 16 | 0.0016753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6644-8_0_3_line_5 |  | 3 | 9 | 0.54825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_6644-8_0_3_line_6 |  | 4 | 20 | 0.011922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6644-8_0_3_line_7 |  | 4 | 7 | 0.47917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_6644-8_0_3_line_8 |  | 5 | 6 | 0.02949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6644-8_0_3_line_9 |  | 5 | 7 | 0.2622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_6644-8_0_3_line_10 |  | 5 | 8 | 0.098891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_6644-8_0_3_line_11 |  | 7 | 13 | 0.24676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6644-8_0_3_line_12 |  | 7 | 14 | 0.052933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6644-8_0_3_line_13 |  | 8 | 21 | 0.005114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_6644-8_0_3_line_14 |  | 8 | 22 | 0.024566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6644-8_0_3_line_15 |  | 9 | 10 | 0.018589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6644-8_0_3_line_16 |  | 9 | 11 | 0.64354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_6644-8_0_3_line_17 |  | 9 | 12 | 0.037316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6644-8_0_3_line_18 |  | 11 | 15 | 0.67599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6644-8_0_3_line_19 |  | 12 | 17 | 0.0075628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6644-8_0_3_line_20 |  | 13 | 23 | 0.1138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6644-8_0_3_line_21 |  | 14 | 24 | 0.034148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6644-8_0_3_line_22 |  | 16 | 18 | 0.0049028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6644-8_0_3_line_23 |  | 18 | 19 | 0.026175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6644-8_0_3_line_24 |  | 19 | 25 | 0.01431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6644-8_0_3_line_25 |  | 21 | 29 | 0.058881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6644-8_0_3_line_26 |  | 21 | 30 | 0.015183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_6644-8_0_3_line_27 |  | 22 | 26 | 0.0061096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6644-8_0_3_line_28 |  | 23 | 33 | 0.0044088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6644-8_0_3_line_29 |  | 24 | 32 | 0.025293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6644-8_0_3_line_30 |  | 26 | 27 | 0.0015061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6644-8_0_3_line_31 |  | 27 | 28 | 0.039463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6644-8_0_3_line_32 |  | 30 | 31 | 0.012294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6644-8_0_3_trafo_54 | 0.63 MVA 20/0.4 kV | 34 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33
0 | 2499933.7494 | 1127727.0681 | 2499921.8133 | 1127709.9345
1 | 2499903.3501 | 1127691.5497 | 2499906.1339 | 1127693.5047 | 2499912.1024 | 1127698.3533 | 2499919.2624 | 1127706.2729 | 2499921.8133 | 1127709.9345
2 | 2499933.7494 | 1127727.0681 | 2499933.0488 | 1127727.58 | 2499930.1961 | 1127728.4389 | 2499954.6332 | 1127763.6894 | 2499956.0403 | 1127767.6797 | 2499955.2873 | 1127778.51 | 2499954.7724 | 1127782.3209 | 2499954.0348 | 1127785.713 | 2499952.6592 | 1127791.9953 | 2499977.8509 | 1127828.1561 | 2499987.0481 | 1127841.3676 | 2500123.7475 | 1128037.7501 | 2500125.218 | 1128021.8269 | 2500126.3726 | 1128006.376 | 2500126.9399 | 1127998.7397 | 2500131.1345 | 1127949.9733 | 2500133.0413 | 1127947.8404 | 2500134.5479 | 1127946.6703 | 2500137.4064 | 1127945.2333 | 2500139.2015 | 1127945.2036 | 2500141.7108 | 1127945.4845 | 2500143.8884 | 1127946.2156 | 2500145.3406 | 1127947.3479 | 2500146.3081 | 1127948.5326 | 2500147.167 | 1127950.1416 | 2500147.5327 | 1127952.2147 | 2500147.6021 | 1127963.3982 | 2500147.7537 | 1127969.2994 | 2500148.1139 | 1127972.9068 | 2500148.6658 | 1127975.0546 | 2500149.258 | 1127976.8459 | 2500150.4486 | 1127978.9386 | 2500154.8837 | 1127984.7578 | 2500167.85 | 1127997.1067
3 | 2499765.0554 | 1127621.3771 | 2499774.5642 | 1127614.3149 | 2499784.5886 | 1127608.1336 | 2499813.0734 | 1127591.8509 | 2499853.9023 | 1127650.1991 | 2499864.2067 | 1127652.0628 | 2499868.3776 | 1127654.4729 | 2499887.5662 | 1127681.7829 | 2499899.8565 | 1127689.0838 | 2499903.3501 | 1127691.5497
4 | 2500167.85 | 1127997.1067 | 2500169.272 | 1127997.9925
5 | 2500051.4317 | 1128304.9905 | 2500066.1451 | 1128291.6387 | 2500067.4605 | 1128291.0277 | 2500071.6109 | 1128296.8849 | 2500176.6919 | 1128209.2815 | 2500182.1562 | 1128204.655 | 2500218.4069 | 1128173.9146 | 2500215.9287 | 1128170.3756 | 2500205.3993 | 1128155.3068 | 2500154.6533 | 1128082.1778 | 2500123.7475 | 1128037.7501 | 2500125.218 | 1128021.8269 | 2500126.3726 | 1128006.376 | 2500126.9399 | 1127998.7397 | 2500131.1345 | 1127949.9733 | 2500133.0413 | 1127947.8404 | 2500134.5479 | 1127946.6703 | 2500137.4064 | 1127945.2333 | 2500139.2015 | 1127945.2036 | 2500141.7108 | 1127945.4845 | 2500143.8884 | 1127946.2156 | 2500145.3406 | 1127947.3479 | 2500146.3081 | 1127948.5326 | 2500147.167 | 1127950.1416 | 2500147.5327 | 1127952.2147 | 2500147.6021 | 1127963.3982 | 2500147.7537 | 1127969.2994 | 2500148.1139 | 1127972.9068 | 2500148.6658 | 1127975.0546 | 2500149.258 | 1127976.8459 | 2500150.4486 | 1127978.9386 | 2500154.8837 | 1127984.7578 | 2500167.85 | 1127997.1067
6 | 2499765.0554 | 1127621.3771 | 2499756.0964 | 1127629.0639 | 2499756.0153 | 1127629.1486
7 | 2499765.0554 | 1127621.3771 | 2499774.5642 | 1127614.3149 | 2499784.5886 | 1127608.1336 | 2499813.0734 | 1127591.8509 | 2499824.6063 | 1127585.0776 | 2499830.6636 | 1127581.7974 | 2499835.7397 | 1127579.3005 | 2499849.1981 | 1127573.3737 | 2499885.893 | 1127556.7328 | 2499959.8659 | 1127522.786 | 2500005.3866 | 1127499.6623 | 2500049.0043 | 1127473.3017 | 2500107.0964 | 1127439.9422 | 2500045.7346 | 1127372.1818
8 | 2500168.6118 | 1127341.3749 | 2500167.053 | 1127331.9393 | 2500166.6249 | 1127323.2965 | 2500166.2998 | 1127312.0282
9 | 2500045.7346 | 1127372.1818 | 2500107.0964 | 1127439.9422 | 2500122.1411 | 1127431.566 | 2500143.3457 | 1127421.4313 | 2500163.8698 | 1127413.954 | 2500199.6759 | 1127404.979 | 2500196.434 | 1127397.2277 | 2500176.0668 | 1127364.3327 | 2500173.0722 | 1127357.5557 | 2500170.6944 | 1127350.3239 | 2500168.6118 | 1127341.3749
10 | 2500168.6118 | 1127341.3749 | 2500181.318 | 1127340.242 | 2500208.474 | 1127330.1648 | 2500237.6431 | 1127314.5733 | 2500260.1336 | 1127305.2628
11 | 2500045.7346 | 1127372.1818 | 2499923.6024 | 1127237.7202 | 2499911.4298 | 1127223.1573 | 2499901.8031 | 1127210.609 | 2499894.0359 | 1127200.0422 | 2499886.5456 | 1127186.6469 | 2499885.6429 | 1127184.7384
12 | 2500045.7346 | 1127372.1818 | 2500063.8296 | 1127341.8079 | 2500068.583 | 1127334.2356 | 2500073.3528 | 1127327.1857 | 2500073.4228 | 1127327.0816
13 | 2500264.8722 | 1127303.3056 | 2500260.1336 | 1127305.2628
14 | 2500260.1336 | 1127305.2628 | 2500260.5458 | 1127300.3529 | 2500259.8383 | 1127294.8501 | 2500258.0458 | 1127292.7228 | 2500256.0597 | 1127291.4659 | 2500253.0907 | 1127289.9696 | 2500250.3599 | 1127287.4909 | 2500249.2723 | 1127285.878
15 | 2500033.4346 | 1128300.1409 | 2500051.4317 | 1128304.9905
16 | 2500051.4317 | 1128304.9905 | 2500066.1451 | 1128291.6387 | 2500067.4605 | 1128291.0277 | 2500071.6109 | 1128296.8849 | 2500176.6919 | 1128209.2815 | 2500182.1562 | 1128204.655 | 2500218.4069 | 1128173.9146 | 2500361.2275 | 1128057.1841 | 2500366.6187 | 1128052.7814 | 2500370.8089 | 1128040.5157 | 2500372.9028 | 1128028.7072 | 2500374.6218 | 1128015.6596 | 2500377.2099 | 1127984.2974 | 2500388.5286 | 1127859.9445 | 2500390.3715 | 1127845.0604 | 2500392.9539 | 1127836.6904 | 2500397.0146 | 1127831.0422 | 2500403.8268 | 1127829.6067
17 | 2500051.4317 | 1128304.9905 | 2500023.2093 | 1128329.4951
18 | 2500403.8268 | 1127829.6067 | 2500405.3789 | 1127793.3586 | 2500406.4535 | 1127757.1295 | 2500407.1455 | 1127721.0623 | 2500407.3849 | 1127684.6579 | 2500407.2851 | 1127648.2481 | 2500406.8579 | 1127612.0771 | 2500406.0528 | 1127575.8901 | 2500404.7951 | 1127539.3659 | 2500403.2143 | 1127502.8804 | 2500401.2191 | 1127466.9687 | 2500398.9385 | 1127431.0506 | 2500396.2564 | 1127395.0836 | 2500392.9595 | 1127359.2268 | 2500390.2621 | 1127330.2755 | 2500388.9755 | 1127317.2331 | 2500383.6508 | 1127268.724 | 2500379.1741 | 1127231.9083 | 2500374.5387 | 1127196.2181 | 2500369.5322 | 1127160.9343 | 2500368.7293 | 1127155.5843
19 | 2500023.2093 | 1128329.4951 | 2500021.2936 | 1128328.2927 | 2500016.2628 | 1128329.9637
20 | 2499885.6429 | 1127184.7384 | 2499878.2297 | 1127193.1888 | 2499856.7298 | 1127218.0718 | 2499829.8901 | 1127244.8891 | 2499808.6806 | 1127268.4937
21 | 2500096.1135 | 1127302.1482 | 2500083.8391 | 1127311.6136 | 2500073.4228 | 1127327.0816
22 | 2500173.3879 | 1128000.6507 | 2500172.7011 | 1128000.1284 | 2500169.272 | 1127997.9925
23 | 2500173.3879 | 1128000.6507 | 2500175.893 | 1128002.5438 | 2500191.9802 | 1128019.0772
24 | 2500191.9802 | 1128019.0772 | 2500193.4526 | 1128017.7075 | 2500195.4695 | 1128017.5741 | 2500197.2894 | 1128018.578 | 2500203.2941 | 1128024.1612
25 | 2500264.8722 | 1127303.3056 | 2500270.9969 | 1127298.0122 | 2500271.641 | 1127295.9448 | 2500271.3228 | 1127292.5479 | 2500269.4342 | 1127284.5964 | 2500269.9653 | 1127282.2195 | 2500298.3701 | 1127262.3271
26 | 2500264.8722 | 1127303.3056 | 2500268.6685 | 1127303.0983 | 2500271.3575 | 1127303.5097 | 2500273.5308 | 1127304.43 | 2500276.5203 | 1127307.1712 | 2500277.8782 | 1127308.9583
27 | 2500249.2723 | 1127285.878 | 2500247.713 | 1127283.5655 | 2500244.8939 | 1127281.811
28 | 2499805.734 | 1127271.7731 | 2499808.6806 | 1127268.4937
29 | 2500102.1132 | 1127283.1937 | 2500106.3191 | 1127287.2378 | 2500106.3015 | 1127292.697 | 2500103.1845 | 1127296.6955 | 2500096.1135 | 1127302.1482
30 | 2500244.8939 | 1127281.811 | 2500244.8939 | 1127281.811 | 2500243.4521 | 1127282.2462
31 | 2500221.725 | 1127296.714 | 2500225.7562 | 1127302.7845 | 2500227.546 | 1127304.7562 | 2500229.9286 | 1127305.2838 | 2500231.5203 | 1127304.5905 | 2500242.1907 | 1127284.2682 | 2500243.4521 | 1127282.2462 | 2500243.4521 | 1127282.2462
32 | 2500283.3497 | 1127319.8108 | 2500280.9087 | 1127312.9468 | 2500277.8782 | 1127308.9583

## bus_geodata
| x | y | coords
0 | 2499921.8133 | 1127709.9345
1 | 2499933.7494 | 1127727.0681
2 | 2499903.3501 | 1127691.5497
3 | 2500167.85 | 1127997.1067
4 | 2499765.0554 | 1127621.3771
5 | 2500168.6118 | 1127341.3749
6 | 2500166.2998 | 1127312.0282
7 | 2500045.7346 | 1127372.1818
8 | 2500260.1336 | 1127305.2628
9 | 2500051.4317 | 1128304.9905
10 | 2500033.4346 | 1128300.1409
11 | 2500403.8268 | 1127829.6067
12 | 2500023.2093 | 1128329.4951
13 | 2499885.6429 | 1127184.7384
14 | 2500073.4228 | 1127327.0816
15 | 2500368.7293 | 1127155.5843
16 | 2500169.272 | 1127997.9925
17 | 2500016.2628 | 1128329.9637
18 | 2500173.3879 | 1128000.6507
19 | 2500191.9802 | 1128019.0772
20 | 2499756.0153 | 1127629.1486
21 | 2500264.8722 | 1127303.3056
22 | 2500249.2723 | 1127285.878
23 | 2499808.6806 | 1127268.4937
24 | 2500096.1135 | 1127302.1482
25 | 2500203.2941 | 1128024.1612
26 | 2500244.8939 | 1127281.811
27 | 2500243.4521 | 1127282.2462
28 | 2500221.725 | 1127296.714
29 | 2500298.3701 | 1127262.3271
30 | 2500277.8782 | 1127308.9583
31 | 2500283.3497 | 1127319.8108
32 | 2500102.1132 | 1127283.1937
33 | 2499805.734 | 1127271.7731
34 | 2500283.3497 | 1127319.8108

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1