## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_669-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_669-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_669-1_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_669-1_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_669-1_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_669-1_0_6_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_669-1_0_6_node_131 | 0.4 | n |  | TRUE
7 | bus_LV_669-1_0_6_node_130 | 0.4 | n |  | TRUE
8 | bus_LV_669-1_0_6_node_137 | 0.4 | n |  | TRUE
9 | bus_LV_669-1_0_6_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_669-1_0_6_node_69 | 0.4 | n |  | TRUE
11 | bus_LV_669-1_0_6_node_122 | 0.4 | n |  | TRUE
12 | bus_LV_669-1_0_6_node_111 | 0.4 | n |  | TRUE
13 | bus_LV_669-1_0_6_node_81 | 0.4 | n |  | TRUE
14 | bus_LV_669-1_0_6_node_128 | 0.4 | n |  | TRUE
15 | bus_LV_669-1_0_6_node_138 | 0.4 | n |  | TRUE
16 | bus_LV_669-1_0_6_node_68 | 0.4 | n |  | TRUE
17 | bus_LV_669-1_0_6_node_82 | 0.4 | n |  | TRUE
18 | bus_LV_669-1_0_6_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_669-1_0_6_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_669-1_0_6_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_669-1_0_6_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_669-1_0_6_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_669-1_0_6_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_669-1_0_6_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_669-1_0_6_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_669-1_0_6_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_669-1_0_6_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_669-1_0_6_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_669-1_0_6_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_669-1_0_6_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_669-1_0_6_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_669-1_0_6_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_669-1_0_6_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_669-1_0_6_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_669-1_0_6_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_669-1_0_6_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_669-1_0_6_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_669-1_0_6_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_669-1_0_6_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_669-1_0_6_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_669-1_0_6_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_669-1_0_6_node_170 | 0.4 | n |  | TRUE
43 | bus_LV_669-1_0_6_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_669-1_0_6_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_669-1_0_6_node_185 | 0.4 | n |  | TRUE
46 | bus_LV_669-1_0_6_node_72 | 0.4 | n |  | TRUE
47 | bus_LV_669-1_0_6_node_71 | 0.4 | n |  | TRUE
48 | bus_LV_669-1_0_6_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_669-1_0_6_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_669-1_0_6_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_669-1_0_6_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_669-1_0_6_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_669-1_0_6_node_63 | 0.4 | n |  | TRUE
54 | bus_LV_669-1_0_6_node_62 | 0.4 | n |  | TRUE
55 | bus_LV_669-1_0_6_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_669-1_0_6_node_41 | 0.4 | n |  | TRUE
57 | bus_LV_669-1_0_6_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_669-1_0_6_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_669-1_0_6_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_669-1_0_6_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_669-1_0_6_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_669-1_0_6_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_669-1_0_6_node_55 | 0.4 | n |  | TRUE
64 | bus_LV_669-1_0_6_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_669-1_0_6_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_669-1_0_6_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_669-1_0_6_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_669-1_0_6_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_669-1_0_6_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_669-1_0_6_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_669-1_0_6_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_669-1_0_6_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_669-1_0_6_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_669-1_0_6_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_669-1_0_6_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_669-1_0_6_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_669-1_0_6_node_149 | 0.4 | n |  | TRUE
78 | bus_LV_669-1_0_6_node_136 | 0.4 | n |  | TRUE
79 | bus_LV_669-1_0_6_node_175 | 0.4 | n |  | TRUE
80 | bus_LV_669-1_0_6_node_135 | 0.4 | n |  | TRUE
81 | bus_LV_669-1_0_6_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_669-1_0_6_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_669-1_0_6_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_669-1_0_6_node_83 | 0.4 | n |  | TRUE
85 | bus_LV_669-1_0_6_node_84 | 0.4 | n |  | TRUE
86 | bus_LV_669-1_0_6_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_669-1_0_6_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_669-1_0_6_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_669-1_0_6_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_669-1_0_6_node_76 | 0.4 | n |  | TRUE
91 | bus_LV_669-1_0_6_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_669-1_0_6_node_102 | 0.4 | n |  | TRUE
93 | bus_LV_669-1_0_6_node_103 | 0.4 | n |  | TRUE
94 | bus_LV_669-1_0_6_node_125 | 0.4 | n |  | TRUE
95 | bus_LV_669-1_0_6_node_123 | 0.4 | n |  | TRUE
96 | bus_LV_669-1_0_6_node_178 | 0.4 | n |  | TRUE
97 | bus_LV_669-1_0_6_node_140 | 0.4 | n |  | TRUE
98 | bus_LV_669-1_0_6_node_112 | 0.4 | n |  | TRUE
99 | bus_LV_669-1_0_6_node_78 | 0.4 | n |  | TRUE
100 | bus_LV_669-1_0_6_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_669-1_0_6_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_669-1_0_6_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_669-1_0_6_node_95 | 0.4 | n |  | TRUE
104 | bus_LV_669-1_0_6_node_176 | 0.4 | n |  | TRUE
105 | bus_LV_669-1_0_6_node_110 | 0.4 | n |  | TRUE
106 | bus_LV_669-1_0_6_node_151 | 0.4 | n |  | TRUE
107 | bus_LV_669-1_0_6_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_669-1_0_6_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_669-1_0_6_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_669-1_0_6_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_669-1_0_6_node_90 | 0.4 | n |  | TRUE
112 | bus_LV_669-1_0_6_node_113 | 0.4 | n |  | TRUE
113 | bus_LV_669-1_0_6_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_669-1_0_6_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_669-1_0_6_node_126 | 0.4 | n |  | TRUE
116 | bus_LV_669-1_0_6_node_139 | 0.4 | n |  | TRUE
117 | bus_LV_669-1_0_6_node_105 | 0.4 | n |  | TRUE
118 | bus_LV_669-1_0_6_node_91 | 0.4 | n |  | TRUE
119 | bus_LV_669-1_0_6_node_92 | 0.4 | n |  | TRUE
120 | bus_LV_669-1_0_6_node_93 | 0.4 | n |  | TRUE
121 | bus_LV_669-1_0_6_node_94 | 0.4 | n |  | TRUE
122 | bus_LV_669-1_0_6_node_101 | 0.4 | n |  | TRUE
123 | bus_LV_669-1_0_6_node_98 | 0.4 | n |  | TRUE
124 | bus_LV_669-1_0_6_node_166 | 0.4 | n |  | TRUE
125 | bus_LV_669-1_0_6_node_146 | 0.4 | n |  | TRUE
126 | bus_LV_669-1_0_6_node_108 | 0.4 | n |  | TRUE
127 | bus_LV_669-1_0_6_node_150 | 0.4 | n |  | TRUE
128 | bus_LV_669-1_0_6_node_96 | 0.4 | n |  | TRUE
129 | bus_LV_669-1_0_6_node_97 | 0.4 | n |  | TRUE
130 | bus_LV_669-1_0_6_node_99 | 0.4 | n |  | TRUE
131 | bus_LV_669-1_0_6_node_100 | 0.4 | n |  | TRUE
132 | bus_LV_669-1_0_6_node_119 | 0.4 | n |  | TRUE
133 | bus_LV_669-1_0_6_node_120 | 0.4 | n |  | TRUE
134 | bus_LV_669-1_0_6_node_124 | 0.4 | n |  | TRUE
135 | bus_LV_669-1_0_6_node_179 | 0.4 | n |  | TRUE
136 | bus_LV_669-1_0_6_node_107 | 0.4 | n |  | TRUE
137 | bus_LV_669-1_0_6_node_132 | 0.4 | n |  | TRUE
138 | bus_LV_669-1_0_6_node_148 | 0.4 | n |  | TRUE
139 | bus_LV_669-1_0_6_node_147 | 0.4 | n |  | TRUE
140 | bus_LV_669-1_0_6_node_133 | 0.4 | n |  | TRUE
141 | bus_LV_669-1_0_6_node_114 | 0.4 | n |  | TRUE
142 | bus_LV_669-1_0_6_node_115 | 0.4 | n |  | TRUE
143 | bus_LV_669-1_0_6_node_116 | 0.4 | n |  | TRUE
144 | bus_LV_669-1_0_6_node_117 | 0.4 | n |  | TRUE
145 | bus_LV_669-1_0_6_node_118 | 0.4 | n |  | TRUE
146 | bus_LV_669-1_0_6_node_145 | 0.4 | n |  | TRUE
147 | bus_LV_669-1_0_6_node_143 | 0.4 | n |  | TRUE
148 | bus_LV_669-1_0_6_node_121 | 0.4 | n |  | TRUE
149 | bus_LV_669-1_0_6_node_159 | 0.4 | n |  | TRUE
150 | bus_LV_669-1_0_6_node_161 | 0.4 | n |  | TRUE
151 | bus_LV_669-1_0_6_node_157 | 0.4 | n |  | TRUE
152 | bus_LV_669-1_0_6_node_127 | 0.4 | n |  | TRUE
153 | bus_LV_669-1_0_6_node_129 | 0.4 | n |  | TRUE
154 | bus_LV_669-1_0_6_node_134 | 0.4 | n |  | TRUE
155 | bus_LV_669-1_0_6_node_141 | 0.4 | n |  | TRUE
156 | bus_LV_669-1_0_6_node_142 | 0.4 | n |  | TRUE
157 | bus_LV_669-1_0_6_node_144 | 0.4 | n |  | TRUE
158 | bus_LV_669-1_0_6_node_169 | 0.4 | n |  | TRUE
159 | bus_LV_669-1_0_6_node_173 | 0.4 | n |  | TRUE
160 | bus_LV_669-1_0_6_node_152 | 0.4 | n |  | TRUE
161 | bus_LV_669-1_0_6_node_153 | 0.4 | n |  | TRUE
162 | bus_LV_669-1_0_6_node_154 | 0.4 | n |  | TRUE
163 | bus_LV_669-1_0_6_node_155 | 0.4 | n |  | TRUE
164 | bus_LV_669-1_0_6_node_156 | 0.4 | n |  | TRUE
165 | bus_LV_669-1_0_6_node_168 | 0.4 | n |  | TRUE
166 | bus_LV_669-1_0_6_node_174 | 0.4 | n |  | TRUE
167 | bus_LV_669-1_0_6_node_167 | 0.4 | n |  | TRUE
168 | bus_LV_669-1_0_6_node_172 | 0.4 | n |  | TRUE
169 | bus_LV_669-1_0_6_node_158 | 0.4 | n |  | TRUE
170 | bus_LV_669-1_0_6_node_160 | 0.4 | n |  | TRUE
171 | bus_LV_669-1_0_6_node_177 | 0.4 | n |  | TRUE
172 | bus_LV_669-1_0_6_node_182 | 0.4 | n |  | TRUE
173 | bus_LV_669-1_0_6_node_162 | 0.4 | n |  | TRUE
174 | bus_LV_669-1_0_6_node_163 | 0.4 | n |  | TRUE
175 | bus_LV_669-1_0_6_node_164 | 0.4 | n |  | TRUE
176 | bus_LV_669-1_0_6_node_165 | 0.4 | n |  | TRUE
177 | bus_LV_669-1_0_6_node_171 | 0.4 | n |  | TRUE
178 | bus_LV_669-1_0_6_node_183 | 0.4 | n |  | TRUE
179 | bus_LV_669-1_0_6_node_184 | 0.4 | n |  | TRUE
180 | bus_LV_669-1_0_6_node_180 | 0.4 | n |  | TRUE
181 | bus_LV_669-1_0_6_node_181 | 0.4 | n |  | TRUE
182 | bus_LV_669-1_0_6_node_186 | 0.4 | n |  | TRUE
183 | bus_LV_669-1_0_6_node_187 | 0.4 | n |  | TRUE
184 | bus_LV_669-1_0_6_node_188 | 0.4 | n |  | TRUE
185 | bus_LV_669-1_0_6_node_204 | 0.4 | n |  | TRUE
186 | bus_LV_669-1_0_6_node_201 | 0.4 | n |  | TRUE
187 | bus_LV_669-1_0_6_node_205 | 0.4 | n |  | TRUE
188 | bus_LV_669-1_0_6_node_198 | 0.4 | n |  | TRUE
189 | bus_LV_669-1_0_6_node_189 | 0.4 | n |  | TRUE
190 | bus_LV_669-1_0_6_node_190 | 0.4 | n |  | TRUE
191 | bus_LV_669-1_0_6_node_191 | 0.4 | n |  | TRUE
192 | bus_LV_669-1_0_6_node_192 | 0.4 | n |  | TRUE
193 | bus_LV_669-1_0_6_node_193 | 0.4 | n |  | TRUE
194 | bus_LV_669-1_0_6_node_194 | 0.4 | n |  | TRUE
195 | bus_LV_669-1_0_6_node_213 | 0.4 | n |  | TRUE
196 | bus_LV_669-1_0_6_node_215 | 0.4 | n |  | TRUE
197 | bus_LV_669-1_0_6_node_202 | 0.4 | n |  | TRUE
198 | bus_LV_669-1_0_6_node_203 | 0.4 | n |  | TRUE
199 | bus_LV_669-1_0_6_node_195 | 0.4 | n |  | TRUE
200 | bus_LV_669-1_0_6_node_196 | 0.4 | n |  | TRUE
201 | bus_LV_669-1_0_6_node_197 | 0.4 | n |  | TRUE
202 | bus_LV_669-1_0_6_node_199 | 0.4 | n |  | TRUE
203 | bus_LV_669-1_0_6_node_200 | 0.4 | n |  | TRUE
204 | bus_LV_669-1_0_6_node_206 | 0.4 | n |  | TRUE
205 | bus_LV_669-1_0_6_node_207 | 0.4 | n |  | TRUE
206 | bus_LV_669-1_0_6_node_208 | 0.4 | n |  | TRUE
207 | bus_LV_669-1_0_6_node_209 | 0.4 | n |  | TRUE
208 | bus_LV_669-1_0_6_node_210 | 0.4 | n |  | TRUE
209 | bus_LV_669-1_0_6_node_211 | 0.4 | n |  | TRUE
210 | bus_LV_669-1_0_6_node_212 | 0.4 | n |  | TRUE
211 | bus_LV_669-1_0_6_node_216 | 0.4 | n |  | TRUE
212 | bus_MV_379_0_node_189 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_669-1_0_6_load_0 | 0 | 0.010595 | 0.0026554 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_669-1_0_6_load_1 | 1 | 0.0277 | 0.0069423 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_669-1_0_6_load_4 | 3 | 0.0031339 | 0.00078544 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_669-1_0_6_load_131 | 6 | 0.014682 | 0.0036798 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_669-1_0_6_load_137 | 8 | 0.0028964 | 0.00072592 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_669-1_0_6_load_69 | 10 | 0.0016665 | 0.00041767 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_669-1_0_6_load_122 | 11 | 0.0044521 | 0.0011158 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_669-1_0_6_load_81 | 13 | 0.0010369 | 0.00025987 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_669-1_0_6_load_128 | 14 | 0.0039729 | 0.00099571 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_669-1_0_6_load_138 | 15 | 0.0029545 | 0.00074047 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_669-1_0_6_load_68 | 16 | 0.003573 | 0.00089548 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_669-1_0_6_load_82 | 17 | 0.003402 | 0.00085262 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_669-1_0_6_load_9 | 18 | 0.0024361 | 0.00061054 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_669-1_0_6_load_10 | 19 | 0.0026409 | 0.00066188 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_669-1_0_6_load_11 | 20 | 0.0025619 | 0.00064207 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_669-1_0_6_load_12 | 23 | 0.0014582 | 0.00036547 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_669-1_0_6_load_13 | 24 | 0.00093033 | 0.00023316 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_669-1_0_6_load_14 | 25 | 0.001123 | 0.00028145 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_669-1_0_6_load_15 | 26 | 0.0018815 | 0.00047154 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_669-1_0_6_load_16 | 27 | 0.0043319 | 0.0010857 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_669-1_0_6_load_22 | 28 | 0.0013521 | 0.00033887 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_669-1_0_6_load_25 | 30 | 0.004398 | 0.0011023 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_669-1_0_6_load_23 | 31 | 0.0011949 | 0.00029947 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_669-1_0_6_load_19 | 32 | 0.002299 | 0.00057617 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_669-1_0_6_load_17 | 33 | 0.0017983 | 0.00045069 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_669-1_0_6_load_18 | 34 | 0.0059348 | 0.0014874 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_669-1_0_6_load_29 | 35 | 0.0026298 | 0.0006591 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_669-1_0_6_load_24 | 36 | 0.0016343 | 0.00040959 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_669-1_0_6_load_26 | 37 | 0.0028581 | 0.0007163 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_669-1_0_6_load_33 | 39 | 0.001026 | 0.00025713 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_669-1_0_6_load_35 | 40 | 0.0028864 | 0.0007234 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_669-1_0_6_load_170 | 42 | 0.0015549 | 0.00038969 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_669-1_0_6_load_30 | 43 | 0.00092858 | 0.00023273 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_669-1_0_6_load_34 | 44 | 0.0045499 | 0.0011403 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_669-1_0_6_load_72 | 46 | 0.0036055 | 0.00090363 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_669-1_0_6_load_71 | 47 | 0.0019882 | 0.0004983 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_669-1_0_6_load_36 | 48 | 0.0022138 | 0.00055483 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_669-1_0_6_load_37 | 49 | 0.0030311 | 0.00075966 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_669-1_0_6_load_38 | 50 | 0.002043 | 0.00051203 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_669-1_0_6_load_39 | 51 | 0.0054665 | 0.00137 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_669-1_0_6_load_63 | 53 | 0.0032598 | 0.00081698 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_669-1_0_6_load_62 | 54 | 0.0040694 | 0.0010199 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_669-1_0_6_load_41 | 56 | 0.0042629 | 0.0010684 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_669-1_0_6_load_42 | 57 | 0.0010164 | 0.00025473 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_669-1_0_6_load_44 | 59 | 0.0047362 | 0.001187 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_669-1_0_6_load_52 | 60 | 0.001855 | 0.00046491 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_669-1_0_6_load_56 | 61 | 0.0028194 | 0.00070662 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_669-1_0_6_load_51 | 62 | 0.0065471 | 0.0016409 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_669-1_0_6_load_55 | 63 | 0.002883 | 0.00072255 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_669-1_0_6_load_46 | 64 | 0.0005557 | 0.00013927 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_669-1_0_6_load_47 | 65 | 0.001597 | 0.00040025 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_669-1_0_6_load_48 | 66 | 0.010963 | 0.0027475 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_669-1_0_6_load_49 | 67 | 0.0050891 | 0.0012754 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_669-1_0_6_load_50 | 68 | 0.0024602 | 0.00061659 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_669-1_0_6_load_61 | 69 | 0.0024971 | 0.00062583 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_669-1_0_6_load_58 | 70 | 0.00086653 | 0.00021717 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_669-1_0_6_load_53 | 71 | 0.0022508 | 0.00056412 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_669-1_0_6_load_54 | 72 | 0.0022098 | 0.00055382 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_669-1_0_6_load_59 | 73 | 0.0063863 | 0.0016006 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_669-1_0_6_load_57 | 75 | 0.0028056 | 0.00070315 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_669-1_0_6_load_149 | 77 | 0.0043331 | 0.001086 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_669-1_0_6_load_136 | 78 | 0.004827 | 0.0012097 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_669-1_0_6_load_175 | 79 | 0.0015159 | 0.00037992 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_669-1_0_6_load_65 | 81 | 0.0011643 | 0.0002918 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_669-1_0_6_load_66 | 82 | 0.0010549 | 0.00026438 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_669-1_0_6_load_67 | 83 | 0.001218 | 0.00030525 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_669-1_0_6_load_83 | 84 | 0.0011649 | 0.00029196 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_669-1_0_6_load_84 | 85 | 0.0011645 | 0.00029184 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_669-1_0_6_load_73 | 87 | 0.00074373 | 0.0001864 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_669-1_0_6_load_74 | 88 | 0.00059738 | 0.00014972 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_669-1_0_6_load_75 | 89 | 0.0024372 | 0.00061081 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_669-1_0_6_load_77 | 91 | 0.0005085 | 0.00012744 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_669-1_0_6_load_102 | 92 | 0.00087295 | 0.00021878 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_669-1_0_6_load_103 | 93 | 0.0006231 | 0.00015616 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_669-1_0_6_load_178 | 96 | 0.00074348 | 0.00018633 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_669-1_0_6_load_140 | 97 | 0.0018988 | 0.00047588 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_669-1_0_6_load_78 | 99 | 0.0031769 | 0.0007962 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_669-1_0_6_load_79 | 100 | 0.0011791 | 0.0002955 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_669-1_0_6_load_80 | 101 | 0.0050664 | 0.0012698 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_669-1_0_6_load_85 | 102 | 0.0012803 | 0.00032088 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_669-1_0_6_load_176 | 104 | 0.0013032 | 0.00032661 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_669-1_0_6_load_86 | 107 | 0.002571 | 0.00064436 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_669-1_0_6_load_87 | 108 | 0.0032483 | 0.0008141 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_669-1_0_6_load_89 | 110 | 0.0043547 | 0.0010914 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_669-1_0_6_load_113 | 112 | 0.0025266 | 0.00063323 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_669-1_0_6_load_106 | 113 | 0.0018507 | 0.00046383 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_669-1_0_6_load_104 | 114 | 0.0032424 | 0.00081263 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_669-1_0_6_load_126 | 115 | 0.0015444 | 0.00038706 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_669-1_0_6_load_139 | 116 | 0.0027431 | 0.00068749 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_669-1_0_6_load_105 | 117 | 0.0030468 | 0.00076359 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_669-1_0_6_load_91 | 118 | 0.0018763 | 0.00047025 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_669-1_0_6_load_92 | 119 | 0.0015464 | 0.00038757 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_669-1_0_6_load_93 | 120 | 0.00014762 | 3.6997e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_669-1_0_6_load_94 | 121 | 0.00080136 | 0.00020084 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_669-1_0_6_load_101 | 122 | 0.00051659 | 0.00012947 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_669-1_0_6_load_146 | 125 | 0.0051688 | 0.0012954 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_669-1_0_6_load_108 | 126 | 0.00099026 | 0.00024818 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_669-1_0_6_load_150 | 127 | 0.0030594 | 0.00076676 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_669-1_0_6_load_96 | 128 | 0.0021546 | 0.00054 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_669-1_0_6_load_97 | 129 | 0.0019383 | 0.00048577 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_669-1_0_6_load_99 | 130 | 0.0016462 | 0.00041258 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_669-1_0_6_load_100 | 131 | 0.00058517 | 0.00014666 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_669-1_0_6_load_119 | 132 | 0.001321 | 0.00033108 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_669-1_0_6_load_120 | 133 | 0.00027461 | 6.8824e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_669-1_0_6_load_124 | 134 | 0.0002894 | 7.2531e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_669-1_0_6_load_107 | 136 | 0.0083876 | 0.0021021 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_669-1_0_6_load_132 | 137 | 0.0026345 | 0.00066027 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_669-1_0_6_load_148 | 138 | 0.0040324 | 0.0010106 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_669-1_0_6_load_147 | 139 | 0.00075364 | 0.00018888 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_669-1_0_6_load_133 | 140 | 0.0064944 | 0.0016277 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_669-1_0_6_load_114 | 141 | 0.0084075 | 0.0021071 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_669-1_0_6_load_115 | 142 | 0.0017717 | 0.00044403 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_669-1_0_6_load_116 | 143 | 0.0011648 | 0.00029194 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_669-1_0_6_load_118 | 145 | 0.001387 | 0.00034763 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_669-1_0_6_load_145 | 146 | 0.0051705 | 0.0012958 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_669-1_0_6_load_143 | 147 | 0.0010905 | 0.00027331 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_669-1_0_6_load_121 | 148 | 0.0022488 | 0.0005636 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_669-1_0_6_load_157 | 151 | 0.00097769 | 0.00024503 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_669-1_0_6_load_127 | 152 | 0.0072574 | 0.0018189 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_669-1_0_6_load_129 | 153 | 0.0067344 | 0.0016878 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_669-1_0_6_load_134 | 154 | 0.0056368 | 0.0014127 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_669-1_0_6_load_141 | 155 | 0.0017807 | 0.00044628 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_669-1_0_6_load_142 | 156 | 0.0016201 | 0.00040604 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_669-1_0_6_load_144 | 157 | 0.0031371 | 0.00078624 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_669-1_0_6_load_169 | 158 | 0.0012837 | 0.00032172 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_669-1_0_6_load_173 | 159 | 0.0018973 | 0.00047551 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_669-1_0_6_load_152 | 160 | 0.0027295 | 0.00068408 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_669-1_0_6_load_153 | 161 | 0.0028867 | 0.00072347 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_669-1_0_6_load_154 | 162 | 0.0038019 | 0.00095286 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_669-1_0_6_load_155 | 163 | 0.0013955 | 0.00034974 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_669-1_0_6_load_156 | 164 | 0.0023854 | 0.00059783 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_669-1_0_6_load_174 | 166 | 0.0035782 | 0.00089678 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_669-1_0_6_load_167 | 167 | 0.0034506 | 0.0008648 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_669-1_0_6_load_172 | 168 | 0.0027457 | 0.00068814 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_669-1_0_6_load_158 | 169 | 0.00044865 | 0.00011244 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_669-1_0_6_load_160 | 170 | 0.0008116 | 0.00020341 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_669-1_0_6_load_177 | 171 | 0.0011501 | 0.00028825 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_669-1_0_6_load_182 | 172 | 0.001227 | 0.0003075 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_669-1_0_6_load_162 | 173 | 0.0036212 | 0.00090756 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_669-1_0_6_load_163 | 174 | 0.0043641 | 0.0010938 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_669-1_0_6_load_165 | 176 | 0.0053078 | 0.0013303 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_669-1_0_6_load_171 | 177 | 0.002283 | 0.00057217 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_669-1_0_6_load_183 | 178 | 0.0010331 | 0.00025892 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_669-1_0_6_load_184 | 179 | 0.0010185 | 0.00025527 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_669-1_0_6_load_180 | 180 | 0.0006343 | 0.00015897 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_669-1_0_6_load_181 | 181 | 0.00047027 | 0.00011786 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_669-1_0_6_load_187 | 183 | 0.0036459 | 0.00091375 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_669-1_0_6_load_201 | 186 | 0.00072929 | 0.00018278 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_669-1_0_6_load_205 | 187 | 0.00086797 | 0.00021753 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_669-1_0_6_load_189 | 189 | 0.008378 | 0.0020997 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_669-1_0_6_load_190 | 190 | 0.0076755 | 0.0019236 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_669-1_0_6_load_191 | 191 | 0.0023743 | 0.00059505 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_669-1_0_6_load_192 | 192 | 0.013914 | 0.0034872 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_669-1_0_6_load_194 | 194 | 0.00073357 | 0.00018385 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_669-1_0_6_load_213 | 195 | 0.0030463 | 0.00076349 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_669-1_0_6_load_202 | 197 | 0.00076172 | 0.0001909 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_669-1_0_6_load_203 | 198 | 0.00086297 | 0.00021628 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_669-1_0_6_load_195 | 199 | 0.0014304 | 0.00035849 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_669-1_0_6_load_196 | 200 | 0.0034103 | 0.0008547 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_669-1_0_6_load_199 | 202 | 0.00073262 | 0.00018361 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_669-1_0_6_load_200 | 203 | 0.0008011 | 0.00020078 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_669-1_0_6_load_206 | 204 | 0.00076755 | 0.00019237 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_669-1_0_6_load_207 | 205 | 0.00076217 | 0.00019102 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_669-1_0_6_load_208 | 206 | 0.00071583 | 0.0001794 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_669-1_0_6_load_209 | 207 | 0.00075167 | 0.00018839 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_669-1_0_6_load_210 | 208 | 0.00078487 | 0.00019671 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_669-1_0_6_load_211 | 209 | 0.0040759 | 0.0010215 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_669-1_0_6_load_212 | 210 | 0.00075353 | 0.00018885 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_669-1_0_6_load_216 | 211 | 0.0034761 | 0.0008712 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 104 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_669-1_0_6_line_0 |  | 0 | 1 | 0.045157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_669-1_0_6_line_1 |  | 0 | 2 | 0.039661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_669-1_0_6_line_2 |  | 2 | 3 | 0.062721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_669-1_0_6_line_3 |  | 2 | 4 | 0.048092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_669-1_0_6_line_4 |  | 4 | 5 | 0.051191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_669-1_0_6_line_5 |  | 4 | 6 | 0.037084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_669-1_0_6_line_6 |  | 5 | 7 | 0.057295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_669-1_0_6_line_7 |  | 5 | 8 | 0.021943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_669-1_0_6_line_8 |  | 6 | 12 | 0.02835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_669-1_0_6_line_9 |  | 7 | 13 | 0.017443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_669-1_0_6_line_10 |  | 7 | 14 | 0.020628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_669-1_0_6_line_11 |  | 8 | 15 | 0.0067714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_669-1_0_6_line_12 |  | 9 | 10 | 0.004115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_669-1_0_6_line_13 |  | 9 | 11 | 0.024036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_669-1_0_6_line_14 |  | 10 | 16 | 0.0076812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_669-1_0_6_line_15 |  | 11 | 17 | 0.0057709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_669-1_0_6_line_16 |  | 12 | 137 | 0.027679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_669-1_0_6_line_17 |  | 13 | 100 | 0.0056014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_669-1_0_6_line_18 |  | 14 | 152 | 0.0023446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_669-1_0_6_line_19 |  | 15 | 116 | 0.051798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_669-1_0_6_line_20 |  | 16 | 86 | 0.054348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_669-1_0_6_line_21 |  | 17 | 101 | 0.027806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_669-1_0_6_line_22 |  | 18 | 19 | 0.029689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_669-1_0_6_line_23 |  | 19 | 20 | 0.030477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_669-1_0_6_line_24 |  | 20 | 21 | 0.053325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_669-1_0_6_line_25 |  | 21 | 22 | 0.035757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_669-1_0_6_line_26 |  | 22 | 35 | 0.04143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_669-1_0_6_line_27 |  | 22 | 34 | 0.0094907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_669-1_0_6_line_28 |  | 23 | 24 | 0.0019633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_669-1_0_6_line_29 |  | 23 | 25 | 0.0028336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_669-1_0_6_line_30 |  | 24 | 26 | 0.010649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_669-1_0_6_line_31 |  | 25 | 27 | 0.040041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_669-1_0_6_line_32 |  | 26 | 28 | 0.014637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_669-1_0_6_line_33 |  | 27 | 29 | 0.0062662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_669-1_0_6_line_34 |  | 28 | 30 | 0.0096934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_669-1_0_6_line_35 |  | 29 | 31 | 0.017396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_669-1_0_6_line_36 |  | 29 | 32 | 0.046684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_669-1_0_6_line_37 |  | 30 | 36 | 0.017725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_669-1_0_6_line_38 |  | 32 | 33 | 0.025279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_669-1_0_6_line_39 |  | 33 | 34 | 0.019175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_669-1_0_6_line_40 |  | 36 | 37 | 0.0098579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_669-1_0_6_line_41 |  | 37 | 38 | 0.074515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_669-1_0_6_line_42 |  | 38 | 39 | 0.037704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_669-1_0_6_line_43 |  | 38 | 40 | 0.032586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_669-1_0_6_line_44 |  | 39 | 41 | 0.027347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_669-1_0_6_line_45 |  | 40 | 42 | 0.02851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_669-1_0_6_line_46 |  | 41 | 43 | 0.08804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_669-1_0_6_line_47 |  | 42 | 47 | 0.020391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_669-1_0_6_line_48 |  | 44 | 45 | 0.0087246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_669-1_0_6_line_49 |  | 45 | 46 | 0.038502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_669-1_0_6_line_50 |  | 46 | 86 | 0.031079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_669-1_0_6_line_51 |  | 47 | 86 | 0.0051103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_669-1_0_6_line_52 |  | 48 | 49 | 0.058938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_669-1_0_6_line_53 |  | 48 | 50 | 0.035993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_669-1_0_6_line_54 |  | 49 | 51 | 0.020524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_669-1_0_6_line_55 |  | 50 | 52 | 0.067925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_669-1_0_6_line_56 |  | 52 | 53 | 0.02849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_669-1_0_6_line_57 |  | 52 | 54 | 0.030805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_669-1_0_6_line_58 |  | 53 | 55 | 0.017303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_669-1_0_6_line_59 |  | 55 | 61 | 0.018495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_669-1_0_6_line_60 |  | 55 | 58 | 0.018766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_669-1_0_6_line_61 |  | 56 | 57 | 0.018896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_669-1_0_6_line_62 |  | 56 | 58 | 0.018712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_669-1_0_6_line_63 |  | 57 | 59 | 0.015099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_669-1_0_6_line_64 |  | 59 | 60 | 0.032959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_669-1_0_6_line_65 |  | 60 | 62 | 0.039621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_669-1_0_6_line_66 |  | 61 | 63 | 0.013125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_669-1_0_6_line_67 |  | 62 | 71 | 0.093774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_669-1_0_6_line_68 |  | 63 | 75 | 0.0021224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_669-1_0_6_line_69 |  | 64 | 65 | 0.0026116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_669-1_0_6_line_70 |  | 64 | 66 | 0.015724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_669-1_0_6_line_71 |  | 65 | 67 | 0.020754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_669-1_0_6_line_72 |  | 66 | 68 | 0.0066276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_669-1_0_6_line_73 |  | 67 | 69 | 0.028686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_669-1_0_6_line_74 |  | 69 | 70 | 0.016569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_669-1_0_6_line_75 |  | 70 | 75 | 0.0059498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_669-1_0_6_line_76 |  | 71 | 72 | 0.004425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_669-1_0_6_line_77 |  | 72 | 73 | 0.013544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_669-1_0_6_line_78 |  | 73 | 74 | 0.021425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_669-1_0_6_line_79 |  | 74 | 76 | 0.076398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_669-1_0_6_line_80 |  | 76 | 77 | 0.040285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_669-1_0_6_line_81 |  | 76 | 78 | 0.086284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_669-1_0_6_line_82 |  | 77 | 79 | 0.048719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_669-1_0_6_line_83 |  | 78 | 80 | 0.021937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_669-1_0_6_line_84 |  | 79 | 159 | 0.012591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_669-1_0_6_line_85 |  | 80 | 154 | 0.039085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_669-1_0_6_line_86 |  | 81 | 82 | 0.0027636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_669-1_0_6_line_87 |  | 82 | 83 | 0.019508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_669-1_0_6_line_88 |  | 83 | 84 | 0.0027898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_669-1_0_6_line_89 |  | 84 | 85 | 0.026825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_669-1_0_6_line_90 |  | 85 | 102 | 0.0053608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_669-1_0_6_line_91 |  | 87 | 88 | 0.026715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_669-1_0_6_line_92 |  | 87 | 89 | 0.013516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_669-1_0_6_line_93 |  | 88 | 90 | 0.019174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_669-1_0_6_line_94 |  | 89 | 91 | 0.084806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_669-1_0_6_line_95 |  | 90 | 92 | 0.0073083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_669-1_0_6_line_96 |  | 90 | 93 | 0.069763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_669-1_0_6_line_97 |  | 91 | 94 | 0.031673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_669-1_0_6_line_98 |  | 92 | 95 | 0.0051759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_669-1_0_6_line_99 |  | 93 | 96 | 0.017038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_669-1_0_6_line_100 |  | 94 | 97 | 0.019354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_669-1_0_6_line_101 |  | 94 | 98 | 0.01928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_669-1_0_6_line_102 |  | 95 | 134 | 0.025492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_669-1_0_6_line_103 |  | 96 | 135 | 0.00096977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_669-1_0_6_line_104 |  | 97 | 145 | 0.016583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_669-1_0_6_line_105 |  | 98 | 138 | 0.016749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_669-1_0_6_line_106 |  | 99 | 100 | 0.016935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_669-1_0_6_line_107 |  | 99 | 101 | 0.0041265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_669-1_0_6_line_108 |  | 102 | 103 | 0.036926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_669-1_0_6_line_109 |  | 103 | 104 | 0.017112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_669-1_0_6_line_110 |  | 103 | 105 | 0.013804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_669-1_0_6_line_111 |  | 103 | 106 | 0.060119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_669-1_0_6_line_112 |  | 104 | 124 | 0.036797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_669-1_0_6_line_113 |  | 105 | 125 | 0.029234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_669-1_0_6_line_114 |  | 105 | 126 | 0.018878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_669-1_0_6_line_115 |  | 106 | 127 | 0.015002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_669-1_0_6_line_116 |  | 107 | 108 | 0.026998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_669-1_0_6_line_117 |  | 107 | 109 | 0.030457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_669-1_0_6_line_118 |  | 108 | 110 | 0.034002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_669-1_0_6_line_119 |  | 109 | 111 | 0.049305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_669-1_0_6_line_120 |  | 110 | 112 | 0.0033633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_669-1_0_6_line_121 |  | 111 | 113 | 0.011629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_669-1_0_6_line_122 |  | 111 | 114 | 0.01933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_669-1_0_6_line_123 |  | 112 | 115 | 0.011684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_669-1_0_6_line_124 |  | 113 | 116 | 0.036507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_669-1_0_6_line_125 |  | 114 | 117 | 0.0010944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_669-1_0_6_line_126 |  | 115 | 140 | 0.021169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_669-1_0_6_line_127 |  | 117 | 130 | 0.063016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_669-1_0_6_line_128 |  | 118 | 119 | 0.048636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_669-1_0_6_line_129 |  | 118 | 120 | 0.027331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_669-1_0_6_line_130 |  | 120 | 121 | 0.01232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_669-1_0_6_line_131 |  | 121 | 122 | 0.031907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_669-1_0_6_line_132 |  | 122 | 123 | 0.041252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_669-1_0_6_line_133 |  | 123 | 131 | 0.031804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_669-1_0_6_line_134 |  | 123 | 128 | 0.012452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_669-1_0_6_line_135 |  | 124 | 178 | 0.018002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_669-1_0_6_line_136 |  | 124 | 175 | 0.047759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_669-1_0_6_line_137 |  | 125 | 139 | 0.010636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
138 | LV_669-1_0_6_line_138 |  | 126 | 136 | 0.056734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_669-1_0_6_line_139 |  | 127 | 137 | 0.016898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
140 | LV_669-1_0_6_line_140 |  | 128 | 129 | 0.028909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_669-1_0_6_line_141 |  | 129 | 130 | 0.032464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_669-1_0_6_line_142 |  | 131 | 132 | 0.064456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_669-1_0_6_line_143 |  | 132 | 133 | 0.023285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_669-1_0_6_line_144 |  | 133 | 148 | 0.004693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_669-1_0_6_line_145 |  | 134 | 149 | 0.0036101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_669-1_0_6_line_146 |  | 135 | 180 | 0.041664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_669-1_0_6_line_147 |  | 135 | 181 | 0.033679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_669-1_0_6_line_148 |  | 138 | 139 | 0.026425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
149 | LV_669-1_0_6_line_149 |  | 141 | 142 | 0.0045228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_669-1_0_6_line_150 |  | 141 | 143 | 0.029588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_669-1_0_6_line_151 |  | 142 | 144 | 0.0086092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_669-1_0_6_line_152 |  | 143 | 145 | 0.018939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_669-1_0_6_line_153 |  | 144 | 146 | 0.012722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_669-1_0_6_line_154 |  | 146 | 147 | 0.0055038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_669-1_0_6_line_155 |  | 147 | 155 | 0.066217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_669-1_0_6_line_156 |  | 149 | 150 | 0.068981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_669-1_0_6_line_157 |  | 149 | 151 | 0.017983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_669-1_0_6_line_158 |  | 150 | 172 | 0.034483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_669-1_0_6_line_159 |  | 151 | 169 | 0.022464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_669-1_0_6_line_160 |  | 152 | 153 | 0.010739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_669-1_0_6_line_161 |  | 155 | 156 | 0.030702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_669-1_0_6_line_162 |  | 156 | 157 | 0.027756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_669-1_0_6_line_163 |  | 157 | 158 | 0.017852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_669-1_0_6_line_164 |  | 159 | 168 | 0.0064002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
165 | LV_669-1_0_6_line_165 |  | 160 | 161 | 0.026835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
166 | LV_669-1_0_6_line_166 |  | 160 | 162 | 0.039761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
167 | LV_669-1_0_6_line_167 |  | 161 | 163 | 0.017878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
168 | LV_669-1_0_6_line_168 |  | 162 | 164 | 0.034191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
169 | LV_669-1_0_6_line_169 |  | 163 | 165 | 0.0021749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
170 | LV_669-1_0_6_line_170 |  | 164 | 166 | 0.017026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
171 | LV_669-1_0_6_line_171 |  | 165 | 167 | 0.024633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
172 | LV_669-1_0_6_line_172 |  | 166 | 168 | 0.0069305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
173 | LV_669-1_0_6_line_173 |  | 167 | 175 | 0.017026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
174 | LV_669-1_0_6_line_174 |  | 169 | 170 | 0.020846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_669-1_0_6_line_175 |  | 170 | 171 | 0.029275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_669-1_0_6_line_176 |  | 173 | 174 | 0.028115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_669-1_0_6_line_177 |  | 173 | 175 | 0.042387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_669-1_0_6_line_178 |  | 174 | 176 | 0.044741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_669-1_0_6_line_179 |  | 176 | 177 | 0.017513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_669-1_0_6_line_180 |  | 178 | 179 | 0.023019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_669-1_0_6_line_181 |  | 180 | 182 | 0.092656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_669-1_0_6_line_182 |  | 182 | 183 | 0.032395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_669-1_0_6_line_183 |  | 182 | 184 | 0.03221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_669-1_0_6_line_184 |  | 184 | 185 | 0.029079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_669-1_0_6_line_185 |  | 184 | 186 | 0.018111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_669-1_0_6_line_186 |  | 185 | 187 | 0.021371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_669-1_0_6_line_187 |  | 186 | 188 | 0.0035177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_669-1_0_6_line_188 |  | 187 | 204 | 0.018365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_669-1_0_6_line_189 |  | 188 | 203 | 0.014415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_669-1_0_6_line_190 |  | 189 | 190 | 0.0087848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_669-1_0_6_line_191 |  | 189 | 191 | 0.020372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_669-1_0_6_line_192 |  | 190 | 192 | 0.016099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_669-1_0_6_line_193 |  | 191 | 193 | 0.03655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_669-1_0_6_line_194 |  | 193 | 194 | 0.0013065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_669-1_0_6_line_195 |  | 194 | 197 | 0.020527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_669-1_0_6_line_196 |  | 195 | 196 | 0.017148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_669-1_0_6_line_197 |  | 196 | 211 | 0.012966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_669-1_0_6_line_198 |  | 197 | 198 | 0.01824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_669-1_0_6_line_199 |  | 198 | 202 | 0.01815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_669-1_0_6_line_200 |  | 199 | 200 | 0.0012961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_669-1_0_6_line_201 |  | 199 | 201 | 0.015889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_669-1_0_6_line_202 |  | 201 | 202 | 0.0051684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_669-1_0_6_line_203 |  | 201 | 203 | 0.013247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_669-1_0_6_line_204 |  | 204 | 205 | 0.017995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_669-1_0_6_line_205 |  | 205 | 206 | 0.017765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_669-1_0_6_line_206 |  | 206 | 207 | 0.018517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_669-1_0_6_line_207 |  | 207 | 208 | 0.018366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_669-1_0_6_line_208 |  | 208 | 209 | 0.013462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_669-1_0_6_line_209 |  | 209 | 210 | 0.0090226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_669-1_0_6_line_210 |  | 210 | 211 | 0.050759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_669-1_0_6_trafo_176 | 0.63 MVA 20/0.4 kV | 212 | 104 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2576238.5539 | 1195735.569 | 2576256.9951 | 1195738.8084 | 2576265.7716 | 1195725.5107 | 2576270.6143 | 1195716.1932
1 | 2576214.7936 | 1195707.1486 | 2576222.228 | 1195708.8087 | 2576230.7021 | 1195722.838 | 2576236.2206 | 1195727.4073 | 2576238.5539 | 1195735.569 | 2576238.5539 | 1195735.569
2 | 2576214.7936 | 1195707.1486 | 2576213.6963 | 1195722.3389 | 2576198.0974 | 1195742.1674 | 2576194.3349 | 1195751.921 | 2576199.9394 | 1195757.0236 | 2576203.603 | 1195759.1358
3 | 2576179.4692 | 1195713.1596 | 2576182.153 | 1195702.2652 | 2576183.1051 | 1195698.4149 | 2576199.5894 | 1195703.7519 | 2576214.7936 | 1195707.1486
4 | 2576179.4692 | 1195713.1596 | 2576182.153 | 1195702.2652 | 2576183.1051 | 1195698.4149 | 2576185.5577 | 1195686.8767 | 2576190.0325 | 1195676.1641 | 2576197.7786 | 1195666.2278
5 | 2576179.4692 | 1195713.1596 | 2576153.1828 | 1195719.835 | 2576143.222 | 1195719.6362
6 | 2576197.7786 | 1195666.2278 | 2576211.9853 | 1195654.4425 | 2576221.5044 | 1195645.8888 | 2576231.8477 | 1195637.6765 | 2576239.1744 | 1195631.4328 | 2576242.4251 | 1195630.8528
7 | 2576197.7786 | 1195666.2278 | 2576194.3094 | 1195661.6837 | 2576190.971 | 1195655.5715 | 2576186.5026 | 1195647.4592
8 | 2576115.7148 | 1195723.198 | 2576124.3153 | 1195719.3059 | 2576135.0881 | 1195719.4739 | 2576143.222 | 1195719.6362
9 | 2576242.4251 | 1195630.8528 | 2576246.1478 | 1195630.1821 | 2576252.7576 | 1195631.3786 | 2576259.294 | 1195633.7212
10 | 2576242.4251 | 1195630.8528 | 2576242.9151 | 1195623.8026 | 2576242.1402 | 1195618.6363 | 2576239.9542 | 1195613.0086 | 2576239.0292 | 1195610.9038
11 | 2576183.2356 | 1195641.528 | 2576186.5026 | 1195647.4592
12 | 2576341.5321 | 1195650.1911 | 2576345.6012 | 1195649.5779
13 | 2576341.5321 | 1195650.1911 | 2576325.3651 | 1195649.9107 | 2576317.6172 | 1195648.5505
14 | 2576353.1967 | 1195648.4333 | 2576345.6012 | 1195649.5779
15 | 2576311.9332 | 1195647.5527 | 2576317.6172 | 1195648.5505
16 | 2576115.7148 | 1195723.198 | 2576090.8553 | 1195730.4349 | 2576089.6703 | 1195731.7737
17 | 2576264.6077 | 1195635.4927 | 2576260.0283 | 1195633.9844 | 2576259.294 | 1195633.7212
18 | 2576239.0292 | 1195610.9038 | 2576238.0859 | 1195608.7573
19 | 2576183.2356 | 1195641.528 | 2576173.3131 | 1195623.5138 | 2576163.9645 | 1195604.2408 | 2576163.8209 | 1195594.4304
20 | 2576406.5945 | 1195646.9424 | 2576399.2083 | 1195645.9156 | 2576380.5853 | 1195642.9878 | 2576370.0536 | 1195644.0968 | 2576358.7315 | 1195647.5992 | 2576353.1967 | 1195648.4333
21 | 2576311.9332 | 1195647.5527 | 2576309.6986 | 1195647.1604 | 2576288.5456 | 1195642.1641 | 2576284.8599 | 1195641.2288
22 | 2576653.2332 | 1195611.178 | 2576682.6743 | 1195615.0058
23 | 2576623.7582 | 1195604.4127 | 2576634.3603 | 1195608.7243 | 2576653.2332 | 1195611.178
24 | 2576574.3615 | 1195584.3245 | 2576623.7582 | 1195604.4127
25 | 2576574.3615 | 1195584.3245 | 2576570.4899 | 1195611.0541 | 2576575.4701 | 1195618.2495
26 | 2576575.4701 | 1195618.2495 | 2576564.4621 | 1195624.1738 | 2576551.9579 | 1195627.3914 | 2576541.8056 | 1195624.263 | 2576537.1791 | 1195621.4899
27 | 2576575.4701 | 1195618.2495 | 2576584.4819 | 1195621.2264
28 | 2576625.4949 | 1195675.5964 | 2576623.7474 | 1195676.4912
29 | 2576625.4949 | 1195675.5964 | 2576628.0172 | 1195674.305
30 | 2576613.2609 | 1195678.3469 | 2576623.7474 | 1195676.4912 | 2576623.7474 | 1195676.4912
31 | 2576663.6584 | 1195656.0562 | 2576628.0172 | 1195674.305
32 | 2576613.2609 | 1195678.3469 | 2576598.8482 | 1195680.8974
33 | 2576669.236 | 1195653.2004 | 2576663.6584 | 1195656.0562
34 | 2576589.3031 | 1195682.5865 | 2576598.8482 | 1195680.8974
35 | 2576669.236 | 1195653.2004 | 2576686.5602 | 1195651.6232
36 | 2576669.236 | 1195653.2004 | 2576660.0132 | 1195646.1772 | 2576626.6924 | 1195635.1701
37 | 2576589.3031 | 1195682.5865 | 2576585.0051 | 1195683.347 | 2576571.8529 | 1195681.0014
38 | 2576626.6924 | 1195635.1701 | 2576602.6889 | 1195627.2409
39 | 2576602.6889 | 1195627.2409 | 2576584.4819 | 1195621.2264
40 | 2576562.1482 | 1195679.2706 | 2576571.8529 | 1195681.0014
41 | 2576492.7563 | 1195654.4615 | 2576500.7276 | 1195657.0536 | 2576532.189 | 1195673.9276 | 2576562.1482 | 1195679.2706
42 | 2576492.7563 | 1195654.4615 | 2576489.0136 | 1195648.1284 | 2576481.4053 | 1195642.9223 | 2576461.8031 | 1195635.0386
43 | 2576492.7563 | 1195654.4615 | 2576481.5182 | 1195652.2157 | 2576460.4083 | 1195651.4068
44 | 2576436.4316 | 1195624.8347 | 2576461.8031 | 1195635.0386
45 | 2576431.9849 | 1195649.322 | 2576449.9585 | 1195651.0064 | 2576460.4083 | 1195651.4068
46 | 2576436.4316 | 1195624.8347 | 2576442.3907 | 1195605.9899 | 2576441.874 | 1195589.005 | 2576437.9739 | 1195566.0081 | 2576452.5559 | 1195569.9748 | 2576465.337 | 1195571.2583
47 | 2576431.9849 | 1195649.322 | 2576411.6825 | 1195647.4193
48 | 2576396.5407 | 1195587.9505 | 2576401.817 | 1195594.8989
49 | 2576396.5407 | 1195587.9505 | 2576394.1398 | 1195608.7935 | 2576389.6051 | 1195619.873 | 2576389.4519 | 1195625.421
50 | 2576406.5945 | 1195646.9424 | 2576407.0658 | 1195637.0686 | 2576397.2167 | 1195631.638 | 2576389.4519 | 1195625.421
51 | 2576406.5945 | 1195646.9424 | 2576411.6825 | 1195647.4193
52 | 2575384.207 | 1195838.8392 | 2575386.2172 | 1195840.2856 | 2575423.7815 | 1195867.9232 | 2575431.6394 | 1195873.8222
53 | 2575384.207 | 1195838.8392 | 2575367.2757 | 1195826.6565 | 2575354.8494 | 1195818.018
54 | 2575431.6394 | 1195873.8222 | 2575448.0531 | 1195886.1442
55 | 2575307.0013 | 1195775.1227 | 2575306.0555 | 1195778.5062 | 2575306.2746 | 1195781.7404 | 2575307.536 | 1195784.6589 | 2575309.8399 | 1195787.2619 | 2575348.1833 | 1195813.3839 | 2575354.8494 | 1195818.018
56 | 2575307.0013 | 1195775.1227 | 2575323.033 | 1195757.5023 | 2575326.5475 | 1195754.4306
57 | 2575307.0013 | 1195775.1227 | 2575287.2252 | 1195798.7415
58 | 2575342.2731 | 1195747.4951 | 2575335.486 | 1195749.502 | 2575330.5668 | 1195751.8681 | 2575326.5475 | 1195754.4306
59 | 2575342.2731 | 1195747.4951 | 2575344.2327 | 1195751.6114 | 2575347.544 | 1195754.6438 | 2575352.7107 | 1195756.8903 | 2575356.3452 | 1195758.0393
60 | 2575341.4642 | 1195728.7661 | 2575341.7196 | 1195742.6058 | 2575342.2731 | 1195747.4951
61 | 2575360.0489 | 1195726.5872 | 2575376.9477 | 1195724.606 | 2575378.8152 | 1195724.379
62 | 2575341.4642 | 1195728.7661 | 2575360.0489 | 1195726.5872
63 | 2575378.8152 | 1195724.379 | 2575393.804 | 1195722.5567
64 | 2575426.5895 | 1195719.2633 | 2575425.0194 | 1195719.3158 | 2575408.7529 | 1195720.7392 | 2575393.804 | 1195722.5567
65 | 2575466.1995 | 1195718.5034 | 2575455.5497 | 1195718.4895 | 2575441.3201 | 1195718.7705 | 2575426.5895 | 1195719.2633
66 | 2575368.8595 | 1195761.9957 | 2575356.3452 | 1195758.0393
67 | 2575466.1995 | 1195718.5034 | 2575469.9101 | 1195718.5082 | 2575496.0125 | 1195719.1233 | 2575524.7624 | 1195720.706 | 2575553.0045 | 1195722.9246 | 2575559.7857 | 1195723.7528
68 | 2575368.8595 | 1195761.9957 | 2575370.8832 | 1195762.6355
69 | 2575436.9585 | 1195795.0449 | 2575436.7886 | 1195794.819 | 2575434.6545 | 1195793.8864
70 | 2575436.9585 | 1195795.0449 | 2575444.6938 | 1195805.3255 | 2575447.2935 | 1195806.5135
71 | 2575415.6368 | 1195785.5753 | 2575434.6545 | 1195793.8864
72 | 2575453.3215 | 1195809.2683 | 2575447.2935 | 1195806.5135
73 | 2575390.9515 | 1195772.1183 | 2575401.606 | 1195775.8206 | 2575407.8333 | 1195782.165 | 2575415.6368 | 1195785.5753
74 | 2575390.9515 | 1195772.1183 | 2575382.3197 | 1195769.1189 | 2575376.5562 | 1195764.4291 | 2575376.5562 | 1195764.4291
75 | 2575376.5562 | 1195764.4291 | 2575370.8832 | 1195762.6355
76 | 2575564.1781 | 1195724.2892 | 2575559.7857 | 1195723.7528
77 | 2575564.1781 | 1195724.2892 | 2575577.6223 | 1195725.9311
78 | 2575598.889 | 1195728.5284 | 2575577.6223 | 1195725.9311
79 | 2575598.889 | 1195728.5284 | 2575617.9059 | 1195730.8629 | 2575636.9664 | 1195732.6859 | 2575656.0551 | 1195733.953 | 2575675.2317 | 1195734.3861
80 | 2575675.2317 | 1195734.3861 | 2575715.4913 | 1195732.943
81 | 2575675.2317 | 1195734.3861 | 2575683.881 | 1195751.8157 | 2575692.2608 | 1195759.2411 | 2575700.7357 | 1195761.9746 | 2575718.527 | 1195775.7762 | 2575723.904 | 1195788.5278 | 2575725.252 | 1195798.8087
82 | 2575764.2024 | 1195732.8437 | 2575758.0418 | 1195732.6588 | 2575737.0912 | 1195732.5106 | 2575716.5314 | 1195732.9057 | 2575715.4913 | 1195732.943
83 | 2575727.1507 | 1195820.6319 | 2575725.6584 | 1195809.6432 | 2575725.39 | 1195799.8612 | 2575725.252 | 1195798.8087
84 | 2575776.788 | 1195733.2216 | 2575764.2024 | 1195732.8437
85 | 2575727.1507 | 1195820.6319 | 2575735.3246 | 1195828.0581 | 2575748.9965 | 1195833.0496 | 2575753.696 | 1195836.5879 | 2575758.2586 | 1195840.1824 | 2575759.5972 | 1195841.3796
86 | 2576013.4 | 1195899.5772 | 2576014.6287 | 1195897.1017
87 | 2576023.3019 | 1195879.6277 | 2576014.6287 | 1195897.1017
88 | 2576023.3019 | 1195879.6277 | 2576024.5423 | 1195877.1287
89 | 2576024.5423 | 1195877.1287 | 2576036.4684 | 1195853.1011
90 | 2576036.4684 | 1195853.1011 | 2576038.8518 | 1195848.2992
91 | 2576115.4239 | 1195970.8039 | 2576119.0563 | 1195978.9222 | 2576126.16 | 1195987.4761 | 2576130.8855 | 1195992.2281
92 | 2576115.4239 | 1195970.8039 | 2576113.7832 | 1195967.137 | 2576111.838 | 1195957.8394
93 | 2576144.0605 | 1196006.1367 | 2576140.9372 | 1196002.3361 | 2576130.8855 | 1195992.2281
94 | 2576141.5669 | 1195881.0183 | 2576121.2256 | 1195915.7796 | 2576111.9298 | 1195934.3046 | 2576110.3127 | 1195943.2603 | 2576110.3984 | 1195949.43 | 2576111.4454 | 1195955.9626 | 2576111.838 | 1195957.8394
95 | 2576144.0605 | 1196006.1367 | 2576147.8031 | 1196012.414
96 | 2576144.0605 | 1196006.1367 | 2576132.7776 | 1196026.8264 | 2576100.4589 | 1196052.3697 | 2576096.6107 | 1196055.5656
97 | 2576157.086 | 1195853.7025 | 2576156.1577 | 1195857.7862 | 2576152.2919 | 1195862.6265 | 2576143.5003 | 1195877.7143 | 2576141.5669 | 1195881.0183
98 | 2576149.6964 | 1196017.2312 | 2576147.8031 | 1196012.414
99 | 2576083.1485 | 1196066.0053 | 2576094.3925 | 1196057.4079 | 2576096.6107 | 1196055.5656
100 | 2576157.086 | 1195853.7025 | 2576170.2192 | 1195857.4409 | 2576175.0959 | 1195860.3891
101 | 2576157.086 | 1195853.7025 | 2576156.1189 | 1195849.9822 | 2576152.6448 | 1195846.1273 | 2576148.1514 | 1195836.907
102 | 2576149.6964 | 1196017.2312 | 2576152.6551 | 1196031.2936 | 2576153.4432 | 1196037.8607 | 2576153.5712 | 1196042.3666
103 | 2576083.1485 | 1196066.0053 | 2576082.3781 | 1196066.5944
104 | 2576175.0959 | 1195860.3891 | 2576189.2867 | 1195868.9683
105 | 2576148.1514 | 1195836.907 | 2576131.4154 | 1195836.2409
106 | 2576280.8602 | 1195640.2138 | 2576272.5005 | 1195638.0924 | 2576264.6077 | 1195635.4927
107 | 2576284.8599 | 1195641.2288 | 2576280.8602 | 1195640.2138
108 | 2576055.2689 | 1195815.2235 | 2576038.8518 | 1195848.2992
109 | 2576055.2689 | 1195815.2235 | 2576039.8646 | 1195807.7727
110 | 2576055.2689 | 1195815.2235 | 2576067.8014 | 1195821.0874
111 | 2576055.2689 | 1195815.2235 | 2576057.4005 | 1195812.947 | 2576077.279 | 1195775.7805 | 2576079.0934 | 1195770.4037 | 2576079.8407 | 1195764.8977 | 2576078.8668 | 1195761.4108
112 | 2576006.7387 | 1195791.7505 | 2576039.8646 | 1195807.7727
113 | 2576067.8014 | 1195821.0874 | 2576094.7798 | 1195832.3463
114 | 2576067.8014 | 1195821.0874 | 2576072.0985 | 1195806.062 | 2576074.0416 | 1195803.4567
115 | 2576078.8668 | 1195761.4108 | 2576083.1643 | 1195747.0375
116 | 2576151.1554 | 1195474.9861 | 2576125.1134 | 1195467.8668
117 | 2576166.3986 | 1195498.6187 | 2576163.2111 | 1195484.5461 | 2576160.2893 | 1195479.7663 | 2576154.4533 | 1195475.8876 | 2576151.1554 | 1195474.9861
118 | 2576125.1134 | 1195467.8668 | 2576107.6015 | 1195463.0795 | 2576103.6654 | 1195459.9492 | 2576102.7513 | 1195452.3821 | 2576103.0732 | 1195449.2024
119 | 2576164.5996 | 1195547.8524 | 2576164.4495 | 1195525.5743 | 2576165.5 | 1195510.1174 | 2576165.6666 | 1195507.9711 | 2576166.3986 | 1195498.6187
120 | 2576103.0732 | 1195449.2024 | 2576103.412 | 1195445.8562
121 | 2576164.5996 | 1195547.8524 | 2576167.2451 | 1195552.133 | 2576169.1065 | 1195558.4623
122 | 2576164.5996 | 1195547.8524 | 2576157.0037 | 1195545.8484 | 2576145.5476 | 1195546.4838
123 | 2576104.8628 | 1195434.2667 | 2576104.0923 | 1195439.1363 | 2576103.412 | 1195445.8562
124 | 2576163.8209 | 1195594.4304 | 2576163.7652 | 1195590.6232 | 2576168.0205 | 1195572.652 | 2576169.1065 | 1195558.4623
125 | 2576145.5476 | 1195546.4838 | 2576144.4549 | 1195546.5444
126 | 2576104.8628 | 1195434.2667 | 2576108.1711 | 1195413.3573
127 | 2576082.0788 | 1195545.2923 | 2576093.6508 | 1195548.1701 | 2576115.8122 | 1195549.9378 | 2576137.9924 | 1195546.9028 | 2576144.4549 | 1195546.5444
128 | 2575905.53 | 1195485.1672 | 2575901.3226 | 1195483.7547 | 2575860.4693 | 1195466.8899
129 | 2575905.53 | 1195485.1672 | 2575931.4401 | 1195493.8658
130 | 2575943.1196 | 1195497.7869 | 2575931.4401 | 1195493.8658
131 | 2575943.1196 | 1195497.7869 | 2575973.3671 | 1195507.9416
132 | 2576012.4742 | 1195521.0707 | 2575973.3671 | 1195507.9416
133 | 2576012.4742 | 1195521.0707 | 2575996.8317 | 1195493.3792
134 | 2576012.4742 | 1195521.0707 | 2576024.0723 | 1195525.6022
135 | 2576006.7387 | 1195791.7505 | 2575998.8572 | 1195807.9359
136 | 2575963.5296 | 1195771.1469 | 2576006.7387 | 1195791.7505
137 | 2576094.7798 | 1195832.3463 | 2576096.4551 | 1195833.0455 | 2576105.0112 | 1195835.1901 | 2576105.0112 | 1195835.1901
138 | 2576074.0416 | 1195803.4567 | 2576080.4562 | 1195794.8558 | 2576090.7886 | 1195793.5247 | 2576093.7829 | 1195787.9319 | 2576103.0119 | 1195779.3014 | 2576119.5997 | 1195780.1019
139 | 2576089.6703 | 1195731.7737 | 2576086.7373 | 1195735.0873 | 2576083.1643 | 1195747.0375
140 | 2576024.0723 | 1195525.6022 | 2576050.9992 | 1195536.1227
141 | 2576082.0788 | 1195545.2923 | 2576061.141 | 1195540.0852 | 2576050.9992 | 1195536.1227
142 | 2575996.8317 | 1195493.3792 | 2575987.8816 | 1195477.5352 | 2575977.0304 | 1195454.2554 | 2575970.3377 | 1195434.8007
143 | 2575970.3377 | 1195434.8007 | 2575963.2776 | 1195414.2782 | 2575962.9578 | 1195412.7287
144 | 2575962.0094 | 1195408.1325 | 2575962.9578 | 1195412.7287
145 | 2576153.6737 | 1196045.9752 | 2576153.5712 | 1196042.3666
146 | 2576082.3781 | 1196066.5944 | 2576074.608 | 1196074.1741 | 2576069.7148 | 1196079.2076 | 2576065.3671 | 1196085.3839 | 2576056.9335 | 1196099.2583
147 | 2576082.3781 | 1196066.5944 | 2576085.6262 | 1196069.2161 | 2576093.4429 | 1196077.0222 | 2576097.5912 | 1196083.787 | 2576100.4701 | 1196091.2239 | 2576101.4612 | 1196093.5705
148 | 2576131.4154 | 1195836.2409 | 2576105.0112 | 1195835.1901
149 | 2576232.418 | 1195899.54 | 2576229.2995 | 1195898.2046 | 2576228.3577 | 1195897.5794
150 | 2576204.7767 | 1195879.775 | 2576217.7964 | 1195890.5686 | 2576228.3577 | 1195897.5794
151 | 2576240.5299 | 1195902.3954 | 2576235.0609 | 1195900.6718 | 2576232.418 | 1195899.54
152 | 2576204.7767 | 1195879.775 | 2576198.3519 | 1195874.4487 | 2576189.2867 | 1195868.9683
153 | 2576240.5299 | 1195902.3954 | 2576250.8129 | 1195904.0108 | 2576253.0491 | 1195904.6018
154 | 2576258.3701 | 1195906.0083 | 2576253.0491 | 1195904.6018
155 | 2576258.3701 | 1195906.0083 | 2576273.4773 | 1195910.0015 | 2576292.3105 | 1195916.1409 | 2576308.6504 | 1195925.5921 | 2576318.2888 | 1195932.5816
156 | 2576153.6737 | 1196045.9752 | 2576157.0239 | 1196051.2647 | 2576158.6302 | 1196056.7056 | 2576159.9993 | 1196073.3091 | 2576162.0776 | 1196088.2088 | 2576163.9985 | 1196096.1165 | 2576166.3233 | 1196102.1882 | 2576169.3037 | 1196106.4564 | 2576173.1512 | 1196110.3987
157 | 2576153.6737 | 1196045.9752 | 2576152.7272 | 1196063.9334
158 | 2576173.1512 | 1196110.3987 | 2576196.8443 | 1196097.6082 | 2576203.3183 | 1196093.7076
159 | 2576152.0249 | 1196086.3804 | 2576152.0666 | 1196076.4647 | 2576152.7272 | 1196063.9334
160 | 2576233.7652 | 1195598.9258 | 2576238.0859 | 1195608.7573
161 | 2576318.2888 | 1195932.5816 | 2576343.1432 | 1195950.6053
162 | 2576365.3855 | 1195967.2007 | 2576357.9126 | 1195961.3157 | 2576343.1432 | 1195950.6053
163 | 2576379.4108 | 1195978.246 | 2576365.3855 | 1195967.2007
164 | 2575776.788 | 1195733.2216 | 2575783.1854 | 1195733.4137
165 | 2575906.8302 | 1195746.8953 | 2575902.7631 | 1195745.5786 | 2575886.3314 | 1195741.9876 | 2575880.6622 | 1195741.0831
166 | 2575841.271 | 1195735.8794 | 2575854.8023 | 1195736.9571 | 2575880.6622 | 1195741.0831
167 | 2575906.8302 | 1195746.8953 | 2575914.396 | 1195749.3447 | 2575923.5721 | 1195753.1285
168 | 2575807.1305 | 1195734.1448 | 2575830.0963 | 1195734.9895 | 2575841.271 | 1195735.8794
169 | 2575925.5828 | 1195753.9576 | 2575923.5721 | 1195753.1285
170 | 2575807.1305 | 1195734.1448 | 2575805.3259 | 1195734.0784 | 2575790.1128 | 1195733.6217
171 | 2575925.5828 | 1195753.9576 | 2575948.0207 | 1195764.1216
172 | 2575790.1128 | 1195733.6217 | 2575783.1854 | 1195733.4137
173 | 2575963.5296 | 1195771.1469 | 2575948.0207 | 1195764.1216
174 | 2576152.0249 | 1196086.3804 | 2576152.0159 | 1196088.527 | 2576152.6656 | 1196104.2884 | 2576152.9426 | 1196107.1994
175 | 2576157.0738 | 1196136.1565 | 2576154.1527 | 1196119.9131 | 2576152.9426 | 1196107.1994
176 | 2575924.0369 | 1195829.5493 | 2575939.7859 | 1195806.2595
177 | 2575963.5296 | 1195771.1469 | 2575939.7859 | 1195806.2595
178 | 2575924.0369 | 1195829.5493 | 2575919.0544 | 1195836.9175 | 2575914.9255 | 1195838.8241 | 2575909.5819 | 1195837.9897 | 2575887.7591 | 1195824.0595
179 | 2575872.9969 | 1195814.6363 | 2575887.7591 | 1195824.0595
180 | 2575988.7793 | 1195828.6316 | 2575998.8572 | 1195807.9359
181 | 2576025.9548 | 1196180.4269 | 2576021.7386 | 1196173.8514 | 2576020.2043 | 1196169.2663 | 2576019.8427 | 1196164.5985 | 2576020.6206 | 1196161.0379 | 2576022.5086 | 1196156.9837 | 2576055.4837 | 1196101.6435 | 2576056.9335 | 1196099.2583
182 | 2576025.9548 | 1196180.4269 | 2576037.2658 | 1196197.1793 | 2576044.3336 | 1196207.1015
183 | 2576000.5025 | 1196198.8615 | 2576001.6993 | 1196197.178 | 2576008.1831 | 1196189.9147 | 2576012.1378 | 1196186.4191 | 2576018.0736 | 1196183.06 | 2576025.9548 | 1196180.4269
184 | 2576000.5025 | 1196198.8615 | 2575989.3099 | 1196192.581 | 2575977.2636 | 1196188.105 | 2575973.8191 | 1196187.752
185 | 2576000.5025 | 1196198.8615 | 2575991.3676 | 1196214.5003
186 | 2575973.8191 | 1196187.752 | 2575969.4588 | 1196190.7712 | 2575962.1436 | 1196205.0773
187 | 2575989.5933 | 1196217.5378 | 2575991.3676 | 1196214.5003
188 | 2575962.1436 | 1196205.0773 | 2575953.7824 | 1196221.4291
189 | 2575989.5933 | 1196217.5378 | 2575982.8767 | 1196230.2925
190 | 2575977.3837 | 1196327.7196 | 2575976.193 | 1196336.4233
191 | 2575977.3837 | 1196327.7196 | 2575980.145 | 1196307.5355
192 | 2575974.011 | 1196352.3733 | 2575976.193 | 1196336.4233
193 | 2575946.3597 | 1196297.6331 | 2575975.7288 | 1196302.3616 | 2575980.145 | 1196307.5355 | 2575980.145 | 1196307.5355
194 | 2575946.3597 | 1196297.6331 | 2575946.911 | 1196296.4486
195 | 2575946.911 | 1196296.4486 | 2575951.782 | 1196285.9827 | 2575956.2074 | 1196278.1652
196 | 2575898.7982 | 1196358.3025 | 2575900.5239 | 1196361.2193 | 2575903.572 | 1196363.3748 | 2575912.6495 | 1196367.6316
197 | 2575898.7982 | 1196358.3025 | 2575896.8039 | 1196345.4925
198 | 2575956.2074 | 1196278.1652 | 2575965.1165 | 1196262.4273 | 2575965.193 | 1196262.2926
199 | 2575965.193 | 1196262.2926 | 2575974.1527 | 1196246.5087
200 | 2575991.3153 | 1196248.2559 | 2575992.5072 | 1196248.7651
201 | 2575976.7041 | 1196242.014 | 2575991.3153 | 1196248.2559
202 | 2575976.7041 | 1196242.014 | 2575974.1527 | 1196246.5087
203 | 2575976.7041 | 1196242.014 | 2575982.8767 | 1196230.2925
204 | 2575953.7824 | 1196221.4291 | 2575945.59 | 1196237.4508
205 | 2575945.59 | 1196237.4508 | 2575937.5022 | 1196253.2679
206 | 2575937.5022 | 1196253.2679 | 2575929.0722 | 1196269.7545
207 | 2575929.0722 | 1196269.7545 | 2575926.2809 | 1196275.2132 | 2575924.6075 | 1196287.3334
208 | 2575924.6075 | 1196287.3334 | 2575923.7055 | 1196293.867 | 2575920.4866 | 1196296.5704 | 2575917.8249 | 1196296.4798
209 | 2575908.8074 | 1196296.173 | 2575917.8249 | 1196296.4798
210 | 2575908.8074 | 1196296.173 | 2575896.8039 | 1196345.4925

## bus_geodata
| x | y | coords
0 | 2576238.5539 | 1195735.569
1 | 2576270.6143 | 1195716.1932
2 | 2576214.7936 | 1195707.1486
3 | 2576203.603 | 1195759.1358
4 | 2576179.4692 | 1195713.1596
5 | 2576197.7786 | 1195666.2278
6 | 2576143.222 | 1195719.6362
7 | 2576242.4251 | 1195630.8528
8 | 2576186.5026 | 1195647.4592
9 | 2576341.5321 | 1195650.1911
10 | 2576345.6012 | 1195649.5779
11 | 2576317.6172 | 1195648.5505
12 | 2576115.7148 | 1195723.198
13 | 2576259.294 | 1195633.7212
14 | 2576239.0292 | 1195610.9038
15 | 2576183.2356 | 1195641.528
16 | 2576353.1967 | 1195648.4333
17 | 2576311.9332 | 1195647.5527
18 | 2576682.6743 | 1195615.0058
19 | 2576653.2332 | 1195611.178
20 | 2576623.7582 | 1195604.4127
21 | 2576574.3615 | 1195584.3245
22 | 2576575.4701 | 1195618.2495
23 | 2576625.4949 | 1195675.5964
24 | 2576623.7474 | 1195676.4912
25 | 2576628.0172 | 1195674.305
26 | 2576613.2609 | 1195678.3469
27 | 2576663.6584 | 1195656.0562
28 | 2576598.8482 | 1195680.8974
29 | 2576669.236 | 1195653.2004
30 | 2576589.3031 | 1195682.5865
31 | 2576686.5602 | 1195651.6232
32 | 2576626.6924 | 1195635.1701
33 | 2576602.6889 | 1195627.2409
34 | 2576584.4819 | 1195621.2264
35 | 2576537.1791 | 1195621.4899
36 | 2576571.8529 | 1195681.0014
37 | 2576562.1482 | 1195679.2706
38 | 2576492.7563 | 1195654.4615
39 | 2576461.8031 | 1195635.0386
40 | 2576460.4083 | 1195651.4068
41 | 2576436.4316 | 1195624.8347
42 | 2576431.9849 | 1195649.322
43 | 2576465.337 | 1195571.2583
44 | 2576401.817 | 1195594.8989
45 | 2576396.5407 | 1195587.9505
46 | 2576389.4519 | 1195625.421
47 | 2576411.6825 | 1195647.4193
48 | 2575384.207 | 1195838.8392
49 | 2575431.6394 | 1195873.8222
50 | 2575354.8494 | 1195818.018
51 | 2575448.0531 | 1195886.1442
52 | 2575307.0013 | 1195775.1227
53 | 2575326.5475 | 1195754.4306
54 | 2575287.2252 | 1195798.7415
55 | 2575342.2731 | 1195747.4951
56 | 2575360.0489 | 1195726.5872
57 | 2575378.8152 | 1195724.379
58 | 2575341.4642 | 1195728.7661
59 | 2575393.804 | 1195722.5567
60 | 2575426.5895 | 1195719.2633
61 | 2575356.3452 | 1195758.0393
62 | 2575466.1995 | 1195718.5034
63 | 2575368.8595 | 1195761.9957
64 | 2575436.9585 | 1195795.0449
65 | 2575434.6545 | 1195793.8864
66 | 2575447.2935 | 1195806.5135
67 | 2575415.6368 | 1195785.5753
68 | 2575453.3215 | 1195809.2683
69 | 2575390.9515 | 1195772.1183
70 | 2575376.5562 | 1195764.4291
71 | 2575559.7857 | 1195723.7528
72 | 2575564.1781 | 1195724.2892
73 | 2575577.6223 | 1195725.9311
74 | 2575598.889 | 1195728.5284
75 | 2575370.8832 | 1195762.6355
76 | 2575675.2317 | 1195734.3861
77 | 2575715.4913 | 1195732.943
78 | 2575725.252 | 1195798.8087
79 | 2575764.2024 | 1195732.8437
80 | 2575727.1507 | 1195820.6319
81 | 2576013.4 | 1195899.5772
82 | 2576014.6287 | 1195897.1017
83 | 2576023.3019 | 1195879.6277
84 | 2576024.5423 | 1195877.1287
85 | 2576036.4684 | 1195853.1011
86 | 2576406.5945 | 1195646.9424
87 | 2576115.4239 | 1195970.8039
88 | 2576130.8855 | 1195992.2281
89 | 2576111.838 | 1195957.8394
90 | 2576144.0605 | 1196006.1367
91 | 2576141.5669 | 1195881.0183
92 | 2576147.8031 | 1196012.414
93 | 2576096.6107 | 1196055.5656
94 | 2576157.086 | 1195853.7025
95 | 2576149.6964 | 1196017.2312
96 | 2576083.1485 | 1196066.0053
97 | 2576175.0959 | 1195860.3891
98 | 2576148.1514 | 1195836.907
99 | 2576280.8602 | 1195640.2138
100 | 2576264.6077 | 1195635.4927
101 | 2576284.8599 | 1195641.2288
102 | 2576038.8518 | 1195848.2992
103 | 2576055.2689 | 1195815.2235
104 | 2576039.8646 | 1195807.7727
105 | 2576067.8014 | 1195821.0874
106 | 2576078.8668 | 1195761.4108
107 | 2576151.1554 | 1195474.9861
108 | 2576125.1134 | 1195467.8668
109 | 2576166.3986 | 1195498.6187
110 | 2576103.0732 | 1195449.2024
111 | 2576164.5996 | 1195547.8524
112 | 2576103.412 | 1195445.8562
113 | 2576169.1065 | 1195558.4623
114 | 2576145.5476 | 1195546.4838
115 | 2576104.8628 | 1195434.2667
116 | 2576163.8209 | 1195594.4304
117 | 2576144.4549 | 1195546.5444
118 | 2575905.53 | 1195485.1672
119 | 2575860.4693 | 1195466.8899
120 | 2575931.4401 | 1195493.8658
121 | 2575943.1196 | 1195497.7869
122 | 2575973.3671 | 1195507.9416
123 | 2576012.4742 | 1195521.0707
124 | 2576006.7387 | 1195791.7505
125 | 2576094.7798 | 1195832.3463
126 | 2576074.0416 | 1195803.4567
127 | 2576083.1643 | 1195747.0375
128 | 2576024.0723 | 1195525.6022
129 | 2576050.9992 | 1195536.1227
130 | 2576082.0788 | 1195545.2923
131 | 2575996.8317 | 1195493.3792
132 | 2575970.3376 | 1195434.8007
133 | 2575962.9578 | 1195412.7287
134 | 2576153.5712 | 1196042.3666
135 | 2576082.3781 | 1196066.5944
136 | 2576119.5997 | 1195780.1019
137 | 2576089.6703 | 1195731.7737
138 | 2576131.4154 | 1195836.2409
139 | 2576105.0112 | 1195835.1901
140 | 2576108.1711 | 1195413.3573
141 | 2576228.3577 | 1195897.5794
142 | 2576232.418 | 1195899.54
143 | 2576204.7767 | 1195879.775
144 | 2576240.5299 | 1195902.3954
145 | 2576189.2867 | 1195868.9683
146 | 2576253.0491 | 1195904.6018
147 | 2576258.3701 | 1195906.0083
148 | 2575962.0094 | 1195408.1325
149 | 2576153.6737 | 1196045.9752
150 | 2576173.1512 | 1196110.3987
151 | 2576152.7272 | 1196063.9334
152 | 2576238.0859 | 1195608.7573
153 | 2576233.7652 | 1195598.9258
154 | 2575759.5972 | 1195841.3796
155 | 2576318.2888 | 1195932.5816
156 | 2576343.1432 | 1195950.6053
157 | 2576365.3855 | 1195967.2007
158 | 2576379.4108 | 1195978.246
159 | 2575776.788 | 1195733.2216
160 | 2575880.6622 | 1195741.0831
161 | 2575906.8302 | 1195746.8953
162 | 2575841.271 | 1195735.8794
163 | 2575923.5721 | 1195753.1285
164 | 2575807.1305 | 1195734.1448
165 | 2575925.5828 | 1195753.9576
166 | 2575790.1128 | 1195733.6217
167 | 2575948.0207 | 1195764.1216
168 | 2575783.1854 | 1195733.4137
169 | 2576152.0249 | 1196086.3804
170 | 2576152.9426 | 1196107.1994
171 | 2576157.0738 | 1196136.1565
172 | 2576203.3183 | 1196093.7076
173 | 2575939.7859 | 1195806.2595
174 | 2575924.0369 | 1195829.5493
175 | 2575963.5296 | 1195771.1469
176 | 2575887.7591 | 1195824.0595
177 | 2575872.9969 | 1195814.6363
178 | 2575998.8572 | 1195807.9359
179 | 2575988.7793 | 1195828.6316
180 | 2576056.9335 | 1196099.2583
181 | 2576101.4612 | 1196093.5705
182 | 2576025.9548 | 1196180.4269
183 | 2576044.3336 | 1196207.1015
184 | 2576000.5025 | 1196198.8615
185 | 2575973.8191 | 1196187.752
186 | 2575991.3676 | 1196214.5003
187 | 2575962.1436 | 1196205.0773
188 | 2575989.5933 | 1196217.5378
189 | 2575977.3837 | 1196327.7196
190 | 2575976.193 | 1196336.4233
191 | 2575980.145 | 1196307.5355
192 | 2575974.011 | 1196352.3733
193 | 2575946.3597 | 1196297.6331
194 | 2575946.911 | 1196296.4486
195 | 2575912.6495 | 1196367.6316
196 | 2575898.7982 | 1196358.3025
197 | 2575956.2074 | 1196278.1652
198 | 2575965.193 | 1196262.2926
199 | 2575991.3153 | 1196248.2559
200 | 2575992.5072 | 1196248.7651
201 | 2575976.7041 | 1196242.014
202 | 2575974.1527 | 1196246.5087
203 | 2575982.8767 | 1196230.2925
204 | 2575953.7824 | 1196221.4291
205 | 2575945.59 | 1196237.4508
206 | 2575937.5022 | 1196253.2679
207 | 2575929.0722 | 1196269.7545
208 | 2575924.6075 | 1196287.3334
209 | 2575917.8249 | 1196296.4798
210 | 2575908.8074 | 1196296.1729
211 | 2575896.8039 | 1196345.4925
212 | 2576055.2689 | 1195815.2235

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1