## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_69-25_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_69-25_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_69-25_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_69-25_0_4_node_92 | 0.4 | n |  | TRUE
4 | bus_LV_69-25_0_4_node_91 | 0.4 | n |  | TRUE
5 | bus_LV_69-25_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_69-25_0_4_node_44 | 0.4 | n |  | TRUE
7 | bus_LV_69-25_0_4_node_75 | 0.4 | n |  | TRUE
8 | bus_LV_69-25_0_4_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_69-25_0_4_node_93 | 0.4 | n |  | TRUE
10 | bus_LV_69-25_0_4_node_94 | 0.4 | n |  | TRUE
11 | bus_LV_69-25_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_69-25_0_4_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_69-25_0_4_node_95 | 0.4 | n |  | TRUE
14 | bus_LV_69-25_0_4_node_65 | 0.4 | n |  | TRUE
15 | bus_LV_69-25_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_69-25_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_69-25_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_69-25_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_69-25_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_69-25_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_69-25_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_69-25_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_69-25_0_4_node_62 | 0.4 | n |  | TRUE
24 | bus_LV_69-25_0_4_node_76 | 0.4 | n |  | TRUE
25 | bus_LV_69-25_0_4_node_63 | 0.4 | n |  | TRUE
26 | bus_LV_69-25_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_69-25_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_69-25_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_69-25_0_4_node_42 | 0.4 | n |  | TRUE
30 | bus_LV_69-25_0_4_node_53 | 0.4 | n |  | TRUE
31 | bus_LV_69-25_0_4_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_69-25_0_4_node_64 | 0.4 | n |  | TRUE
33 | bus_LV_69-25_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_69-25_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_69-25_0_4_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_69-25_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_69-25_0_4_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_69-25_0_4_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_69-25_0_4_node_60 | 0.4 | n |  | TRUE
40 | bus_LV_69-25_0_4_node_84 | 0.4 | n |  | TRUE
41 | bus_LV_69-25_0_4_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_69-25_0_4_node_87 | 0.4 | n |  | TRUE
43 | bus_LV_69-25_0_4_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_69-25_0_4_node_52 | 0.4 | n |  | TRUE
45 | bus_LV_69-25_0_4_node_85 | 0.4 | n |  | TRUE
46 | bus_LV_69-25_0_4_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_69-25_0_4_node_25 | 0.4 | n |  | TRUE
48 | bus_LV_69-25_0_4_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_69-25_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_69-25_0_4_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_69-25_0_4_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_69-25_0_4_node_66 | 0.4 | n |  | TRUE
53 | bus_LV_69-25_0_4_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_69-25_0_4_node_69 | 0.4 | n |  | TRUE
55 | bus_LV_69-25_0_4_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_69-25_0_4_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_69-25_0_4_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_69-25_0_4_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_69-25_0_4_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_69-25_0_4_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_69-25_0_4_node_39 | 0.4 | n |  | TRUE
62 | bus_LV_69-25_0_4_node_79 | 0.4 | n |  | TRUE
63 | bus_LV_69-25_0_4_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_69-25_0_4_node_88 | 0.4 | n |  | TRUE
65 | bus_LV_69-25_0_4_node_81 | 0.4 | n |  | TRUE
66 | bus_LV_69-25_0_4_node_80 | 0.4 | n |  | TRUE
67 | bus_LV_69-25_0_4_node_83 | 0.4 | n |  | TRUE
68 | bus_LV_69-25_0_4_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_69-25_0_4_node_47 | 0.4 | n |  | TRUE
70 | bus_LV_69-25_0_4_node_86 | 0.4 | n |  | TRUE
71 | bus_LV_69-25_0_4_node_41 | 0.4 | n |  | TRUE
72 | bus_LV_69-25_0_4_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_69-25_0_4_node_45 | 0.4 | n |  | TRUE
74 | bus_LV_69-25_0_4_node_48 | 0.4 | n |  | TRUE
75 | bus_LV_69-25_0_4_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_69-25_0_4_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_69-25_0_4_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_69-25_0_4_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_69-25_0_4_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_69-25_0_4_node_55 | 0.4 | n |  | TRUE
81 | bus_LV_69-25_0_4_node_56 | 0.4 | n |  | TRUE
82 | bus_LV_69-25_0_4_node_57 | 0.4 | n |  | TRUE
83 | bus_LV_69-25_0_4_node_59 | 0.4 | n |  | TRUE
84 | bus_LV_69-25_0_4_node_90 | 0.4 | n |  | TRUE
85 | bus_LV_69-25_0_4_node_89 | 0.4 | n |  | TRUE
86 | bus_LV_69-25_0_4_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_69-25_0_4_node_68 | 0.4 | n |  | TRUE
88 | bus_LV_69-25_0_4_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_69-25_0_4_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_69-25_0_4_node_74 | 0.4 | n |  | TRUE
91 | bus_MV_552_0_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_69-25_0_4_load_0 | 0 | 0.029192 | 0.0073163 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_69-25_0_4_load_92 | 3 | 0.0024141 | 0.00060502 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_69-25_0_4_load_91 | 4 | 0.003564 | 0.00089321 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_69-25_0_4_load_5 | 5 | 0.017629 | 0.0044182 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_69-25_0_4_load_75 | 7 | 0.004834 | 0.0012115 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_69-25_0_4_load_3 | 8 | 0.048667 | 0.012197 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_69-25_0_4_load_93 | 9 | 0.0034862 | 0.00087371 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_69-25_0_4_load_94 | 10 | 0.0021267 | 0.00053299 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_69-25_0_4_load_6 | 11 | 0.015951 | 0.0039977 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_69-25_0_4_load_95 | 13 | 0.0096891 | 0.0024283 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_69-25_0_4_load_7 | 15 | 0.010277 | 0.0025757 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_69-25_0_4_load_8 | 16 | 0.0070406 | 0.0017645 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_69-25_0_4_load_10 | 18 | 0.0071579 | 0.0017939 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_69-25_0_4_load_12 | 20 | 0.0039595 | 0.00099235 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_69-25_0_4_load_15 | 21 | 0.0034595 | 0.00086703 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_69-25_0_4_load_13 | 22 | 0.0075643 | 0.0018958 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_69-25_0_4_load_62 | 23 | 0.0061485 | 0.001541 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_69-25_0_4_load_76 | 24 | 0.0054448 | 0.0013646 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_69-25_0_4_load_16 | 27 | 0.0062161 | 0.0015579 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_69-25_0_4_load_40 | 31 | 0.012865 | 0.0032243 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_69-25_0_4_load_64 | 32 | 0.0063651 | 0.0015952 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_69-25_0_4_load_18 | 33 | 0.0056126 | 0.0014067 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_69-25_0_4_load_19 | 34 | 0.010079 | 0.0025259 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_69-25_0_4_load_21 | 36 | 0.005113 | 0.0012814 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_69-25_0_4_load_23 | 38 | 0.0046699 | 0.0011704 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_69-25_0_4_load_60 | 39 | 0.0097835 | 0.002452 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_69-25_0_4_load_84 | 40 | 0.013834 | 0.003467 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_69-25_0_4_load_54 | 41 | 0.0077294 | 0.0019372 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_69-25_0_4_load_87 | 42 | 0.0046647 | 0.0011691 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_69-25_0_4_load_85 | 45 | 0.0078453 | 0.0019662 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_69-25_0_4_load_24 | 46 | 0.0074841 | 0.0018757 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_69-25_0_4_load_27 | 48 | 0.0094055 | 0.0023572 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_69-25_0_4_load_28 | 49 | 0.0056193 | 0.0014083 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_69-25_0_4_load_29 | 50 | 0.0031784 | 0.00079658 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_69-25_0_4_load_31 | 51 | 0.0028859 | 0.00072327 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_69-25_0_4_load_66 | 52 | 0.0023843 | 0.00059756 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_69-25_0_4_load_32 | 53 | 0.012253 | 0.0030709 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_69-25_0_4_load_33 | 55 | 0.0045728 | 0.0011461 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_69-25_0_4_load_36 | 58 | 0.0023912 | 0.00059928 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_69-25_0_4_load_37 | 59 | 0.014334 | 0.0035923 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_69-25_0_4_load_38 | 60 | 0.010646 | 0.0026681 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_69-25_0_4_load_39 | 61 | 0.0045728 | 0.0011461 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_69-25_0_4_load_79 | 62 | 0.00045701 | 0.00011454 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_69-25_0_4_load_88 | 64 | 0.0045779 | 0.0011473 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_69-25_0_4_load_81 | 65 | 0.0018611 | 0.00046642 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_69-25_0_4_load_80 | 66 | 0.001439 | 0.00036065 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_69-25_0_4_load_83 | 67 | 0.003426 | 0.00085864 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_69-25_0_4_load_61 | 68 | 0.0041767 | 0.0010468 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_69-25_0_4_load_47 | 69 | 0.0087616 | 0.0021959 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_69-25_0_4_load_86 | 70 | 0.0046882 | 0.001175 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_69-25_0_4_load_50 | 72 | 0.011633 | 0.0029156 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_69-25_0_4_load_45 | 73 | 0.0074046 | 0.0018558 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_69-25_0_4_load_46 | 75 | 0.0041767 | 0.0010468 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_69-25_0_4_load_51 | 76 | 0.010775 | 0.0027005 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_69-25_0_4_load_58 | 78 | 0.0033502 | 0.00083964 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_69-25_0_4_load_70 | 79 | 0.01375 | 0.0034461 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_69-25_0_4_load_55 | 80 | 0.0030663 | 0.00076849 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_69-25_0_4_load_56 | 81 | 0.0033481 | 0.0008391 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_69-25_0_4_load_57 | 82 | 0.0030633 | 0.00076774 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_69-25_0_4_load_59 | 83 | 0.003063 | 0.00076765 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_69-25_0_4_load_90 | 84 | 0.0030633 | 0.00076775 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_69-25_0_4_load_89 | 85 | 0.0030663 | 0.00076849 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_69-25_0_4_load_67 | 86 | 0.0023768 | 0.00059568 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_69-25_0_4_load_68 | 87 | 0.0024149 | 0.00060522 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_69-25_0_4_load_71 | 88 | 0.0213 | 0.0053383 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_69-25_0_4_load_74 | 90 | 0.0030633 | 0.00076775 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_69-25_0_4_line_0 |  | 0 | 1 | 0.024411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_69-25_0_4_line_1 |  | 1 | 2 | 0.031584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_69-25_0_4_line_2 |  | 2 | 4 | 0.028218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_69-25_0_4_line_3 |  | 3 | 4 | 0.028452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_69-25_0_4_line_4 |  | 3 | 5 | 0.034395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_69-25_0_4_line_5 |  | 4 | 6 | 0.018407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_69-25_0_4_line_6 |  | 5 | 7 | 0.0099567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_69-25_0_4_line_7 |  | 6 | 9 | 0.017262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_69-25_0_4_line_8 |  | 6 | 71 | 0.047573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_69-25_0_4_line_9 |  | 8 | 9 | 0.026873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_69-25_0_4_line_10 |  | 9 | 10 | 0.028038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_69-25_0_4_line_11 |  | 11 | 12 | 0.023275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_69-25_0_4_line_12 |  | 12 | 13 | 0.018245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_69-25_0_4_line_13 |  | 12 | 14 | 0.045565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_69-25_0_4_line_14 |  | 14 | 32 | 0.0085432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_69-25_0_4_line_15 |  | 14 | 28 | 0.039226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_69-25_0_4_line_16 |  | 15 | 16 | 0.033503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_69-25_0_4_line_17 |  | 15 | 17 | 0.021718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_69-25_0_4_line_18 |  | 16 | 18 | 0.013988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_69-25_0_4_line_19 |  | 17 | 19 | 0.016064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_69-25_0_4_line_20 |  | 17 | 20 | 0.013602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_69-25_0_4_line_21 |  | 19 | 21 | 0.015043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_69-25_0_4_line_22 |  | 19 | 22 | 0.030495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_69-25_0_4_line_23 |  | 20 | 23 | 0.049642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_69-25_0_4_line_24 |  | 21 | 24 | 0.026108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_69-25_0_4_line_25 |  | 23 | 25 | 0.025063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_69-25_0_4_line_26 |  | 24 | 30 | 0.0067828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_69-25_0_4_line_27 |  | 25 | 54 | 0.016673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_69-25_0_4_line_28 |  | 25 | 86 | 0.023041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_69-25_0_4_line_29 |  | 26 | 27 | 0.022986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_69-25_0_4_line_30 |  | 26 | 28 | 0.004168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_69-25_0_4_line_31 |  | 27 | 29 | 0.021723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_69-25_0_4_line_32 |  | 29 | 31 | 0.004384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_69-25_0_4_line_33 |  | 30 | 44 | 0.013051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_69-25_0_4_line_34 |  | 30 | 53 | 0.026568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_69-25_0_4_line_35 |  | 31 | 71 | 0.029437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_69-25_0_4_line_36 |  | 32 | 48 | 0.020851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_69-25_0_4_line_37 |  | 33 | 34 | 0.00019823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_69-25_0_4_line_38 |  | 33 | 35 | 0.017685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_69-25_0_4_line_39 |  | 34 | 36 | 0.014594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_69-25_0_4_line_40 |  | 35 | 37 | 0.007224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_69-25_0_4_line_41 |  | 35 | 38 | 0.013625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_69-25_0_4_line_42 |  | 36 | 39 | 0.0015841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_69-25_0_4_line_43 |  | 37 | 40 | 0.014132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_69-25_0_4_line_44 |  | 37 | 41 | 0.0080663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_69-25_0_4_line_45 |  | 38 | 42 | 0.00019504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_69-25_0_4_line_46 |  | 39 | 43 | 0.016861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_69-25_0_4_line_47 |  | 41 | 44 | 0.018168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_69-25_0_4_line_48 |  | 42 | 45 | 0.0023493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_69-25_0_4_line_49 |  | 43 | 72 | 0.020938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_69-25_0_4_line_50 |  | 43 | 71 | 0.005984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_69-25_0_4_line_51 |  | 44 | 73 | 0.019725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_69-25_0_4_line_52 |  | 45 | 70 | 0.022432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_69-25_0_4_line_53 |  | 46 | 47 | 0.019685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_69-25_0_4_line_54 |  | 47 | 48 | 0.013731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_69-25_0_4_line_55 |  | 49 | 50 | 0.010563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_69-25_0_4_line_56 |  | 50 | 51 | 0.020897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_69-25_0_4_line_57 |  | 51 | 52 | 0.012916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_69-25_0_4_line_58 |  | 52 | 54 | 0.015317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_69-25_0_4_line_59 |  | 55 | 56 | 0.051896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_69-25_0_4_line_60 |  | 55 | 57 | 0.029983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_69-25_0_4_line_61 |  | 56 | 58 | 0.022343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_69-25_0_4_line_62 |  | 57 | 59 | 0.040834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_69-25_0_4_line_63 |  | 57 | 60 | 0.017369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_69-25_0_4_line_64 |  | 57 | 61 | 0.01675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_69-25_0_4_line_65 |  | 58 | 62 | 0.095958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_69-25_0_4_line_66 |  | 60 | 63 | 0.012001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_69-25_0_4_line_67 |  | 61 | 64 | 0.00020232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_69-25_0_4_line_68 |  | 62 | 65 | 0.043801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_69-25_0_4_line_69 |  | 63 | 68 | 0.014356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_69-25_0_4_line_70 |  | 63 | 69 | 0.0024263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_69-25_0_4_line_71 |  | 64 | 70 | 0.007515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_69-25_0_4_line_72 |  | 65 | 66 | 0.031187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_69-25_0_4_line_73 |  | 66 | 67 | 0.06274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_69-25_0_4_line_74 |  | 68 | 78 | 0.0064975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_69-25_0_4_line_75 |  | 69 | 75 | 0.0058695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_69-25_0_4_line_76 |  | 72 | 74 | 0.029748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_69-25_0_4_line_77 |  | 74 | 76 | 0.010896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_69-25_0_4_line_78 |  | 76 | 77 | 0.00695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_69-25_0_4_line_79 |  | 77 | 79 | 0.014271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_69-25_0_4_line_80 |  | 78 | 81 | 0.022099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_69-25_0_4_line_81 |  | 80 | 81 | 0.01737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_69-25_0_4_line_82 |  | 80 | 82 | 0.0061758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_69-25_0_4_line_83 |  | 82 | 83 | 0.0061724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_69-25_0_4_line_84 |  | 83 | 84 | 0.0063604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_69-25_0_4_line_85 |  | 84 | 85 | 0.0061743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_69-25_0_4_line_86 |  | 85 | 90 | 0.0061743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_69-25_0_4_line_87 |  | 86 | 87 | 0.023179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_69-25_0_4_line_88 |  | 88 | 89 | 0.016725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_69-25_0_4_line_89 |  | 89 | 90 | 0.020832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_69-25_0_4_trafo_60 | 0.63 MVA 20/0.4 kV | 91 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2688392.9473 | 1251783.4828 | 2688416.9223 | 1251788.0762
1 | 2688392.9473 | 1251783.4828 | 2688386.0937 | 1251814.3151
2 | 2688374.3235 | 1251839.961 | 2688386.0937 | 1251814.3151
3 | 2688401.5282 | 1251848.2934 | 2688374.3235 | 1251839.961
4 | 2688401.5282 | 1251848.2934 | 2688432.5374 | 1251833.4116
5 | 2688356.7234 | 1251834.5703 | 2688374.3235 | 1251839.961
6 | 2688432.5374 | 1251833.4116 | 2688441.7461 | 1251837.1979
7 | 2688356.7234 | 1251834.5703 | 2688340.218 | 1251829.5158
8 | 2688356.7234 | 1251834.5703 | 2688341.6181 | 1251879.6906
9 | 2688340.218 | 1251829.5158 | 2688346.7025 | 1251803.4368
10 | 2688313.4087 | 1251821.3059 | 2688340.218 | 1251829.5158
11 | 2688243.0451 | 1251796.2696 | 2688253.4555 | 1251775.4521
12 | 2688255.6641 | 1251807.0101 | 2688256.1787 | 1251804.894 | 2688253.9231 | 1251801.7691 | 2688249.9169 | 1251799.1074 | 2688244.0869 | 1251796.7633 | 2688243.0451 | 1251796.2696
13 | 2688243.0451 | 1251796.2696 | 2688241.5045 | 1251798.8486 | 2688239.9305 | 1251799.6258 | 2688238.0393 | 1251799.3974 | 2688234.6802 | 1251798.3911 | 2688232.9644 | 1251798.0431 | 2688231.7133 | 1251798.4247 | 2688231.0898 | 1251799.7387 | 2688231.1049 | 1251801.2623 | 2688232.9205 | 1251803.5244 | 2688235.256 | 1251805.8498 | 2688236.3566 | 1251807.4674 | 2688236.6018 | 1251809.7506 | 2688236.0513 | 1251811.7439 | 2688236.0764 | 1251812.5894 | 2688235.4169 | 1251817.3387 | 2688236.4826 | 1251821.8024 | 2688234.3357 | 1251828.0975
14 | 2688234.3357 | 1251828.0975 | 2688226.1698 | 1251825.5866
15 | 2688270.8905 | 1251842.3416 | 2688264.4813 | 1251838.8546 | 2688247.4547 | 1251832.1292 | 2688234.3357 | 1251828.0975
16 | 2688191.391 | 1251892.6815 | 2688157.8892 | 1251892.9773
17 | 2688213.1048 | 1251892.308 | 2688204.8283 | 1251892.5628 | 2688191.391 | 1251892.6815
18 | 2688143.9015 | 1251893.1009 | 2688157.8892 | 1251892.9773
19 | 2688213.1048 | 1251892.308 | 2688228.3682 | 1251887.1647
20 | 2688213.1048 | 1251892.308 | 2688211.2606 | 1251899.5639 | 2688206.7848 | 1251903.7305
21 | 2688228.3682 | 1251887.1647 | 2688234.4329 | 1251893.0038 | 2688240.6693 | 1251895.2367
22 | 2688228.3682 | 1251887.1647 | 2688253.6603 | 1251870.1278
23 | 2688206.7848 | 1251903.7305 | 2688206.1935 | 1251904.2809 | 2688171.7702 | 1251928.8874 | 2688166.7636 | 1251933.0643
24 | 2688240.6693 | 1251895.2367 | 2688265.2493 | 1251904.0372
25 | 2688147.5191 | 1251949.1198 | 2688166.7636 | 1251933.0643
26 | 2688271.6351 | 1251906.3236 | 2688265.2493 | 1251904.0372
27 | 2688147.5191 | 1251949.1198 | 2688147.1771 | 1251952.3171 | 2688148.1427 | 1251955.4005 | 2688154.2169 | 1251963.6415
28 | 2688147.5191 | 1251949.1198 | 2688142.7783 | 1251949.1604 | 2688138.033 | 1251947.9889 | 2688129.7279 | 1251944.0846 | 2688125.5663 | 1251943.3012
29 | 2688273.3157 | 1251845.7358 | 2688280.8034 | 1251844.224 | 2688295.2267 | 1251849.4675
30 | 2688270.8905 | 1251842.3416 | 2688273.3157 | 1251845.7358
31 | 2688313.7958 | 1251860.4613 | 2688304.6992 | 1251853.9541 | 2688300.7057 | 1251851.4594 | 2688295.2267 | 1251849.4675
32 | 2688313.7958 | 1251860.4613 | 2688317.4022 | 1251862.9538
33 | 2688271.6351 | 1251906.3236 | 2688274.839 | 1251907.6056 | 2688284.2802 | 1251905.6781
34 | 2688271.6351 | 1251906.3236 | 2688262.9955 | 1251931.4473
35 | 2688341.6181 | 1251879.6906 | 2688317.4022 | 1251862.9538
36 | 2688206.2397 | 1251819.4586 | 2688226.1698 | 1251825.5866
37 | 2688324.7536 | 1251907.5188 | 2688324.6257 | 1251907.6702
38 | 2688313.2222 | 1251921.1878 | 2688317.2872 | 1251916.3558 | 2688324.6257 | 1251907.6702
39 | 2688324.7536 | 1251907.5188 | 2688329.1816 | 1251902.278 | 2688334.3601 | 1251896.5345
40 | 2688307.5528 | 1251916.6888 | 2688313.2222 | 1251921.1878
41 | 2688313.2222 | 1251921.1878 | 2688323.8805 | 1251929.6752
42 | 2688335.4208 | 1251895.358 | 2688334.3601 | 1251896.5345
43 | 2688298.6407 | 1251927.6755 | 2688307.5528 | 1251916.6888
44 | 2688307.5528 | 1251916.6888 | 2688301.2332 | 1251911.6759
45 | 2688324.0331 | 1251929.7967 | 2688323.8805 | 1251929.6752
46 | 2688346.7115 | 1251882.8356 | 2688335.4208 | 1251895.358
47 | 2688284.2802 | 1251905.6781 | 2688298.9665 | 1251909.8779 | 2688301.2332 | 1251911.6759
48 | 2688325.8709 | 1251931.2602 | 2688324.0331 | 1251929.7967
49 | 2688346.7115 | 1251882.8356 | 2688351.7271 | 1251885.6236 | 2688362.4733 | 1251890.3319 | 2688365.8398 | 1251891.1626
50 | 2688341.6181 | 1251879.6906 | 2688343.3354 | 1251880.9505 | 2688346.7115 | 1251882.8356
51 | 2688284.2802 | 1251905.6781 | 2688291.4775 | 1251896.8008 | 2688296.7809 | 1251890.4201
52 | 2688325.8709 | 1251931.2602 | 2688343.4189 | 1251945.234
53 | 2688193.0109 | 1251815.8397 | 2688173.6949 | 1251812.0445
54 | 2688193.0109 | 1251815.8397 | 2688197.0524 | 1251816.6337 | 2688206.2397 | 1251819.4586
55 | 2688201.7578 | 1251954.5819 | 2688211.9989 | 1251951.9956
56 | 2688201.7578 | 1251954.5819 | 2688181.4972 | 1251959.6985
57 | 2688181.4972 | 1251959.6985 | 2688168.9747 | 1251962.8609
58 | 2688154.2169 | 1251963.6415 | 2688156.4652 | 1251964.7203 | 2688159.8704 | 1251965.1601 | 2688168.9747 | 1251962.8609
59 | 2688316.9677 | 1252025.8344 | 2688349.693 | 1251985.5572
60 | 2688362.5588 | 1251960.4754 | 2688360.0224 | 1251963.5288 | 2688358.2085 | 1251966.2149 | 2688359.181 | 1251973.8797 | 2688349.693 | 1251985.5572
61 | 2688316.9677 | 1252025.8344 | 2688337.2952 | 1252035.1075
62 | 2688362.5588 | 1251960.4754 | 2688362.5003 | 1251963.8883 | 2688365.4494 | 1251969.0918 | 2688366.52 | 1251974.7342 | 2688374.8301 | 1251980.8184 | 2688387.7825 | 1251972.4923
63 | 2688362.5588 | 1251960.4754 | 2688373.5176 | 1251947.0005
64 | 2688362.5588 | 1251960.4754 | 2688349.4559 | 1251950.0414
65 | 2688337.2952 | 1252035.1075 | 2688396.9476 | 1252110.2713
66 | 2688381.0896 | 1251937.69 | 2688373.5176 | 1251947.0005
67 | 2688349.4559 | 1251950.0414 | 2688349.2977 | 1251949.9154
68 | 2688369.2115 | 1252144.1714 | 2688396.9476 | 1252110.2713
69 | 2688381.0896 | 1251937.69 | 2688392.1496 | 1251946.8432
70 | 2688381.0896 | 1251937.69 | 2688382.7286 | 1251935.9009
71 | 2688343.4189 | 1251945.234 | 2688349.2977 | 1251949.9154
72 | 2688349.4629 | 1252168.309 | 2688369.2115 | 1252144.1714
73 | 2688349.4629 | 1252168.309 | 2688288.3182 | 1252154.2498
74 | 2688397.1851 | 1251950.9485 | 2688396.0312 | 1251950.0556 | 2688392.1496 | 1251946.8432
75 | 2688386.6936 | 1251931.5731 | 2688382.7286 | 1251935.9009
76 | 2688394.9718 | 1251897.1439 | 2688373.6486 | 1251893.0895 | 2688365.8398 | 1251891.1626
77 | 2688394.9718 | 1251897.1439 | 2688405.8487 | 1251896.4916
78 | 2688412.7862 | 1251896.0755 | 2688405.8487 | 1251896.4916
79 | 2688412.7862 | 1251896.0755 | 2688413.8514 | 1251896.0136 | 2688427.0075 | 1251897.1422
80 | 2688417.3296 | 1251951.9872 | 2688413.9285 | 1251954.5482 | 2688411.9384 | 1251955.3858 | 2688409.3793 | 1251955.4032 | 2688405.3238 | 1251954.5421 | 2688398.8443 | 1251952.2325 | 2688397.1851 | 1251950.9485
81 | 2688431.2294 | 1251941.5704 | 2688418.9821 | 1251950.7429 | 2688417.3296 | 1251951.9872
82 | 2688431.2294 | 1251941.5704 | 2688436.1726 | 1251937.8683
83 | 2688441.113 | 1251934.1682 | 2688436.1726 | 1251937.8683
84 | 2688446.1462 | 1251930.2797 | 2688441.6762 | 1251933.7464 | 2688441.113 | 1251934.1682
85 | 2688451.0251 | 1251926.4958 | 2688446.1462 | 1251930.2797
86 | 2688455.9041 | 1251922.7119 | 2688451.0251 | 1251926.4958
87 | 2688125.5663 | 1251943.3012 | 2688121.9676 | 1251942.6237 | 2688102.4544 | 1251942.2173
88 | 2688471.8155 | 1251909.5001 | 2688455.9113 | 1251904.3238
89 | 2688471.8155 | 1251909.5001 | 2688471.1456 | 1251910.8911 | 2688455.9041 | 1251922.7119

## bus_geodata
| x | y | coords
0 | 2688416.9223 | 1251788.0762
1 | 2688392.9473 | 1251783.4828
2 | 2688386.0937 | 1251814.3151
3 | 2688401.5282 | 1251848.2934
4 | 2688374.3235 | 1251839.961
5 | 2688432.5374 | 1251833.4116
6 | 2688356.7234 | 1251834.5703
7 | 2688441.7461 | 1251837.1979
8 | 2688346.7025 | 1251803.4368
9 | 2688340.218 | 1251829.5158
10 | 2688313.4087 | 1251821.3059
11 | 2688253.4555 | 1251775.4521
12 | 2688243.0451 | 1251796.2696
13 | 2688255.6641 | 1251807.0101
14 | 2688234.3357 | 1251828.0975
15 | 2688191.391 | 1251892.6815
16 | 2688157.8892 | 1251892.9773
17 | 2688213.1048 | 1251892.308
18 | 2688143.9015 | 1251893.1008
19 | 2688228.3682 | 1251887.1647
20 | 2688206.7848 | 1251903.7305
21 | 2688240.6693 | 1251895.2367
22 | 2688253.6603 | 1251870.1278
23 | 2688166.7636 | 1251933.0643
24 | 2688265.2493 | 1251904.0372
25 | 2688147.5191 | 1251949.1198
26 | 2688273.3157 | 1251845.7358
27 | 2688295.2267 | 1251849.4675
28 | 2688270.8905 | 1251842.3416
29 | 2688313.7958 | 1251860.4613
30 | 2688271.6351 | 1251906.3236
31 | 2688317.4022 | 1251862.9538
32 | 2688226.1698 | 1251825.5866
33 | 2688324.6257 | 1251907.6702
34 | 2688324.7536 | 1251907.5188
35 | 2688313.2222 | 1251921.1878
36 | 2688334.3601 | 1251896.5345
37 | 2688307.5528 | 1251916.6888
38 | 2688323.8805 | 1251929.6752
39 | 2688335.4208 | 1251895.358
40 | 2688298.6407 | 1251927.6755
41 | 2688301.2332 | 1251911.6759
42 | 2688324.0331 | 1251929.7967
43 | 2688346.7115 | 1251882.8356
44 | 2688284.2802 | 1251905.6781
45 | 2688325.8709 | 1251931.2602
46 | 2688173.6949 | 1251812.0445
47 | 2688193.0109 | 1251815.8397
48 | 2688206.2397 | 1251819.4586
49 | 2688211.9989 | 1251951.9956
50 | 2688201.7578 | 1251954.5819
51 | 2688181.4972 | 1251959.6985
52 | 2688168.9747 | 1251962.8609
53 | 2688262.9955 | 1251931.4473
54 | 2688154.2169 | 1251963.6415
55 | 2688349.693 | 1251985.5572
56 | 2688316.9677 | 1252025.8344
57 | 2688362.5588 | 1251960.4754
58 | 2688337.2952 | 1252035.1075
59 | 2688387.7825 | 1251972.4923
60 | 2688373.5176 | 1251947.0005
61 | 2688349.4559 | 1251950.0414
62 | 2688396.9476 | 1252110.2713
63 | 2688381.0896 | 1251937.69
64 | 2688349.2977 | 1251949.9154
65 | 2688369.2115 | 1252144.1714
66 | 2688349.4629 | 1252168.309
67 | 2688288.3182 | 1252154.2498
68 | 2688392.1496 | 1251946.8432
69 | 2688382.7286 | 1251935.9009
70 | 2688343.4189 | 1251945.234
71 | 2688341.6181 | 1251879.6906
72 | 2688365.8398 | 1251891.1626
73 | 2688296.7809 | 1251890.4201
74 | 2688394.9718 | 1251897.1439
75 | 2688386.6936 | 1251931.5731
76 | 2688405.8487 | 1251896.4916
77 | 2688412.7862 | 1251896.0755
78 | 2688397.1851 | 1251950.9485
79 | 2688427.0075 | 1251897.1422
80 | 2688431.2294 | 1251941.5704
81 | 2688417.3296 | 1251951.9872
82 | 2688436.1726 | 1251937.8683
83 | 2688441.113 | 1251934.1682
84 | 2688446.1462 | 1251930.2797
85 | 2688451.0251 | 1251926.4958
86 | 2688125.5663 | 1251943.3012
87 | 2688102.4544 | 1251942.2173
88 | 2688455.9113 | 1251904.3238
89 | 2688471.8155 | 1251909.5001
90 | 2688455.9041 | 1251922.7119
91 | 2688346.7115 | 1251882.8356

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98974 | -0.1973 | 0.029192 | 0.0073163
1 | 0.9904 | -0.18463 | 0 | 0
2 | 0.99124 | -0.16826 | 0 | 0
3 | 0.99135 | -0.1662 | 0.0024141 | 0.00060502
4 | 0.992 | -0.15366 | 0.003564 | 0.00089321
5 | 0.99064 | -0.17991 | 0.017629 | 0.0044182
6 | 0.99297 | -0.13488 | 0 | 0
7 | 0.9906 | -0.18077 | 0.004834 | 0.0012115
8 | 0.99091 | -0.17465 | 0.048667 | 0.012197
9 | 0.99211 | -0.15146 | 0.0034862 | 0.00087371
10 | 0.99206 | -0.15252 | 0.0021267 | 0.00053299
11 | 0.99032 | -0.18631 | 0.015951 | 0.0039977
12 | 0.99066 | -0.17971 | 0 | 0
13 | 0.99049 | -0.18285 | 0.0096891 | 0.0024283
14 | 0.99173 | -0.15898 | 0 | 0
15 | 0.98802 | -0.23029 | 0.010277 | 0.0025757
16 | 0.98759 | -0.23879 | 0.0070406 | 0.0017645
17 | 0.98851 | -0.22081 | 0 | 0
18 | 0.98749 | -0.24058 | 0.0071579 | 0.0017939
19 | 0.9893 | -0.2055 | 0 | 0
20 | 0.98815 | -0.22784 | 0.0039595 | 0.00099235
21 | 0.99014 | -0.18917 | 0.0034595 | 0.00086703
22 | 0.98909 | -0.20961 | 0.0075643 | 0.0018958
23 | 0.98701 | -0.25003 | 0.0061485 | 0.001541
24 | 0.99169 | -0.15929 | 0.0054448 | 0.0013646
25 | 0.98657 | -0.25849 | 0 | 0
26 | 0.99367 | -0.12145 | 0 | 0
27 | 0.9947 | -0.10163 | 0.0062161 | 0.0015579
28 | 0.99348 | -0.12505 | 0 | 0
29 | 0.99579 | -0.080562 | 0 | 0
30 | 0.99212 | -0.15089 | 0 | 0
31 | 0.99601 | -0.076316 | 0.012865 | 0.0032243
32 | 0.99154 | -0.16251 | 0.0063651 | 0.0015952
33 | 0.99804 | -0.037305 | 0.0056126 | 0.0014067
34 | 0.99806 | -0.036871 | 0.010079 | 0.0025259
35 | 0.99605 | -0.07526 | 0 | 0
36 | 0.99981 | -0.0036675 | 0.005113 | 0.0012814
37 | 0.99532 | -0.089376 | 0 | 0
38 | 0.99438 | -0.10731 | 0.0046699 | 0.0011704
39 | 1 | 0 | -0.48741 | -0.12333
40 | 0.99514 | -0.092816 | 0.013834 | 0.003467
41 | 0.9946 | -0.1032 | 0.0077294 | 0.0019372
42 | 0.99436 | -0.10775 | 0.0046647 | 0.0011691
43 | 0.99833 | -0.031802 | 0 | 0
44 | 0.99311 | -0.13192 | 0 | 0
45 | 0.99409 | -0.1129 | 0.0078453 | 0.0019662
46 | 0.99099 | -0.17319 | 0.0074841 | 0.0018757
47 | 0.99113 | -0.17057 | 0 | 0
48 | 0.99122 | -0.16875 | 0.0094055 | 0.0023572
49 | 0.9858 | -0.27362 | 0.0056193 | 0.0014083
50 | 0.98585 | -0.27256 | 0.0031784 | 0.00079658
51 | 0.98602 | -0.26926 | 0.0028859 | 0.00072327
52 | 0.98616 | -0.26656 | 0.0023843 | 0.00059756
53 | 0.99182 | -0.15665 | 0.012253 | 0.0030709
54 | 0.98636 | -0.26269 | 0 | 0
55 | 0.98893 | -0.21251 | 0.0045728 | 0.0011461
56 | 0.98847 | -0.22138 | 0 | 0
57 | 0.98932 | -0.20495 | 0 | 0
58 | 0.98827 | -0.2252 | 0.0023912 | 0.00059928
59 | 0.98878 | -0.21538 | 0.014334 | 0.0035923
60 | 0.98813 | -0.22791 | 0.010646 | 0.0026681
61 | 0.9909 | -0.17438 | 0.0045728 | 0.0011461
62 | 0.98764 | -0.23752 | 0.00045701 | 0.00011454
63 | 0.98743 | -0.24153 | 0 | 0
64 | 0.99092 | -0.174 | 0.0045779 | 0.0011473
65 | 0.98737 | -0.24279 | 0.0018611 | 0.00046642
66 | 0.98723 | -0.2455 | 0.001439 | 0.00036065
67 | 0.98703 | -0.24935 | 0.003426 | 0.00085864
68 | 0.98676 | -0.25451 | 0.0041767 | 0.0010468
69 | 0.9874 | -0.24209 | 0.0087616 | 0.0021959
70 | 0.99169 | -0.1591 | 0.0046882 | 0.001175
71 | 0.99784 | -0.04122 | 0 | 0
72 | 0.99765 | -0.045052 | 0.011633 | 0.0029156
73 | 0.99297 | -0.1345 | 0.0074046 | 0.0018558
74 | 0.99698 | -0.057837 | 0 | 0
75 | 0.98738 | -0.24253 | 0.0041767 | 0.0010468
76 | 0.99674 | -0.062525 | 0.010775 | 0.0027005
77 | 0.99665 | -0.064201 | 0 | 0
78 | 0.98648 | -0.25991 | 0.0033502 | 0.00083964
79 | 0.99647 | -0.067645 | 0.01375 | 0.0034461
80 | 0.98497 | -0.28933 | 0.0030663 | 0.00076849
81 | 0.98561 | -0.27696 | 0.0033481 | 0.0008391
82 | 0.98476 | -0.2934 | 0.0030633 | 0.00076774
83 | 0.98457 | -0.29712 | 0.003063 | 0.00076765
84 | 0.98439 | -0.30061 | 0.0030633 | 0.00076775
85 | 0.98424 | -0.30366 | 0.0030663 | 0.00076849
86 | 0.98647 | -0.26047 | 0.0023768 | 0.00059568
87 | 0.98642 | -0.26147 | 0.0024149 | 0.00060522
88 | 0.98336 | -0.32077 | 0.0213 | 0.0053383
89 | 0.98369 | -0.31435 | 0 | 0
90 | 0.9841 | -0.30636 | 0.0030633 | 0.00076775
91 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.029192 | -0.0073163 | 0.02921 | 0.0073272 | 1.7633e-05 | 1.0971e-05 | 0.043889 | 0.043888 | 0.043889 | 0.98974 | -0.1973 | 0.9904 | -0.18463 | 12.0573
1 | -0.02921 | -0.0073272 | 0.029233 | 0.0073414 | 2.2814e-05 | 1.4194e-05 | 0.043888 | 0.043888 | 0.043888 | 0.9904 | -0.18463 | 0.99124 | -0.16826 | 12.0573
2 | -0.029233 | -0.0073414 | 0.029253 | 0.0073541 | 2.0382e-05 | 1.2681e-05 | 0.043888 | 0.043888 | 0.043888 | 0.99124 | -0.16826 | 0.992 | -0.15366 | 12.0572
3 | -0.024892 | -0.0062437 | 0.024907 | 0.0062529 | 1.4896e-05 | 9.1663e-06 | 0.037365 | 0.037365 | 0.037365 | 0.99135 | -0.1662 | 0.992 | -0.15366 | 10.265
4 | 0.022478 | 0.0056387 | -0.022463 | -0.0056298 | 1.4684e-05 | 8.9548e-06 | 0.033741 | 0.033741 | 0.033741 | 0.99135 | -0.1662 | 0.99064 | -0.17991 | 9.2696
5 | -0.057724 | -0.0145 | 0.057776 | 0.014533 | 5.1766e-05 | 3.2892e-05 | 0.086599 | 0.086599 | 0.086599 | 0.992 | -0.15366 | 0.99297 | -0.13488 | 23.7909
6 | 0.0048342 | 0.0012115 | -0.004834 | -0.0012115 | 1.9687e-07 | -2.1889e-09 | 0.0072613 | 0.0072614 | 0.0072614 | 0.99064 | -0.17991 | 0.9906 | -0.18077 | 1.9949
7 | 0.054377 | 0.013665 | -0.054334 | -0.013638 | 4.2997e-05 | 2.7295e-05 | 0.0815 | 0.0815 | 0.0815 | 0.99297 | -0.13488 | 0.99211 | -0.15146 | 22.3902
8 | -0.11215 | -0.028198 | 0.11266 | 0.02852 | 0.00050411 | 0.00032201 | 0.1681 | 0.1681 | 0.1681 | 0.99297 | -0.13488 | 0.99784 | -0.04122 | 46.181
9 | -0.048667 | -0.012197 | 0.048721 | 0.012231 | 5.3823e-05 | 3.41e-05 | 0.073082 | 0.073082 | 0.073082 | 0.99091 | -0.17465 | 0.99211 | -0.15146 | 20.0775
10 | 0.0021268 | 0.0005327 | -0.0021267 | -0.00053299 | 1.0698e-07 | -2.9357e-07 | 0.0031897 | 0.0031899 | 0.0031899 | 0.99211 | -0.15146 | 0.99206 | -0.15252 | 0.87633
11 | -0.015951 | -0.0039977 | 0.015956 | 0.0040007 | 5.014e-06 | 2.9094e-06 | 0.023968 | 0.023968 | 0.023968 | 0.99032 | -0.18631 | 0.99066 | -0.17971 | 6.5845
12 | 0.0096905 | 0.002429 | -0.0096891 | -0.0024283 | 1.4496e-06 | 6.9287e-07 | 0.014556 | 0.014556 | 0.014556 | 0.99066 | -0.17971 | 0.99049 | -0.18285 | 3.9989
13 | -0.025647 | -0.0064297 | 0.025672 | 0.0064453 | 2.5358e-05 | 1.5642e-05 | 0.038523 | 0.038523 | 0.038523 | 0.99066 | -0.17971 | 0.99173 | -0.15898 | 10.5834
14 | 0.023265 | 0.0058341 | -0.023261 | -0.0058317 | 3.9042e-06 | 2.3884e-06 | 0.034909 | 0.034909 | 0.034909 | 0.99173 | -0.15898 | 0.99154 | -0.16251 | 9.5904
15 | -0.048937 | -0.012279 | 0.049017 | 0.01233 | 7.9319e-05 | 5.0257e-05 | 0.073432 | 0.073432 | 0.073432 | 0.99173 | -0.15898 | 0.99348 | -0.12505 | 20.1737
16 | 0.014205 | 0.003562 | -0.014199 | -0.0035587 | 5.7505e-06 | 3.2514e-06 | 0.021394 | 0.021394 | 0.021394 | 0.98802 | -0.23029 | 0.98759 | -0.23879 | 5.8775
17 | -0.024482 | -0.0061376 | 0.024493 | 0.0061444 | 1.1072e-05 | 6.8081e-06 | 0.036872 | 0.036872 | 0.036872 | 0.98802 | -0.23029 | 0.98851 | -0.22081 | 10.1296
18 | 0.0071586 | 0.0017942 | -0.0071579 | -0.0017939 | 6.1026e-07 | 2.116e-07 | 0.010786 | 0.010786 | 0.010786 | 0.98759 | -0.23879 | 0.98749 | -0.24058 | 2.9632
19 | -0.053514 | -0.013436 | 0.053553 | 0.01346 | 3.9098e-05 | 2.4817e-05 | 0.080563 | 0.080563 | 0.080563 | 0.98851 | -0.22081 | 0.9893 | -0.2055 | 22.1327
20 | 0.029021 | 0.0072912 | -0.029011 | -0.0072851 | 9.7367e-06 | 6.0572e-06 | 0.043691 | 0.043692 | 0.043692 | 0.98851 | -0.22081 | 0.98815 | -0.22784 | 12.0032
21 | -0.061118 | -0.015357 | 0.061166 | 0.015387 | 4.7687e-05 | 3.0326e-05 | 0.091943 | 0.091943 | 0.091943 | 0.9893 | -0.2055 | 0.99014 | -0.18917 | 25.259
22 | 0.0075657 | 0.0018963 | -0.0075643 | -0.0018958 | 1.4809e-06 | 5.5632e-07 | 0.01138 | 0.01138 | 0.01138 | 0.9893 | -0.2055 | 0.98909 | -0.20961 | 3.1264
23 | 0.025051 | 0.0062928 | -0.025025 | -0.0062765 | 2.6499e-05 | 1.6324e-05 | 0.037729 | 0.037729 | 0.037729 | 0.98815 | -0.22784 | 0.98701 | -0.25003 | 10.3652
24 | -0.064626 | -0.016254 | 0.064718 | 0.016313 | 9.2388e-05 | 5.8792e-05 | 0.097142 | 0.097142 | 0.097142 | 0.99014 | -0.18917 | 0.99169 | -0.15929 | 26.6873
25 | 0.018876 | 0.0047355 | -0.018869 | -0.0047309 | 7.6123e-06 | 4.5517e-06 | 0.02846 | 0.02846 | 0.02846 | 0.98701 | -0.25003 | 0.98657 | -0.25849 | 7.8186
26 | -0.070163 | -0.017678 | 0.070191 | 0.017695 | 2.8209e-05 | 1.7966e-05 | 0.10531 | 0.10531 | 0.10531 | 0.99169 | -0.15929 | 0.99212 | -0.15089 | 28.9318
27 | 0.014077 | 0.0035303 | -0.014074 | -0.0035287 | 2.8186e-06 | 1.591e-06 | 0.021232 | 0.021232 | 0.021232 | 0.98657 | -0.25849 | 0.98636 | -0.26269 | 5.833
28 | 0.0047922 | 0.0012007 | -0.0047918 | -0.0012007 | 4.5138e-07 | -5.2973e-09 | 0.0072278 | 0.0072279 | 0.0072279 | 0.98657 | -0.25849 | 0.98647 | -0.26047 | 1.9857
29 | -0.049025 | -0.012335 | 0.049072 | 0.012364 | 4.6479e-05 | 2.9449e-05 | 0.073432 | 0.073432 | 0.073432 | 0.99367 | -0.12145 | 0.9947 | -0.10163 | 20.1736
30 | 0.049025 | 0.012335 | -0.049017 | -0.01233 | 8.4281e-06 | 5.34e-06 | 0.073432 | 0.073432 | 0.073432 | 0.99367 | -0.12145 | 0.99348 | -0.12505 | 20.1736
31 | -0.055288 | -0.013922 | 0.055343 | 0.013958 | 5.5755e-05 | 3.5401e-05 | 0.082731 | 0.082731 | 0.082731 | 0.9947 | -0.10163 | 0.99579 | -0.080562 | 22.7282
32 | -0.055343 | -0.013958 | 0.055355 | 0.013965 | 1.1252e-05 | 7.1443e-06 | 0.082731 | 0.082731 | 0.082731 | 0.99579 | -0.080562 | 0.99601 | -0.076316 | 22.7282
33 | -0.082447 | -0.020768 | 0.082522 | 0.020816 | 7.4882e-05 | 4.7756e-05 | 0.12369 | 0.12369 | 0.12369 | 0.99212 | -0.15089 | 0.99311 | -0.13192 | 33.982
34 | 0.012256 | 0.0030727 | -0.012253 | -0.0030709 | 3.3668e-06 | 1.8118e-06 | 0.018383 | 0.018383 | 0.018383 | 0.99212 | -0.15089 | 0.99182 | -0.15665 | 5.0503
35 | -0.06822 | -0.017189 | 0.068335 | 0.017262 | 0.00011474 | 7.3048e-05 | 0.10195 | 0.10195 | 0.10195 | 0.99601 | -0.076316 | 0.99784 | -0.04122 | 28.0085
36 | 0.016896 | 0.0042365 | -0.016891 | -0.0042335 | 5.0275e-06 | 2.9488e-06 | 0.025357 | 0.025357 | 0.025357 | 0.99154 | -0.16251 | 0.99122 | -0.16875 | 6.9662
37 | -0.25249 | -0.064082 | 0.25249 | 0.064085 | 5.2751e-06 | 3.3709e-06 | 0.37673 | 0.37673 | 0.37673 | 0.99804 | -0.037305 | 0.99806 | -0.036871 | 51.7482
38 | 0.24688 | 0.062675 | -0.24643 | -0.062388 | 0.00044994 | 0.0002875 | 0.36836 | 0.36836 | 0.36836 | 0.99804 | -0.037305 | 0.99605 | -0.07526 | 50.5988
39 | -0.26257 | -0.066611 | 0.26299 | 0.06688 | 0.00041996 | 0.00026839 | 0.39175 | 0.39175 | 0.39175 | 0.99806 | -0.036871 | 0.99981 | -0.0036675 | 53.8123
40 | 0.11176 | 0.028246 | -0.11168 | -0.028198 | 7.5587e-05 | 4.8282e-05 | 0.16704 | 0.16704 | 0.16704 | 0.99605 | -0.07526 | 0.99532 | -0.089376 | 45.89
41 | 0.13467 | 0.034142 | -0.13446 | -0.034009 | 0.00020708 | 0.00013235 | 0.20132 | 0.20132 | 0.20132 | 0.99605 | -0.07526 | 0.99438 | -0.10731 | 55.3077
42 | -0.2681 | -0.068161 | 0.26815 | 0.068191 | 4.7371e-05 | 3.0276e-05 | 0.39936 | 0.39936 | 0.39936 | 0.99981 | -0.0036675 | 1 | 0 | 54.8575
43 | 0.013836 | 0.0034683 | -0.013834 | -0.003467 | 2.2675e-06 | 1.2676e-06 | 0.020685 | 0.020685 | 0.020685 | 0.99532 | -0.089376 | 0.99514 | -0.092816 | 5.6827
44 | 0.097846 | 0.02473 | -0.097781 | -0.024688 | 6.4792e-05 | 4.1362e-05 | 0.14635 | 0.14635 | 0.14635 | 0.99532 | -0.089376 | 0.9946 | -0.1032 | 40.2073
45 | 0.12979 | 0.032839 | -0.12979 | -0.032837 | 2.7622e-06 | 1.7653e-06 | 0.19433 | 0.19433 | 0.19433 | 0.99438 | -0.10731 | 0.99436 | -0.10775 | 53.3879
46 | 0.21761 | 0.055138 | -0.21728 | -0.054926 | 0.00033191 | 0.00021198 | 0.32402 | 0.32402 | 0.32402 | 1 | 0 | 0.99833 | -0.031802 | 44.5081
47 | 0.090052 | 0.022751 | -0.089928 | -0.022672 | 0.00012378 | 7.8986e-05 | 0.13479 | 0.13479 | 0.13479 | 0.9946 | -0.1032 | 0.99311 | -0.13192 | 37.0304
48 | 0.12512 | 0.031668 | -0.12509 | -0.031648 | 3.0924e-05 | 1.9761e-05 | 0.18735 | 0.18735 | 0.18735 | 0.99436 | -0.10775 | 0.99409 | -0.1129 | 51.4701
49 | 0.036205 | 0.009091 | -0.036182 | -0.0090766 | 2.287e-05 | 1.4363e-05 | 0.05397 | 0.05397 | 0.05397 | 0.99833 | -0.031802 | 0.99765 | -0.045052 | 14.8269
50 | 0.18107 | 0.045835 | -0.18099 | -0.045782 | 8.1824e-05 | 5.2211e-05 | 0.27005 | 0.27005 | 0.27005 | 0.99833 | -0.031802 | 0.99784 | -0.04122 | 37.0947
51 | 0.0074056 | 0.0018561 | -0.0074046 | -0.0018558 | 9.1075e-07 | 3.2769e-07 | 0.011096 | 0.011096 | 0.011096 | 0.99311 | -0.13192 | 0.99297 | -0.1345 | 3.0484
52 | 0.11725 | 0.029682 | -0.11699 | -0.029516 | 0.00025941 | 0.00016573 | 0.17561 | 0.17561 | 0.17561 | 0.99409 | -0.1129 | 0.99169 | -0.1591 | 48.244
53 | -0.0074841 | -0.0018757 | 0.0074851 | 0.001876 | 9.3224e-07 | 3.4297e-07 | 0.011238 | 0.011238 | 0.011238 | 0.99099 | -0.17319 | 0.99113 | -0.17057 | 3.0873
54 | -0.0074851 | -0.001876 | 0.0074857 | 0.0018763 | 6.5023e-07 | 2.3918e-07 | 0.011238 | 0.011238 | 0.011238 | 0.99113 | -0.17057 | 0.99122 | -0.16875 | 3.0873
55 | -0.0056193 | -0.0014083 | 0.0056196 | 0.0014084 | 2.8498e-07 | 4.7713e-08 | 0.0084821 | 0.0084821 | 0.0084821 | 0.9858 | -0.27362 | 0.98585 | -0.27256 | 2.3303
56 | -0.008798 | -0.002205 | 0.0087994 | 0.0022056 | 1.3819e-06 | 6.1791e-07 | 0.013279 | 0.013279 | 0.013279 | 0.98585 | -0.27256 | 0.98602 | -0.26926 | 3.6482
57 | -0.011685 | -0.0029289 | 0.011687 | 0.0029297 | 1.5062e-06 | 7.9918e-07 | 0.017635 | 0.017634 | 0.017635 | 0.98602 | -0.26926 | 0.98616 | -0.26656 | 4.8446
58 | -0.014071 | -0.0035272 | 0.014074 | 0.0035287 | 2.5894e-06 | 1.4618e-06 | 0.021232 | 0.021232 | 0.021232 | 0.98616 | -0.26656 | 0.98636 | -0.26269 | 5.833
59 | 0.0095872 | 0.0024039 | -0.0095832 | -0.002402 | 4.0501e-06 | 1.9265e-06 | 0.014426 | 0.014426 | 0.014426 | 0.98893 | -0.21251 | 0.98847 | -0.22138 | 3.9633
60 | -0.01416 | -0.0035499 | 0.014165 | 0.0035528 | 5.1043e-06 | 2.8819e-06 | 0.021307 | 0.021307 | 0.021307 | 0.98893 | -0.21251 | 0.98932 | -0.20495 | 5.8535
61 | 0.0095832 | 0.002402 | -0.0095814 | -0.0024011 | 1.7437e-06 | 8.2965e-07 | 0.014426 | 0.014426 | 0.014426 | 0.98847 | -0.22138 | 0.98827 | -0.2252 | 3.9633
62 | 0.014341 | 0.0035964 | -0.014334 | -0.0035923 | 7.125e-06 | 4.0359e-06 | 0.02157 | 0.021571 | 0.021571 | 0.98932 | -0.20495 | 0.98878 | -0.21538 | 5.926
63 | 0.07441 | 0.01875 | -0.074329 | -0.018698 | 8.1637e-05 | 5.2025e-05 | 0.11196 | 0.11196 | 0.11196 | 0.98932 | -0.20495 | 0.98813 | -0.22791 | 30.757
64 | -0.10292 | -0.025899 | 0.10307 | 0.025996 | 0.00015058 | 9.6155e-05 | 0.15483 | 0.15483 | 0.15483 | 0.98932 | -0.20495 | 0.9909 | -0.17438 | 42.5364
65 | 0.0071902 | 0.0018018 | -0.007186 | -0.0018004 | 4.2177e-06 | 1.4705e-06 | 0.010826 | 0.010827 | 0.010827 | 0.98827 | -0.2252 | 0.98764 | -0.23752 | 2.9743
66 | 0.063683 | 0.01603 | -0.063641 | -0.016004 | 4.1409e-05 | 2.6348e-05 | 0.095924 | 0.095924 | 0.095924 | 0.98813 | -0.22791 | 0.98743 | -0.24153 | 26.3527
67 | -0.10764 | -0.027142 | 0.10764 | 0.027143 | 1.9837e-06 | 1.267e-06 | 0.1617 | 0.1617 | 0.1617 | 0.9909 | -0.17438 | 0.99092 | -0.174 | 44.4229
68 | 0.006729 | 0.0016858 | -0.0067273 | -0.0016853 | 1.6882e-06 | 5.2008e-07 | 0.010138 | 0.010138 | 0.010138 | 0.98764 | -0.23752 | 0.98737 | -0.24279 | 2.7852
69 | 0.050703 | 0.012761 | -0.050671 | -0.012741 | 3.1445e-05 | 1.9941e-05 | 0.076426 | 0.076426 | 0.076426 | 0.98743 | -0.24153 | 0.98676 | -0.25451 | 20.9961
70 | 0.012939 | 0.0032428 | -0.012938 | -0.0032426 | 3.4592e-07 | 1.9035e-07 | 0.019498 | 0.019498 | 0.019498 | 0.98743 | -0.24153 | 0.9874 | -0.24209 | 5.3567
71 | -0.11222 | -0.02829 | 0.1123 | 0.028341 | 8.0083e-05 | 5.1156e-05 | 0.16857 | 0.16857 | 0.16857 | 0.99092 | -0.174 | 0.99169 | -0.1591 | 46.3114
72 | 0.0048663 | 0.0012189 | -0.0048657 | -0.0012189 | 6.2897e-07 | 3.7169e-09 | 0.0073335 | 0.0073336 | 0.0073336 | 0.98737 | -0.24279 | 0.98723 | -0.2455 | 2.0147
73 | 0.0034266 | 0.00085824 | -0.003426 | -0.00085864 | 6.276e-07 | -4.004e-07 | 0.0051646 | 0.0051649 | 0.0051649 | 0.98723 | -0.2455 | 0.98703 | -0.24935 | 1.4189
74 | 0.046494 | 0.011694 | -0.046482 | -0.011687 | 1.1983e-05 | 7.5859e-06 | 0.070127 | 0.070127 | 0.070127 | 0.98676 | -0.25451 | 0.98648 | -0.25991 | 19.2658
75 | 0.0041768 | 0.0010468 | -0.0041767 | -0.0010468 | 8.7206e-08 | -1.9263e-08 | 0.0062944 | 0.0062944 | 0.0062944 | 0.9874 | -0.24209 | 0.98738 | -0.24253 | 1.7292
76 | 0.024549 | 0.006161 | -0.024534 | -0.0061518 | 1.4959e-05 | 9.1854e-06 | 0.036619 | 0.036619 | 0.036619 | 0.99765 | -0.045052 | 0.99698 | -0.057837 | 10.0601
77 | 0.024534 | 0.0061518 | -0.024529 | -0.0061485 | 5.4792e-06 | 3.3647e-06 | 0.036619 | 0.036619 | 0.036619 | 0.99698 | -0.057837 | 0.99674 | -0.062525 | 10.0601
78 | 0.013754 | 0.003448 | -0.013752 | -0.0034474 | 1.0988e-06 | 6.1265e-07 | 0.020533 | 0.020533 | 0.020533 | 0.99674 | -0.062525 | 0.99665 | -0.064201 | 5.6409
79 | 0.013752 | 0.0034474 | -0.01375 | -0.0034461 | 2.2563e-06 | 1.2581e-06 | 0.020533 | 0.020533 | 0.020533 | 0.99665 | -0.064201 | 0.99647 | -0.067645 | 5.6409
80 | 0.043132 | 0.010847 | -0.043097 | -0.010825 | 3.5092e-05 | 2.2177e-05 | 0.065074 | 0.065074 | 0.065074 | 0.98648 | -0.25991 | 0.98561 | -0.27696 | 17.8775
81 | -0.039726 | -0.0099708 | 0.039749 | 0.0099856 | 2.3465e-05 | 1.4796e-05 | 0.060019 | 0.060019 | 0.060019 | 0.98497 | -0.28933 | 0.98561 | -0.27696 | 16.4889
82 | 0.036659 | 0.0092024 | -0.036652 | -0.0091979 | 7.1047e-06 | 4.4684e-06 | 0.055387 | 0.055387 | 0.055387 | 0.98497 | -0.28933 | 0.98476 | -0.2934 | 15.2163
83 | 0.033589 | 0.0084301 | -0.033583 | -0.0084264 | 5.9635e-06 | 3.7381e-06 | 0.050758 | 0.050758 | 0.050758 | 0.98476 | -0.2934 | 0.98457 | -0.29712 | 13.9446
84 | 0.03052 | 0.0076588 | -0.030515 | -0.0076556 | 5.0754e-06 | 3.1674e-06 | 0.046129 | 0.046129 | 0.046129 | 0.98457 | -0.29712 | 0.98439 | -0.30061 | 12.6729
85 | 0.027452 | 0.0068878 | -0.027448 | -0.0068854 | 3.9874e-06 | 2.4735e-06 | 0.041499 | 0.041499 | 0.041499 | 0.98439 | -0.30061 | 0.98424 | -0.30366 | 11.4007
86 | 0.024381 | 0.0061169 | -0.024378 | -0.0061149 | 3.1463e-06 | 1.9352e-06 | 0.036863 | 0.036863 | 0.036863 | 0.98424 | -0.30366 | 0.9841 | -0.30636 | 10.1272
87 | 0.002415 | 0.000605 | -0.0024149 | -0.00060522 | 1.1534e-07 | -2.2209e-07 | 0.0036427 | 0.0036428 | 0.0036428 | 0.98647 | -0.26047 | 0.98642 | -0.26147 | 1.0008
88 | -0.0213 | -0.0053383 | 0.021307 | 0.0053423 | 6.5157e-06 | 3.9578e-06 | 0.032231 | 0.032231 | 0.032231 | 0.98336 | -0.32077 | 0.98369 | -0.31435 | 8.8547
89 | -0.021307 | -0.0053423 | 0.021315 | 0.0053472 | 8.1155e-06 | 4.9293e-06 | 0.032231 | 0.032231 | 0.032231 | 0.98369 | -0.31435 | 0.9841 | -0.30636 | 8.8547

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4972 | 0.12578

## res_load
| p_mw | q_mvar
0 | 0.029192 | 0.0073163
1 | 0.0024141 | 0.00060502
2 | 0.003564 | 0.00089321
3 | 0.017629 | 0.0044182
4 | 0.004834 | 0.0012115
5 | 0.048667 | 0.012197
6 | 0.0034862 | 0.00087371
7 | 0.0021267 | 0.00053299
8 | 0.015951 | 0.0039977
9 | 0.0096891 | 0.0024283
10 | 0.010277 | 0.0025757
11 | 0.0070406 | 0.0017645
12 | 0.0071579 | 0.0017939
13 | 0.0039595 | 0.00099235
14 | 0.0034595 | 0.00086703
15 | 0.0075643 | 0.0018958
16 | 0.0061485 | 0.001541
17 | 0.0054448 | 0.0013646
18 | 0.0062161 | 0.0015579
19 | 0.012865 | 0.0032243
20 | 0.0063651 | 0.0015952
21 | 0.0056126 | 0.0014067
22 | 0.010079 | 0.0025259
23 | 0.005113 | 0.0012814
24 | 0.0046699 | 0.0011704
25 | 0.0097835 | 0.002452
26 | 0.013834 | 0.003467
27 | 0.0077294 | 0.0019372
28 | 0.0046647 | 0.0011691
29 | 0.0078453 | 0.0019662
30 | 0.0074841 | 0.0018757
31 | 0.0094055 | 0.0023572
32 | 0.0056193 | 0.0014083
33 | 0.0031784 | 0.00079658
34 | 0.0028859 | 0.00072327
35 | 0.0023843 | 0.00059756
36 | 0.012253 | 0.0030709
37 | 0.0045728 | 0.0011461
38 | 0.0023912 | 0.00059928
39 | 0.014334 | 0.0035923
40 | 0.010646 | 0.0026681
41 | 0.0045728 | 0.0011461
42 | 0.00045701 | 0.00011454
43 | 0.0045779 | 0.0011473
44 | 0.0018611 | 0.00046642
45 | 0.001439 | 0.00036065
46 | 0.003426 | 0.00085864
47 | 0.0041767 | 0.0010468
48 | 0.0087616 | 0.0021959
49 | 0.0046882 | 0.001175
50 | 0.011633 | 0.0029156
51 | 0.0074046 | 0.0018558
52 | 0.0041767 | 0.0010468
53 | 0.010775 | 0.0027005
54 | 0.0033502 | 0.00083964
55 | 0.01375 | 0.0034461
56 | 0.0030663 | 0.00076849
57 | 0.0033481 | 0.0008391
58 | 0.0030633 | 0.00076774
59 | 0.003063 | 0.00076765
60 | 0.0030633 | 0.00076775
61 | 0.0030663 | 0.00076849
62 | 0.0023768 | 0.00059568
63 | 0.0024149 | 0.00060522
64 | 0.0213 | 0.0053383
65 | 0.0030633 | 0.00076775

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1