## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_96-25_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_96-25_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_96-25_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_96-25_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_96-25_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_96-25_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_96-25_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_96-25_0_4_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_96-25_0_4_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_96-25_0_4_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_96-25_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_96-25_0_4_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_96-25_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_96-25_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_96-25_0_4_node_91 | 0.4 | n |  | TRUE
15 | bus_LV_96-25_0_4_node_94 | 0.4 | n |  | TRUE
16 | bus_LV_96-25_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_96-25_0_4_node_86 | 0.4 | n |  | TRUE
18 | bus_LV_96-25_0_4_node_90 | 0.4 | n |  | TRUE
19 | bus_LV_96-25_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_96-25_0_4_node_80 | 0.4 | n |  | TRUE
21 | bus_LV_96-25_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_96-25_0_4_node_88 | 0.4 | n |  | TRUE
23 | bus_LV_96-25_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_96-25_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_96-25_0_4_node_79 | 0.4 | n |  | TRUE
26 | bus_LV_96-25_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_96-25_0_4_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_96-25_0_4_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_96-25_0_4_node_46 | 0.4 | n |  | TRUE
30 | bus_LV_96-25_0_4_node_68 | 0.4 | n |  | TRUE
31 | bus_LV_96-25_0_4_node_70 | 0.4 | n |  | TRUE
32 | bus_LV_96-25_0_4_node_85 | 0.4 | n |  | TRUE
33 | bus_LV_96-25_0_4_node_66 | 0.4 | n |  | TRUE
34 | bus_LV_96-25_0_4_node_67 | 0.4 | n |  | TRUE
35 | bus_LV_96-25_0_4_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_96-25_0_4_node_72 | 0.4 | n |  | TRUE
37 | bus_LV_96-25_0_4_node_71 | 0.4 | n |  | TRUE
38 | bus_LV_96-25_0_4_node_89 | 0.4 | n |  | TRUE
39 | bus_MV_669_0_node_139 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_96-25_0_4_load_0 | 0 | 0.0061339 | 0.0015373 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_96-25_0_4_load_2 | 2 | 0.0016378 | 0.00041046 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_96-25_0_4_load_26 | 8 | 0.007412 | 0.0018576 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_96-25_0_4_load_27 | 9 | 0.069119 | 0.017323 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_96-25_0_4_load_28 | 11 | 0.020243 | 0.0050733 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_96-25_0_4_load_91 | 14 | 0.018908 | 0.0047389 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_96-25_0_4_load_94 | 15 | 0.019734 | 0.0049457 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_96-25_0_4_load_86 | 17 | 0.006099 | 0.0015285 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_96-25_0_4_load_90 | 18 | 0.040019 | 0.01003 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_96-25_0_4_load_80 | 20 | 0.022413 | 0.0056171 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_96-25_0_4_load_88 | 22 | 0.065909 | 0.016518 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_96-25_0_4_load_79 | 25 | 0.0085891 | 0.0021526 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_96-25_0_4_load_24 | 26 | 0.0070438 | 0.0017653 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_96-25_0_4_load_25 | 27 | 0.0020029 | 0.00050196 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_96-25_0_4_load_29 | 28 | 0.0017216 | 0.00043147 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_96-25_0_4_load_85 | 32 | 0.010423 | 0.0026122 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_96-25_0_4_load_66 | 33 | 0.0075678 | 0.0018967 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_96-25_0_4_load_67 | 34 | 0.0041723 | 0.0010457 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_96-25_0_4_load_69 | 35 | 0.0025153 | 0.00063039 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_96-25_0_4_load_72 | 36 | 0.0041145 | 0.0010312 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_96-25_0_4_line_0 |  | 0 | 1 | 0.048976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_96-25_0_4_line_1 |  | 0 | 2 | 0.037116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_96-25_0_4_line_2 |  | 1 | 3 | 0.036341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_96-25_0_4_line_3 |  | 1 | 4 | 0.085016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_96-25_0_4_line_4 |  | 3 | 8 | 0.0078789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_96-25_0_4_line_5 |  | 4 | 10 | 0.10345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_96-25_0_4_line_6 |  | 4 | 11 | 0.043326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_96-25_0_4_line_7 |  | 5 | 6 | 0.041353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_96-25_0_4_line_8 |  | 5 | 7 | 0.041537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_96-25_0_4_line_9 |  | 5 | 8 | 0.0093404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_96-25_0_4_line_10 |  | 6 | 9 | 0.020694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_96-25_0_4_line_11 |  | 7 | 26 | 0.038503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_96-25_0_4_line_12 |  | 9 | 27 | 0.012677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_96-25_0_4_line_13 |  | 10 | 15 | 0.001409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_96-25_0_4_line_14 |  | 10 | 12 | 0.056421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_96-25_0_4_line_15 |  | 11 | 28 | 0.04754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_96-25_0_4_line_16 |  | 12 | 13 | 0.030535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_96-25_0_4_line_17 |  | 12 | 14 | 0.04441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_96-25_0_4_line_18 |  | 13 | 18 | 0.029582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_96-25_0_4_line_19 |  | 13 | 16 | 0.029975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_96-25_0_4_line_20 |  | 16 | 17 | 0.03719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_96-25_0_4_line_21 |  | 17 | 24 | 0.011127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_96-25_0_4_line_22 |  | 18 | 38 | 0.037366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_96-25_0_4_line_23 |  | 19 | 20 | 0.008717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_96-25_0_4_line_24 |  | 19 | 21 | 0.013762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_96-25_0_4_line_25 |  | 20 | 37 | 0.017275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_96-25_0_4_line_26 |  | 21 | 22 | 0.027165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_96-25_0_4_line_27 |  | 22 | 38 | 0.010287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_96-25_0_4_line_28 |  | 23 | 24 | 0.054901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_96-25_0_4_line_29 |  | 23 | 25 | 0.026093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_96-25_0_4_line_30 |  | 29 | 30 | 0.01904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_96-25_0_4_line_31 |  | 29 | 31 | 0.019748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_96-25_0_4_line_32 |  | 29 | 32 | 0.054087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_96-25_0_4_line_33 |  | 30 | 35 | 0.038128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_96-25_0_4_line_34 |  | 30 | 33 | 0.041349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_96-25_0_4_line_35 |  | 31 | 37 | 0.015225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_96-25_0_4_line_36 |  | 33 | 34 | 0.034493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_96-25_0_4_line_37 |  | 35 | 36 | 0.0021723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_96-25_0_4_trafo_12 | 0.63 MVA 20/0.4 kV | 39 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2677479.189 | 1255234.4388 | 2677456.247 | 1255254.2202 | 2677442.3027 | 1255266.6546
1 | 2677411.3398 | 1255284.8782 | 2677418.0707 | 1255284.7105 | 2677429.0754 | 1255278.4496 | 2677442.3027 | 1255266.6546
2 | 2677458.2648 | 1255260.2733 | 2677469.1267 | 1255249.3739 | 2677473.9498 | 1255244.5445 | 2677481.4461 | 1255237.7708 | 2677479.189 | 1255234.4388
3 | 2677479.189 | 1255234.4388 | 2677489.4225 | 1255228.3237 | 2677490.8289 | 1255229.7987 | 2677498.2795 | 1255243.2284 | 2677501.1889 | 1255248.5927 | 2677507.1775 | 1255254.9981 | 2677515.7649 | 1255261.1039 | 2677530.4164 | 1255268.4233 | 2677536.7326 | 1255270.5409 | 2677543.8345 | 1255272.0017
4 | 2677458.2648 | 1255260.2733 | 2677460.1495 | 1255262.0882 | 2677463.9349 | 1255265.7438
5 | 2677543.8345 | 1255272.0017 | 2677536.7326 | 1255270.5409 | 2677530.4164 | 1255268.4233 | 2677526.3224 | 1255275.753 | 2677536.2432 | 1255282.5657 | 2677538.6095 | 1255285.6212 | 2677550.019 | 1255300.2926 | 2677564.7613 | 1255297.2167 | 2677564.469 | 1255299.3811 | 2677566.7424 | 1255305.4933 | 2677572.6556 | 1255314.1883 | 2677582.7296 | 1255307.0038
6 | 2677543.8345 | 1255272.0017 | 2677544.065 | 1255262.4642 | 2677543.1774 | 1255254.2131 | 2677552.2679 | 1255230.4019
7 | 2677450.3339 | 1255301.4114 | 2677445.936 | 1255298.5406 | 2677457.4217 | 1255286.0815 | 2677465.1186 | 1255277.8093 | 2677470.653 | 1255272.2331
8 | 2677470.653 | 1255272.2331 | 2677474.0324 | 1255269.3529 | 2677482.782 | 1255270.5572 | 2677485.1626 | 1255270.7996 | 2677484.4898 | 1255273.2148 | 2677483.0931 | 1255285.4056 | 2677485.0017 | 1255286.5426 | 2677486.7849 | 1255288.0448 | 2677486.1265 | 1255294.5522
9 | 2677470.653 | 1255272.2331 | 2677469.3941 | 1255271.0157 | 2677463.9349 | 1255265.7438
10 | 2677450.3339 | 1255301.4114 | 2677441.9487 | 1255309.8302 | 2677437.8255 | 1255311.333 | 2677433.4678 | 1255310.5755
11 | 2677486.1265 | 1255294.5522 | 2677490.0232 | 1255294.7922 | 2677496.7464 | 1255300.9737 | 2677498.9345 | 1255303.8155 | 2677498.4717 | 1255306.9007 | 2677497.2521 | 1255309.5978 | 2677486.4483 | 1255321.1256
12 | 2677424.0486 | 1255302.0914 | 2677433.4678 | 1255310.5755
13 | 2677583.8794 | 1255306.1849 | 2677582.7296 | 1255307.0038
14 | 2677582.7296 | 1255307.0038 | 2677586.8791 | 1255312.1286 | 2677585.6226 | 1255315.3368 | 2677589.608 | 1255318.0243 | 2677615.8706 | 1255321.7267 | 2677620.549 | 1255326.2136 | 2677618.8848 | 1255334.6203
15 | 2677584.6889 | 1255214.3585 | 2677569.3699 | 1255208.611 | 2677563.5945 | 1255208.3907 | 2677559.5114 | 1255211.4284 | 2677552.2679 | 1255230.4019
16 | 2677596.28 | 1255340.1838 | 2677601.4083 | 1255340.8404 | 2677606.2839 | 1255341.7938 | 2677606.9952 | 1255337.6 | 2677617.907 | 1255339.5778 | 2677618.8848 | 1255334.6203
17 | 2677618.8848 | 1255334.6203 | 2677662.4572 | 1255343.2061
18 | 2677596.28 | 1255340.1838 | 2677592.2144 | 1255362.6028 | 2677589.9698 | 1255365.2309 | 2677587.4678 | 1255367.4447
19 | 2677596.28 | 1255340.1838 | 2677601.4083 | 1255340.8404 | 2677606.2839 | 1255341.7938 | 2677625.7483 | 1255345.6184
20 | 2677625.7483 | 1255345.6184 | 2677621.724 | 1255374.0869 | 2677617.9085 | 1255381.4535 | 2677617.8804 | 1255381.5928
21 | 2677615.6742 | 1255392.4992 | 2677617.8804 | 1255381.5928
22 | 2677569.0788 | 1255395.4354 | 2677571.9454 | 1255391.9704 | 2677575.6364 | 1255392.3634 | 2677577.0618 | 1255391.2368 | 2677579.3738 | 1255375.9891 | 2677580.6819 | 1255373.4487 | 2677587.4678 | 1255367.4447
23 | 2677514.6794 | 1255387.1837 | 2677520.6689 | 1255380.8352
24 | 2677520.6689 | 1255380.8352 | 2677524.4767 | 1255384.4099 | 2677532.6042 | 1255387.0293
25 | 2677514.6794 | 1255387.1837 | 2677502.9864 | 1255399.9291
26 | 2677532.6042 | 1255387.0293 | 2677537.5544 | 1255388.6175 | 2677559.0246 | 1255393.261
27 | 2677569.0788 | 1255395.4354 | 2677559.0246 | 1255393.261
28 | 2677590.5003 | 1255428.3294 | 2677604.8106 | 1255431.1412 | 2677605.5718 | 1255427.1704 | 2677607.6025 | 1255416.6892 | 2677610.2637 | 1255411.6314 | 2677615.6742 | 1255392.4992
29 | 2677590.5003 | 1255428.3294 | 2677567.0445 | 1255420.5831 | 2677565.6938 | 1255420.2479
30 | 2677483.6265 | 1255414.0641 | 2677490.8059 | 1255414.7697 | 2677484.6991 | 1255424.8974
31 | 2677483.6265 | 1255414.0641 | 2677490.8059 | 1255414.7697 | 2677496.437 | 1255415.0547 | 2677500.6348 | 1255409.5833
32 | 2677483.6265 | 1255414.0641 | 2677479.347 | 1255418.2891 | 2677477.4074 | 1255427.5818 | 2677474.4939 | 1255433.4814 | 2677466.7247 | 1255457.6645 | 2677466.0998 | 1255464.2346
33 | 2677484.6991 | 1255424.8974 | 2677502.3435 | 1255430.0209 | 2677511.4537 | 1255435.3552 | 2677520.4537 | 1255437.2541
34 | 2677484.6991 | 1255424.8974 | 2677480.4585 | 1255432.492 | 2677473.096 | 1255452.1103 | 2677470.9518 | 1255463.6087
35 | 2677500.6348 | 1255409.5833 | 2677496.0843 | 1255407.4222 | 2677502.9864 | 1255399.9291
36 | 2677470.9518 | 1255463.6087 | 2677469.9726 | 1255468.8598 | 2677468.0808 | 1255488.3384 | 2677467.3328 | 1255497.8901
37 | 2677522.5793 | 1255437.7026 | 2677520.4537 | 1255437.2541

## bus_geodata
| x | y | coords
0 | 2677442.3027 | 1255266.6546
1 | 2677479.189 | 1255234.4388
2 | 2677411.3398 | 1255284.8782
3 | 2677458.2648 | 1255260.2733
4 | 2677543.8345 | 1255272.0017
5 | 2677470.653 | 1255272.2331
6 | 2677450.3339 | 1255301.4114
7 | 2677486.1265 | 1255294.5522
8 | 2677463.9349 | 1255265.7438
9 | 2677433.4678 | 1255310.5755
10 | 2677582.7296 | 1255307.0038
11 | 2677552.2679 | 1255230.4019
12 | 2677618.8848 | 1255334.6203
13 | 2677596.28 | 1255340.1838
14 | 2677662.4572 | 1255343.2061
15 | 2677583.8794 | 1255306.1849
16 | 2677625.7483 | 1255345.6184
17 | 2677617.8804 | 1255381.5928
18 | 2677587.4678 | 1255367.4447
19 | 2677520.6689 | 1255380.8352
20 | 2677514.6794 | 1255387.1837
21 | 2677532.6042 | 1255387.0293
22 | 2677559.0246 | 1255393.261
23 | 2677590.5003 | 1255428.3294
24 | 2677615.6742 | 1255392.4992
25 | 2677565.6938 | 1255420.2479
26 | 2677486.4483 | 1255321.1256
27 | 2677424.0486 | 1255302.0914
28 | 2677584.6889 | 1255214.3585
29 | 2677483.6265 | 1255414.0641
30 | 2677484.6991 | 1255424.8974
31 | 2677500.6348 | 1255409.5833
32 | 2677466.0998 | 1255464.2346
33 | 2677470.9518 | 1255463.6087
34 | 2677467.3328 | 1255497.8901
35 | 2677520.4537 | 1255437.2541
36 | 2677522.5793 | 1255437.7026
37 | 2677502.9864 | 1255399.9291
38 | 2677569.0788 | 1255395.4354
39 | 2677524.4767 | 1255384.4099

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1