## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_0_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_0_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_0_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_0_0_node_98 | 20 | n |  | TRUE
4 | bus_MV_0_0_node_97 | 20 | n |  | TRUE
5 | bus_MV_0_0_node_76 | 20 | n |  | TRUE
6 | bus_MV_0_0_node_17 | 20 | n |  | TRUE
7 | bus_MV_0_0_node_39 | 20 | n |  | TRUE
8 | bus_MV_0_0_node_3 | 20 | n |  | TRUE
9 | bus_MV_0_0_node_5 | 20 | n |  | TRUE
10 | bus_MV_0_0_node_159 | 20 | n |  | TRUE
11 | bus_MV_0_0_node_13 | 20 | n |  | TRUE
12 | bus_MV_0_0_node_9 | 20 | n |  | TRUE
13 | bus_MV_0_0_node_10 | 20 | n |  | TRUE
14 | bus_MV_0_0_node_11 | 20 | n |  | TRUE
15 | bus_MV_0_0_node_15 | 20 | n |  | TRUE
16 | bus_MV_0_0_node_16 | 20 | n |  | TRUE
17 | bus_MV_0_0_node_18 | 20 | n |  | TRUE
18 | bus_MV_0_0_node_96 | 20 | n |  | TRUE
19 | bus_MV_0_0_node_6 | 20 | n |  | TRUE
20 | bus_MV_0_0_node_7 | 20 | n |  | TRUE
21 | bus_MV_0_0_node_8 | 20 | n |  | TRUE
22 | bus_MV_0_0_node_14 | 20 | n |  | TRUE
23 | bus_MV_0_0_node_156 | 20 | n |  | TRUE
24 | bus_MV_0_0_node_12 | 20 | n |  | TRUE
25 | bus_MV_0_0_node_101 | 20 | n |  | TRUE
26 | bus_MV_0_0_node_19 | 20 | n |  | TRUE
27 | bus_MV_0_0_node_20 | 20 | n |  | TRUE
28 | bus_MV_0_0_node_21 | 20 | n |  | TRUE
29 | bus_MV_0_0_node_24 | 20 | n |  | TRUE
30 | bus_MV_0_0_node_23 | 20 | n |  | TRUE
31 | bus_MV_0_0_node_78 | 20 | n |  | TRUE
32 | bus_MV_0_0_node_22 | 20 | n |  | TRUE
33 | bus_MV_0_0_node_26 | 20 | n |  | TRUE
34 | bus_MV_0_0_node_25 | 20 | n |  | TRUE
35 | bus_MV_0_0_node_27 | 20 | n |  | TRUE
36 | bus_MV_0_0_node_77 | 20 | n |  | TRUE
37 | bus_MV_0_0_node_28 | 20 | n |  | TRUE
38 | bus_MV_0_0_node_164 | 20 | n |  | TRUE
39 | bus_MV_0_0_node_29 | 20 | n |  | TRUE
40 | bus_MV_0_0_node_30 | 20 | n |  | TRUE
41 | bus_MV_0_0_node_31 | 20 | n |  | TRUE
42 | bus_MV_0_0_node_32 | 20 | n |  | TRUE
43 | bus_MV_0_0_node_100 | 20 | n |  | TRUE
44 | bus_MV_0_0_node_33 | 20 | n |  | TRUE
45 | bus_MV_0_0_node_99 | 20 | n |  | TRUE
46 | bus_MV_0_0_node_35 | 20 | n |  | TRUE
47 | bus_MV_0_0_node_36 | 20 | n |  | TRUE
48 | bus_MV_0_0_node_34 | 20 | n |  | TRUE
49 | bus_MV_0_0_node_55 | 20 | n |  | TRUE
50 | bus_MV_0_0_node_56 | 20 | n |  | TRUE
51 | bus_MV_0_0_node_57 | 20 | n |  | TRUE
52 | bus_MV_0_0_node_54 | 20 | n |  | TRUE
53 | bus_MV_0_0_node_37 | 20 | n |  | TRUE
54 | bus_MV_0_0_node_38 | 20 | n |  | TRUE
55 | bus_MV_0_0_node_92 | 20 | n |  | TRUE
56 | bus_MV_0_0_node_89 | 20 | n |  | TRUE
57 | bus_MV_0_0_node_40 | 20 | n |  | TRUE
58 | bus_MV_0_0_node_126 | 20 | n |  | TRUE
59 | bus_MV_0_0_node_41 | 20 | n |  | TRUE
60 | bus_MV_0_0_node_124 | 20 | n |  | TRUE
61 | bus_MV_0_0_node_42 | 20 | n |  | TRUE
62 | bus_MV_0_0_node_80 | 20 | n |  | TRUE
63 | bus_MV_0_0_node_81 | 20 | n |  | TRUE
64 | bus_MV_0_0_node_86 | 20 | n |  | TRUE
65 | bus_MV_0_0_node_87 | 20 | n |  | TRUE
66 | bus_MV_0_0_node_88 | 20 | n |  | TRUE
67 | bus_MV_0_0_node_90 | 20 | n |  | TRUE
68 | bus_MV_0_0_node_91 | 20 | n |  | TRUE
69 | bus_MV_0_0_node_125 | 20 | n |  | TRUE
70 | bus_MV_0_0_node_82 | 20 | n |  | TRUE
71 | bus_MV_0_0_node_43 | 20 | n |  | TRUE
72 | bus_MV_0_0_node_44 | 20 | n |  | TRUE
73 | bus_MV_0_0_node_46 | 20 | n |  | TRUE
74 | bus_MV_0_0_node_70 | 20 | n |  | TRUE
75 | bus_MV_0_0_node_163 | 20 | n |  | TRUE
76 | bus_MV_0_0_node_131 | 20 | n |  | TRUE
77 | bus_MV_0_0_node_71 | 20 | n |  | TRUE
78 | bus_MV_0_0_node_72 | 20 | n |  | TRUE
79 | bus_MV_0_0_node_47 | 20 | n |  | TRUE
80 | bus_MV_0_0_node_85 | 20 | n |  | TRUE
81 | bus_MV_0_0_node_83 | 20 | n |  | TRUE
82 | bus_MV_0_0_node_132 | 20 | n |  | TRUE
83 | bus_MV_0_0_node_135 | 20 | n |  | TRUE
84 | bus_MV_0_0_node_134 | 20 | n |  | TRUE
85 | bus_MV_0_0_node_84 | 20 | n |  | TRUE
86 | bus_MV_0_0_node_48 | 20 | n |  | TRUE
87 | bus_MV_0_0_node_49 | 20 | n |  | TRUE
88 | bus_MV_0_0_node_53 | 20 | n |  | TRUE
89 | bus_MV_0_0_node_50 | 20 | n |  | TRUE
90 | bus_MV_0_0_node_162 | 20 | n |  | TRUE
91 | bus_MV_0_0_node_51 | 20 | n |  | TRUE
92 | bus_MV_0_0_node_52 | 20 | n |  | TRUE
93 | bus_MV_0_0_node_129 | 20 | n |  | TRUE
94 | bus_MV_0_0_node_165 | 20 | n |  | TRUE
95 | bus_MV_0_0_node_145 | 20 | n |  | TRUE
96 | bus_MV_0_0_node_75 | 20 | n |  | TRUE
97 | bus_MV_0_0_node_95 | 20 | n |  | TRUE
98 | bus_MV_0_0_node_59 | 20 | n |  | TRUE
99 | bus_MV_0_0_node_61 | 20 | n |  | TRUE
100 | bus_MV_0_0_node_62 | 20 | n |  | TRUE
101 | bus_MV_0_0_node_60 | 20 | n |  | TRUE
102 | bus_MV_0_0_node_64 | 20 | n |  | TRUE
103 | bus_MV_0_0_node_65 | 20 | n |  | TRUE
104 | bus_MV_0_0_node_66 | 20 | n |  | TRUE
105 | bus_MV_0_0_node_63 | 20 | n |  | TRUE
106 | bus_MV_0_0_node_69 | 20 | n |  | TRUE
107 | bus_MV_0_0_node_161 | 20 | n |  | TRUE
108 | bus_MV_0_0_node_157 | 20 | n |  | TRUE
109 | bus_MV_0_0_node_68 | 20 | n |  | TRUE
110 | bus_MV_0_0_node_73 | 20 | n |  | TRUE
111 | bus_MV_0_0_node_67 | 20 | n |  | TRUE
112 | bus_MV_0_0_node_160 | 20 | n |  | TRUE
113 | bus_MV_0_0_node_153 | 20 | n |  | TRUE
114 | bus_MV_0_0_node_152 | 20 | n |  | TRUE
115 | bus_MV_0_0_node_127 | 20 | n |  | TRUE
116 | bus_MV_0_0_node_74 | 20 | n |  | TRUE
117 | bus_MV_0_0_node_154 | 20 | n |  | TRUE
118 | bus_MV_0_0_node_147 | 20 | n |  | TRUE
119 | bus_MV_0_0_node_79 | 20 | n |  | TRUE
120 | bus_MV_0_0_node_93 | 20 | n |  | TRUE
121 | bus_MV_0_0_node_94 | 20 | n |  | TRUE
122 | bus_MV_0_0_node_136 | 20 | n |  | TRUE
123 | bus_MV_0_0_node_133 | 20 | n |  | TRUE
124 | bus_MV_0_0_node_102 | 20 | n |  | TRUE
125 | bus_MV_0_0_node_103 | 20 | n |  | TRUE
126 | bus_MV_0_0_node_104 | 20 | n |  | TRUE
127 | bus_MV_0_0_node_105 | 20 | n |  | TRUE
128 | bus_MV_0_0_node_106 | 20 | n |  | TRUE
129 | bus_MV_0_0_node_107 | 20 | n |  | TRUE
130 | bus_MV_0_0_node_108 | 20 | n |  | TRUE
131 | bus_MV_0_0_node_110 | 20 | n |  | TRUE
132 | bus_MV_0_0_node_114 | 20 | n |  | TRUE
133 | bus_MV_0_0_node_109 | 20 | n |  | TRUE
134 | bus_MV_0_0_node_158 | 20 | n |  | TRUE
135 | bus_MV_0_0_node_113 | 20 | n |  | TRUE
136 | bus_MV_0_0_node_116 | 20 | n |  | TRUE
137 | bus_MV_0_0_node_112 | 20 | n |  | TRUE
138 | bus_MV_0_0_node_111 | 20 | n |  | TRUE
139 | bus_MV_0_0_node_115 | 20 | n |  | TRUE
140 | bus_MV_0_0_node_137 | 20 | n |  | TRUE
141 | bus_MV_0_0_node_148 | 20 | n |  | TRUE
142 | bus_MV_0_0_node_155 | 20 | n |  | TRUE
143 | bus_MV_0_0_node_117 | 20 | n |  | TRUE
144 | bus_MV_0_0_node_138 | 20 | n |  | TRUE
145 | bus_MV_0_0_node_118 | 20 | n |  | TRUE
146 | bus_MV_0_0_node_119 | 20 | n |  | TRUE
147 | bus_MV_0_0_node_120 | 20 | n |  | TRUE
148 | bus_MV_0_0_node_121 | 20 | n |  | TRUE
149 | bus_MV_0_0_node_123 | 20 | n |  | TRUE
150 | bus_MV_0_0_node_149 | 20 | n |  | TRUE
151 | bus_MV_0_0_node_151 | 20 | n |  | TRUE
152 | bus_MV_0_0_node_150 | 20 | n |  | TRUE
153 | bus_MV_0_0_node_128 | 20 | n |  | TRUE
154 | bus_MV_0_0_node_130 | 20 | n |  | TRUE
155 | bus_MV_0_0_node_139 | 20 | n |  | TRUE
156 | bus_MV_0_0_node_140 | 20 | n |  | TRUE
157 | bus_MV_0_0_node_141 | 20 | n |  | TRUE
158 | bus_MV_0_0_node_142 | 20 | n |  | TRUE
159 | bus_MV_0_0_node_143 | 20 | n |  | TRUE
160 | bus_MV_0_0_node_144 | 20 | n |  | TRUE
161 | bus_MV_0_0_node_146 | 20 | n |  | TRUE
162 | bus_HV_0_0_node_95 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_0_0_load_0 | 0 | 0.19609 | 0.094971 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_0_0_load_98 | 3 | 0.1644 | 0.079621 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_0_0_load_97 | 4 | 0.16855 | 0.081631 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_0_0_load_76 | 5 | 0.38339 | 0.18568 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_0_0_load_3 | 8 | 0.26043 | 0.12613 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_0_0_load_159 | 10 | 0.1191 | 0.057684 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_0_0_load_9 | 12 | 0.35396 | 0.17143 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_0_0_load_15 | 15 | 0.20892 | 0.10118 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_0_0_load_96 | 18 | 0.084867 | 0.041103 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_0_0_load_6 | 19 | 0.26835 | 0.12997 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_0_0_load_7 | 20 | 0.12058 | 0.058398 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_0_0_load_156 | 23 | 0.1489 | 0.072113 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_0_0_load_19 | 26 | 0.086396 | 0.041844 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_0_0_load_78 | 31 | 0.083643 | 0.04051 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_0_0_load_25 | 34 | 0.24031 | 0.11639 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_0_0_load_27 | 35 | 0.34859 | 0.16883 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_0_0_load_77 | 36 | 0.067859 | 0.032866 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_0_0_load_164 | 38 | 0.29515 | 0.14295 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_0_0_load_30 | 40 | 0.20266 | 0.098153 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_0_0_load_31 | 41 | 0.27352 | 0.13247 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_0_0_load_99 | 45 | 0.27044 | 0.13098 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_0_0_load_35 | 46 | 0.40686 | 0.19705 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_0_0_load_34 | 48 | 0.37295 | 0.18063 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_0_0_load_54 | 52 | 0.20449 | 0.09904 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_0_0_load_92 | 55 | 0.26962 | 0.13058 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_0_0_load_89 | 56 | 0.2287 | 0.11076 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_0_0_load_126 | 58 | 0.099894 | 0.048381 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_0_0_load_124 | 60 | 0.087382 | 0.042321 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_0_0_load_80 | 62 | 0.35401 | 0.17146 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_0_0_load_81 | 63 | 0.079331 | 0.038422 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_0_0_load_86 | 64 | 0.18552 | 0.08985 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_0_0_load_91 | 68 | 0.24645 | 0.11936 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_0_0_load_43 | 71 | 0.36498 | 0.17677 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_0_0_load_70 | 74 | 0.24988 | 0.12102 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_0_0_load_163 | 75 | 0.27144 | 0.13147 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_0_0_load_131 | 76 | 0.2841 | 0.13759 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_0_0_load_83 | 81 | 0.34306 | 0.16615 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_0_0_load_135 | 83 | 0.24545 | 0.11888 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_0_0_load_134 | 84 | 0.12146 | 0.058827 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_0_0_load_84 | 85 | 0.14559 | 0.070514 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_0_0_load_48 | 86 | 0.1719 | 0.083254 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_0_0_load_162 | 90 | 0.37922 | 0.18367 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_0_0_load_51 | 91 | 0.24286 | 0.11762 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_0_0_load_165 | 94 | 0.32408 | 0.15696 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_0_0_load_145 | 95 | 0.19049 | 0.092257 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_0_0_load_75 | 96 | 0.24357 | 0.11797 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_0_0_load_59 | 98 | 0.38282 | 0.18541 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_0_0_load_69 | 106 | 0.10152 | 0.049166 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_0_0_load_161 | 107 | 0.17061 | 0.082628 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_0_0_load_157 | 108 | 0.37017 | 0.17928 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_0_0_load_73 | 110 | 0.31407 | 0.15211 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_0_0_load_160 | 112 | 0.12364 | 0.059879 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_0_0_load_152 | 114 | 0.10883 | 0.052709 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_0_0_load_74 | 116 | 0.18712 | 0.090625 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_0_0_load_154 | 117 | 0.11538 | 0.05588 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_0_0_load_79 | 119 | 0.22095 | 0.10701 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_0_0_load_94 | 121 | 0.1102 | 0.05337 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_0_0_load_136 | 122 | 0.21649 | 0.10485 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_0_0_load_102 | 124 | 0.89177 | 0.43191 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_0_0_load_107 | 129 | 0.070874 | 0.034326 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_0_0_load_108 | 130 | 0.12267 | 0.059411 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_0_0_load_114 | 132 | 1.2043 | 0.58326 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_0_0_load_158 | 134 | 0.26189 | 0.12684 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_0_0_load_116 | 136 | 0.14713 | 0.07126 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_0_0_load_115 | 139 | 0.58454 | 0.2831 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_0_0_load_137 | 140 | 0.1146 | 0.055504 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_0_0_load_148 | 141 | 0.37867 | 0.1834 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_0_0_load_155 | 142 | 0.11453 | 0.055469 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_0_0_load_119 | 146 | 0.3807 | 0.18438 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_0_0_load_120 | 147 | 1.77 | 0.85724 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_0_0_load_149 | 150 | 0.084724 | 0.041034 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_0_0_load_151 | 151 | 0.16096 | 0.077957 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_0_0_load_150 | 152 | 0.29429 | 0.14253 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_0_0_load_130 | 154 | 0.075934 | 0.036777 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_0_0_load_139 | 155 | 0.10611 | 0.051393 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_0_0_load_140 | 156 | 0.14013 | 0.067869 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_0_0_load_144 | 160 | 0.13663 | 0.066173 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_0_0_load_146 | 161 | 0.25783 | 0.12487 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 97 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_0_0_line_0 |  | 0 | 1 | 0.056318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_0_0_line_1 |  | 1 | 2 | 0.33802 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_0_0_line_2 |  | 2 | 8 | 0.038284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_0_0_line_3 |  | 2 | 3 | 0.15777 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_0_0_line_4 |  | 3 | 4 | 0.055972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_0_0_line_5 |  | 4 | 24 | 0.047135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_0_0_line_6 |  | 5 | 6 | 1.4159 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
7 | MV_0_0_line_7 |  | 5 | 7 | 0.036338 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
8 | MV_0_0_line_8 |  | 6 | 15 | 0.021025 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
9 | MV_0_0_line_9 |  | 7 | 54 | 0.46692 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
10 | MV_0_0_line_10 |  | 9 | 10 | 0.022303 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
11 | MV_0_0_line_11 |  | 9 | 11 | 0.17045 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
12 | MV_0_0_line_12 |  | 10 | 17 | 0.064516 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
13 | MV_0_0_line_13 |  | 11 | 18 | 0.04244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_0_0_line_14 |  | 11 | 14 | 0.12893 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
15 | MV_0_0_line_15 |  | 12 | 13 | 0.013221 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_0_0_line_16 |  | 12 | 14 | 0.050864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_0_0_line_17 |  | 13 | 24 | 0.048012 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_0_0_line_18 |  | 14 | 21 | 0.77175 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
19 | MV_0_0_line_19 |  | 15 | 16 | 0.059766 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
20 | MV_0_0_line_20 |  | 16 | 17 | 0.34677 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
21 | MV_0_0_line_21 |  | 19 | 20 | 0.13507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_0_0_line_22 |  | 20 | 21 | 0.13637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_0_0_line_23 |  | 21 | 22 | 0.60305 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
24 | MV_0_0_line_24 |  | 22 | 23 | 0.31627 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
25 | MV_0_0_line_25 |  | 23 | 25 | 0.2993 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
26 | MV_0_0_line_26 |  | 25 | 43 | 0.65388 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
27 | MV_0_0_line_27 |  | 26 | 27 | 0.027932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_0_0_line_28 |  | 26 | 28 | 0.030564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_0_0_line_29 |  | 27 | 29 | 1.3989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_0_0_line_30 |  | 28 | 30 | 0.65108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_0_0_line_31 |  | 29 | 31 | 0.044986 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_0_0_line_32 |  | 30 | 35 | 0.017323 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_0_0_line_33 |  | 30 | 32 | 0.30379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_0_0_line_34 |  | 31 | 38 | 0.86686 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_0_0_line_35 |  | 32 | 33 | 1.124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_0_0_line_36 |  | 32 | 34 | 0.032214 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_0_0_line_37 |  | 33 | 36 | 0.16217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_0_0_line_38 |  | 35 | 37 | 0.16087 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_0_0_line_39 |  | 37 | 39 | 0.35777 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_0_0_line_40 |  | 38 | 119 | 0.9829 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
41 | MV_0_0_line_41 |  | 39 | 40 | 0.063841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_0_0_line_42 |  | 41 | 42 | 0.038507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_0_0_line_43 |  | 41 | 43 | 1.537 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
44 | MV_0_0_line_44 |  | 42 | 44 | 0.74985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_0_0_line_45 |  | 43 | 45 | 0.16223 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_0_0_line_46 |  | 44 | 48 | 0.080661 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_0_0_line_47 |  | 46 | 47 | 0.081724 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_0_0_line_48 |  | 47 | 53 | 0.24243 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_0_0_line_49 |  | 47 | 54 | 0.45428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_0_0_line_50 |  | 49 | 50 | 0.27926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_0_0_line_51 |  | 49 | 51 | 0.46218 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_0_0_line_52 |  | 49 | 52 | 0.040487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_0_0_line_53 |  | 50 | 94 | 0.034315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_0_0_line_54 |  | 51 | 95 | 0.0015728 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_0_0_line_55 |  | 51 | 96 | 0.012422 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_0_0_line_56 |  | 53 | 55 | 0.016759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_0_0_line_57 |  | 54 | 56 | 0.075629 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
58 | MV_0_0_line_58 |  | 56 | 67 | 0.007277 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
59 | MV_0_0_line_59 |  | 57 | 58 | 0.012347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_0_0_line_60 |  | 57 | 59 | 0.13719 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
61 | MV_0_0_line_61 |  | 57 | 60 | 0.050922 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
62 | MV_0_0_line_62 |  | 59 | 61 | 0.35728 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_0_0_line_63 |  | 59 | 62 | 0.014701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_0_0_line_64 |  | 60 | 69 | 0.05259 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
65 | MV_0_0_line_65 |  | 61 | 63 | 0.053634 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
66 | MV_0_0_line_66 |  | 63 | 70 | 0.043621 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
67 | MV_0_0_line_67 |  | 64 | 65 | 0.10226 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_0_0_line_68 |  | 65 | 66 | 0.21574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_0_0_line_69 |  | 66 | 67 | 0.19483 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
70 | MV_0_0_line_70 |  | 66 | 68 | 0.07841 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
71 | MV_0_0_line_71 |  | 68 | 92 | 0.28021 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
72 | MV_0_0_line_72 |  | 69 | 115 | 0.25794 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
73 | MV_0_0_line_73 |  | 69 | 93 | 0.14856 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
74 | MV_0_0_line_74 |  | 70 | 120 | 0.008771 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
75 | MV_0_0_line_75 |  | 71 | 72 | 0.070907 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_0_0_line_76 |  | 72 | 73 | 0.37398 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
77 | MV_0_0_line_77 |  | 72 | 74 | 1.1656 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
78 | MV_0_0_line_78 |  | 73 | 75 | 0.09649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_0_0_line_79 |  | 73 | 76 | 0.20689 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
80 | MV_0_0_line_80 |  | 74 | 77 | 0.096159 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
81 | MV_0_0_line_81 |  | 76 | 82 | 0.059778 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
82 | MV_0_0_line_82 |  | 77 | 78 | 0.44423 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
83 | MV_0_0_line_83 |  | 78 | 119 | 0.039188 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
84 | MV_0_0_line_84 |  | 79 | 80 | 0.14928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_0_0_line_85 |  | 79 | 81 | 0.051094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_0_0_line_86 |  | 80 | 83 | 0.038462 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
87 | MV_0_0_line_87 |  | 80 | 84 | 0.058161 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
88 | MV_0_0_line_88 |  | 81 | 85 | 0.024229 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_0_0_line_89 |  | 82 | 123 | 0.002242 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
90 | MV_0_0_line_90 |  | 83 | 122 | 0.035971 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
91 | MV_0_0_line_91 |  | 84 | 123 | 0.055057 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
92 | MV_0_0_line_92 |  | 86 | 87 | 0.05078 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_0_0_line_93 |  | 86 | 88 | 0.22297 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
94 | MV_0_0_line_94 |  | 87 | 89 | 0.19628 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
95 | MV_0_0_line_95 |  | 88 | 90 | 0.006614 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
96 | MV_0_0_line_96 |  | 89 | 91 | 0.038449 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
97 | MV_0_0_line_97 |  | 90 | 93 | 0.004103 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
98 | MV_0_0_line_98 |  | 91 | 92 | 0.095383 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
99 | MV_0_0_line_99 |  | 94 | 97 | 0.01814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_0_0_line_100 |  | 97 | 120 | 0.45845 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_0_0_line_101 |  | 98 | 99 | 0.004842 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
102 | MV_0_0_line_102 |  | 98 | 100 | 0.039396 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
103 | MV_0_0_line_103 |  | 98 | 101 | 0.040072 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
104 | MV_0_0_line_104 |  | 99 | 102 | 0.38907 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_0_0_line_105 |  | 99 | 103 | 0.49918 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
106 | MV_0_0_line_106 |  | 100 | 104 | 0.080524 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
107 | MV_0_0_line_107 |  | 101 | 105 | 0.014145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_0_0_line_108 |  | 102 | 107 | 0.022838 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_0_0_line_109 |  | 103 | 108 | 0.031283 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
110 | MV_0_0_line_110 |  | 104 | 109 | 0.4079 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
111 | MV_0_0_line_111 |  | 104 | 110 | 0.063207 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
112 | MV_0_0_line_112 |  | 105 | 106 | 0.028765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_0_0_line_113 |  | 106 | 111 | 0.039557 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_0_0_line_114 |  | 108 | 115 | 0.051085 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
115 | MV_0_0_line_115 |  | 109 | 113 | 0.0526 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
116 | MV_0_0_line_116 |  | 109 | 114 | 0.038799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_0_0_line_117 |  | 110 | 116 | 0.039032 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_0_0_line_118 |  | 111 | 112 | 0.011534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_0_0_line_119 |  | 113 | 117 | 0.039857 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
120 | MV_0_0_line_120 |  | 114 | 118 | 0.049243 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_0_0_line_121 |  | 115 | 153 | 0.28045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_0_0_line_122 |  | 117 | 142 | 0.00065589 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
123 | MV_0_0_line_123 |  | 118 | 159 | 0.29938 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_0_0_line_124 |  | 120 | 121 | 0.062686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_0_0_line_125 |  | 122 | 144 | 0.045812 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
126 | MV_0_0_line_126 |  | 124 | 125 | 0.060301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_0_0_line_127 |  | 124 | 126 | 0.060339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_0_0_line_128 |  | 125 | 127 | 0.004223 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
129 | MV_0_0_line_129 |  | 125 | 128 | 0.033163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_0_0_line_130 |  | 126 | 129 | 0.013263 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_0_0_line_131 |  | 127 | 130 | 0.12284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_0_0_line_132 |  | 127 | 131 | 0.26817 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
133 | MV_0_0_line_133 |  | 128 | 132 | 0.055367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_0_0_line_134 |  | 131 | 136 | 0.017188 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_0_0_line_135 |  | 131 | 137 | 0.16537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_0_0_line_136 |  | 131 | 138 | 0.25804 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
137 | MV_0_0_line_137 |  | 131 | 139 | 0.056219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_0_0_line_138 |  | 131 | 133 | 0.077199 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
139 | MV_0_0_line_139 |  | 132 | 143 | 0.050805 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_0_0_line_140 |  | 133 | 134 | 0.017035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_0_0_line_141 |  | 133 | 135 | 0.071754 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
142 | MV_0_0_line_142 |  | 135 | 142 | 0.047534 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
143 | MV_0_0_line_143 |  | 137 | 141 | 0.042644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_0_0_line_144 |  | 138 | 140 | 0.036048 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
145 | MV_0_0_line_145 |  | 140 | 144 | 0.009173 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
146 | MV_0_0_line_146 |  | 143 | 145 | 0.063597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_0_0_line_147 |  | 144 | 155 | 0.041719 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_0_0_line_148 |  | 145 | 146 | 0.050432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_0_0_line_149 |  | 145 | 147 | 0.0079891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_0_0_line_150 |  | 146 | 148 | 0.036738 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_0_0_line_151 |  | 148 | 149 | 0.18617 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_0_0_line_152 |  | 148 | 150 | 0.11916 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
153 | MV_0_0_line_153 |  | 149 | 151 | 0.0041741 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_0_0_line_154 |  | 150 | 152 | 0.070843 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
155 | MV_0_0_line_155 |  | 153 | 154 | 0.027819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_0_0_line_156 |  | 156 | 157 | 0.012607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_0_0_line_157 |  | 157 | 158 | 0.045837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_0_0_line_158 |  | 158 | 159 | 0.00616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_0_0_line_159 |  | 158 | 160 | 0.040896 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_0_0_line_160 |  | 159 | 161 | 0.044371 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_0_0_trafo_95 | 25 MVA 110/20 kV | 162 | 97 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2672823.475 | 1219539.7193
1 | 2672878.9142 | 1219528.9457
2 | 2672984.4714 | 1219758.3081
3 | 2672881.1486 | 1219877.534
4 | 2672898.0509 | 1219929.4659
5 | 2674822.6836 | 1220887.154
6 | 2673468.6968 | 1220472.9
7 | 2674820.2033 | 1220922.7238
8 | 2673021.303 | 1219748.0527
9 | 2673067.514 | 1220234.99
10 | 2673078.4143 | 1220254.4474
11 | 2672923.0552 | 1220144.5171
12 | 2672953.6056 | 1220018.7097
13 | 2672947.0078 | 1220007.2437
14 | 2672969.4643 | 1220064.5891
15 | 2673455.1191 | 1220460.2577
16 | 2673418.8899 | 1220412.7247
17 | 2673109.728 | 1220310.8125
18 | 2672935.5331 | 1220107.6833
19 | 2672856.0003 | 1220194.0733
20 | 2672833.8177 | 1220060.8404
21 | 2672795.9362 | 1219931.9585
22 | 2672362.9246 | 1219795.2291
23 | 2672437.5643 | 1220094.685
24 | 2672921.7998 | 1219966.342
25 | 2672597.3462 | 1220348.0269
26 | 2676637.8453 | 1219828.7459
27 | 2676659.8658 | 1219825.9162
28 | 2676614.3565 | 1219848.3789
29 | 2677634.202 | 1219840.4746
30 | 2676115.6899 | 1219783.79
31 | 2677627.2786 | 1219884.9136
32 | 2676266.2627 | 1219953.8487
33 | 2676003.6761 | 1220696.1233
34 | 2676296.464 | 1219942.6392
35 | 2676108.6269 | 1219768.7899
36 | 2676132.274 | 1220609.7139
37 | 2676142.0786 | 1219611.4368
38 | 2677764.3855 | 1220740.8646
39 | 2675890.3365 | 1219382.6316
40 | 2675847.3665 | 1219336.1875
41 | 2672231.9415 | 1222111.3953
42 | 2672204.0342 | 1222137.0514
43 | 2672587.7793 | 1220616.1728
44 | 2672318.2072 | 1222554.3859
45 | 2672505.7305 | 1220518.2103
46 | 2674810.7423 | 1221368.8743
47 | 2674877.5027 | 1221416.0105
48 | 2672389.1912 | 1222525.3738
49 | 2674932.8963 | 1222012.253
50 | 2674969.3738 | 1221893.7789
51 | 2675009.5745 | 1222224.6019
52 | 2674964.7784 | 1222004.4825
53 | 2674968.7384 | 1221503.9156
54 | 2675119.7392 | 1221240.4566
55 | 2674979.4546 | 1221516.8256
56 | 2675139.7707 | 1221167.5282
57 | 2675267.1086 | 1221436.8787
58 | 2675271.1178 | 1221425.1995
59 | 2675213.1304 | 1221502.362
60 | 2675279.2892 | 1221466.4206
61 | 2675117.9772 | 1221524.3869
62 | 2675208.8938 | 1221516.44
63 | 2675081.6053 | 1221563.2007
64 | 2675140.808 | 1221018.0213
65 | 2675240.9529 | 1221038.71
66 | 2675329.6373 | 1221154.4064
67 | 2675146.0612 | 1221163.8385
68 | 2675403.2163 | 1221127.3085
69 | 2675303.2103 | 1221488.6356
70 | 2675055.9522 | 1221598.309
71 | 2675776.0439 | 1221949.6566
72 | 2675843.1838 | 1221972.4595
73 | 2675856.0039 | 1222264.1145
74 | 2676998.2192 | 1221815.6757
75 | 2675937.9158 | 1222315.4922
76 | 2675676.1078 | 1222366.2916
77 | 2676998.6058 | 1221719.5173
78 | 2677106.9059 | 1221520.9874
79 | 2675528.326 | 1222081.9861
80 | 2675582.924 | 1222220.2584
81 | 2675483.3859 | 1222106.2954
82 | 2675645.5834 | 1222314.8939
83 | 2675548.7939 | 1222237.9917
84 | 2675613.3926 | 1222269.8002
85 | 2675471.8582 | 1222084.9844
86 | 2675613.1239 | 1221570.9599
87 | 2675663.9607 | 1221567.9034
88 | 2675391.185 | 1221549.5216
89 | 2675569.823 | 1221419.6334
90 | 2675387.9199 | 1221543.7654
91 | 2675531.2649 | 1221419.3108
92 | 2675436.8896 | 1221405.4836
93 | 2675386.931 | 1221539.7836
94 | 2674982.8118 | 1221862.194
95 | 2675010.8155 | 1222225.5683
96 | 2675017.2527 | 1222214.8366
97 | 2674971.613 | 1221847.8992
98 | 2675173.2188 | 1222062.7811
99 | 2675170.9822 | 1222058.4834
100 | 2675191.438 | 1222097.734
101 | 2675211.1365 | 1222049.8179
102 | 2675446.8903 | 1221937.448
103 | 2675246.6283 | 1221773.3071
104 | 2675229.8224 | 1222168.4651
105 | 2675217.9892 | 1222062.2015
106 | 2675243.4475 | 1222048.8114
107 | 2675465.1989 | 1221924.5715
108 | 2675220.1956 | 1221756.729
109 | 2675400.9524 | 1222304.3739
110 | 2675258.5958 | 1222224.7433
111 | 2675268.2515 | 1222079.6256
112 | 2675266.946 | 1222091.0833
113 | 2675426.4703 | 1222350.405
114 | 2675366.9671 | 1222323.0916
115 | 2675240.5808 | 1221711.6013
116 | 2675293.1472 | 1222206.5848
117 | 2675391.5603 | 1222369.637
118 | 2675323.833 | 1222346.8482
119 | 2677140.0121 | 1221499.98
120 | 2675054.0388 | 1221606.8682
121 | 2674994.5543 | 1221588.5397
122 | 2675516.8742 | 1222254.5765
123 | 2675643.5535 | 1222315.8577
124 | 2675444.1131 | 1222499.4197
125 | 2675496.1918 | 1222469.0219
126 | 2675391.7604 | 1222529.4165
127 | 2675499.9632 | 1222467.1018
128 | 2675511.4204 | 1222498.501
129 | 2675385.5374 | 1222517.6967
130 | 2675556.9167 | 1222574.8138
131 | 2675373.0355 | 1222469.9071
132 | 2675462.8464 | 1222525.0722
133 | 2675347.4144 | 1222444.6218
134 | 2675332.2805 | 1222452.5245
135 | 2675349.3512 | 1222392.8901
136 | 2675381.1187 | 1222485.086
137 | 2675258.4966 | 1222444.353
138 | 2675439.2353 | 1222302.0127
139 | 2675331.6446 | 1222499.7697
140 | 2675470.9631 | 1222284.933
141 | 2675220.8564 | 1222464.3953
142 | 2675390.9858 | 1222369.9535
143 | 2675418.2742 | 1222549.4543
144 | 2675478.9826 | 1222280.4799
145 | 2675448.0457 | 1222605.6906
146 | 2675403.6947 | 1222629.6994
147 | 2675455.0337 | 1222601.8185
148 | 2675371.197 | 1222646.8335
149 | 2675460.7082 | 1222810.0299
150 | 2675281.2008 | 1222724.935
151 | 2675462.6608 | 1222813.7192
152 | 2675215.282 | 1222698.9855
153 | 2675124.0335 | 1221595.7322
154 | 2675132.6935 | 1221617.0424
155 | 2675458.9639 | 1222243.878
156 | 2675068.6255 | 1222368.3429
157 | 2675078.6901 | 1222360.751
158 | 2675108.9125 | 1222328.0883
159 | 2675108.9447 | 1222321.9291
160 | 2675129.0692 | 1222363.6718
161 | 2675078.5774 | 1222289.7623
162 | 2674971.613 | 1221847.8992

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99222 | -0.19331 | 0.19609 | 0.094971
1 | 0.99224 | -0.19345 | 0 | 0
2 | 0.99232 | -0.19414 | 0 | 0
3 | 0.99246 | -0.19311 | 0.1644 | 0.079621
4 | 0.9925 | -0.19349 | 0.16855 | 0.081631
5 | 0.99451 | -0.096275 | 0.38339 | 0.18568
6 | 0.99316 | -0.18004 | 0 | 0
7 | 0.99453 | -0.096146 | 0 | 0
8 | 0.99231 | -0.19402 | 0.26043 | 0.12613
9 | 0.99289 | -0.18581 | 0 | 0
10 | 0.99291 | -0.18464 | 0.1191 | 0.057684
11 | 0.99274 | -0.19476 | 0 | 0
12 | 0.99261 | -0.19444 | 0.35396 | 0.17143
13 | 0.9926 | -0.19433 | 0 | 0
14 | 0.99269 | -0.1951 | 0 | 0
15 | 0.99315 | -0.18011 | 0.20892 | 0.10118
16 | 0.99309 | -0.18341 | 0 | 0
17 | 0.99294 | -0.18446 | 0 | 0
18 | 0.99274 | -0.19472 | 0.084867 | 0.041103
19 | 0.99198 | -0.2024 | 0.26835 | 0.12997
20 | 0.99203 | -0.20283 | 0.12058 | 0.058398
21 | 0.99209 | -0.20343 | 0 | 0
22 | 0.99176 | -0.2082 | 0 | 0
23 | 0.99158 | -0.21058 | 0.1489 | 0.072113
24 | 0.99255 | -0.19391 | 0 | 0
25 | 0.99143 | -0.21252 | 0 | 0
26 | 0.98355 | -0.19712 | 0.086396 | 0.041844
27 | 0.98358 | -0.19733 | 0 | 0
28 | 0.98351 | -0.19692 | 0 | 0
29 | 0.98525 | -0.20635 | 0 | 0
30 | 0.9828 | -0.19234 | 0 | 0
31 | 0.98531 | -0.20659 | 0.083643 | 0.04051
32 | 0.98268 | -0.19184 | 0 | 0
33 | 0.98259 | -0.19214 | 0 | 0
34 | 0.98267 | -0.19194 | 0.24031 | 0.11639
35 | 0.98279 | -0.19223 | 0.34859 | 0.16883
36 | 0.98258 | -0.19202 | 0.067859 | 0.032866
37 | 0.98272 | -0.19278 | 0 | 0
38 | 0.98699 | -0.18806 | 0.29515 | 0.14295
39 | 0.98263 | -0.19201 | 0 | 0
40 | 0.98261 | -0.19185 | 0.20266 | 0.098153
41 | 0.98994 | -0.24724 | 0.27352 | 0.13247
42 | 0.98992 | -0.24711 | 0 | 0
43 | 0.99111 | -0.21649 | 0 | 0
44 | 0.98957 | -0.24421 | 0 | 0
45 | 0.99105 | -0.21598 | 0.27044 | 0.13098
46 | 0.99433 | -0.091409 | 0.40686 | 0.19705
47 | 0.99439 | -0.091003 | 0 | 0
48 | 0.98953 | -0.24385 | 0.37295 | 0.18063
49 | 0.99972 | 0.0022668 | 0 | 0
50 | 0.99995 | 0.00040643 | 0 | 0
51 | 0.99947 | 0.0045048 | 0 | 0
52 | 0.99971 | 0.0023646 | 0.20449 | 0.09904
53 | 0.99431 | -0.090263 | 0 | 0
54 | 0.99478 | -0.094381 | 0 | 0
55 | 0.9943 | -0.090208 | 0.26962 | 0.13058
56 | 0.99488 | -0.088339 | 0.2287 | 0.11076
57 | 0.99674 | -0.019009 | 0 | 0
58 | 0.99674 | -0.018995 | 0.099894 | 0.048381
59 | 0.99715 | -0.016631 | 0 | 0
60 | 0.99659 | -0.019885 | 0.087382 | 0.042321
61 | 0.99825 | -0.010289 | 0 | 0
62 | 0.99715 | -0.016568 | 0.35401 | 0.17146
63 | 0.99842 | -0.0093285 | 0.079331 | 0.038422
64 | 0.99493 | -0.087165 | 0.18552 | 0.08985
65 | 0.99497 | -0.086933 | 0 | 0
66 | 0.99502 | -0.08738 | 0 | 0
67 | 0.99489 | -0.088305 | 0 | 0
68 | 0.99513 | -0.080481 | 0.24645 | 0.11936
69 | 0.99643 | -0.020785 | 0 | 0
70 | 0.99855 | -0.0085432 | 0 | 0
71 | 0.9914 | -0.067018 | 0.36498 | 0.17677
72 | 0.99145 | -0.066699 | 0 | 0
73 | 0.99188 | -0.061035 | 0 | 0
74 | 0.98904 | -0.1346 | 0.24988 | 0.12102
75 | 0.99185 | -0.060724 | 0.27144 | 0.13147
76 | 0.99246 | -0.045014 | 0.2841 | 0.13759
77 | 0.98887 | -0.13951 | 0 | 0
78 | 0.98851 | -0.14457 | 0 | 0
79 | 0.99263 | -0.040874 | 0 | 0
80 | 0.99272 | -0.041726 | 0 | 0
81 | 0.9926 | -0.040575 | 0.34306 | 0.16615
82 | 0.99255 | -0.043908 | 0 | 0
83 | 0.99279 | -0.040872 | 0.24545 | 0.11888
84 | 0.99263 | -0.042846 | 0.12146 | 0.058827
85 | 0.99259 | -0.040533 | 0.14559 | 0.070514
86 | 0.99592 | -0.044166 | 0.1719 | 0.083254
87 | 0.99588 | -0.044444 | 0 | 0
88 | 0.99629 | -0.021721 | 0 | 0
89 | 0.99573 | -0.045499 | 0 | 0
90 | 0.99629 | -0.021684 | 0.37922 | 0.18367
91 | 0.9957 | -0.045701 | 0.24286 | 0.11762
92 | 0.99555 | -0.05453 | 0 | 0
93 | 0.9963 | -0.02166 | 0 | 0
94 | 0.99998 | 0.00018609 | 0.32408 | 0.15696
95 | 0.99947 | 0.0045084 | 0.19049 | 0.092257
96 | 0.99946 | 0.0044682 | 0.24357 | 0.11797
97 | 1 | 0 | -20.3282 | -8.849
98 | 0.99469 | -0.029686 | 0.38282 | 0.18541
99 | 0.9947 | -0.029638 | 0 | 0
100 | 0.99461 | -0.03006 | 0 | 0
101 | 0.99467 | -0.029801 | 0 | 0
102 | 0.99461 | -0.028964 | 0 | 0
103 | 0.99571 | -0.024504 | 0 | 0
104 | 0.99446 | -0.030821 | 0 | 0
105 | 0.99466 | -0.029763 | 0 | 0
106 | 0.99466 | -0.029686 | 0.10152 | 0.049166
107 | 0.99461 | -0.028917 | 0.17061 | 0.082628
108 | 0.99578 | -0.024175 | 0.37017 | 0.17928
109 | 0.99371 | -0.034464 | 0 | 0
110 | 0.9944 | -0.031214 | 0.31407 | 0.15211
111 | 0.99465 | -0.029747 | 0 | 0
112 | 0.99464 | -0.02973 | 0.12364 | 0.059879
113 | 0.99362 | -0.034897 | 0 | 0
114 | 0.99368 | -0.034192 | 0.10883 | 0.052709
115 | 0.99588 | -0.023624 | 0 | 0
116 | 0.99439 | -0.031126 | 0.18712 | 0.090625
117 | 0.99355 | -0.035225 | 0.11538 | 0.05588
118 | 0.99364 | -0.033908 | 0 | 0
119 | 0.98847 | -0.14501 | 0.22095 | 0.10701
120 | 0.99858 | -0.0083851 | 0 | 0
121 | 0.99857 | -0.0083052 | 0.1102 | 0.05337
122 | 0.99286 | -0.040023 | 0.21649 | 0.10485
123 | 0.99255 | -0.043867 | 0 | 0
124 | 0.99291 | -0.037064 | 0.89177 | 0.43191
125 | 0.99299 | -0.037759 | 0 | 0
126 | 0.99291 | -0.037016 | 0 | 0
127 | 0.993 | -0.037641 | 0 | 0
128 | 0.99282 | -0.036216 | 0 | 0
129 | 0.99291 | -0.037005 | 0.070874 | 0.034326
130 | 0.99298 | -0.03747 | 0.12267 | 0.059411
131 | 0.99322 | -0.036783 | 0 | 0
132 | 0.99254 | -0.033634 | 1.2043 | 0.58326
133 | 0.99335 | -0.036184 | 0 | 0
134 | 0.99334 | -0.03613 | 0.26189 | 0.12684
135 | 0.99347 | -0.035612 | 0 | 0
136 | 0.99321 | -0.036753 | 0.14713 | 0.07126
137 | 0.99314 | -0.036055 | 0 | 0
138 | 0.99305 | -0.037705 | 0 | 0
139 | 0.99318 | -0.036387 | 0.58454 | 0.2831
140 | 0.99297 | -0.038649 | 0.1146 | 0.055504
141 | 0.99312 | -0.035861 | 0.37867 | 0.1834
142 | 0.99355 | -0.03523 | 0.11453 | 0.055469
143 | 0.99237 | -0.032003 | 0 | 0
144 | 0.99295 | -0.038883 | 0 | 0
145 | 0.99215 | -0.029956 | 0 | 0
146 | 0.99209 | -0.029411 | 0.3807 | 0.18438
147 | 0.99213 | -0.029784 | 1.77 | 0.85724
148 | 0.99207 | -0.029182 | 0 | 0
149 | 0.99203 | -0.028846 | 0 | 0
150 | 0.99198 | -0.029738 | 0.084724 | 0.041034
151 | 0.99203 | -0.028837 | 0.16096 | 0.077957
152 | 0.99194 | -0.029995 | 0.29429 | 0.14253
153 | 0.99586 | -0.023439 | 0 | 0
154 | 0.99585 | -0.023414 | 0.075934 | 0.036777
155 | 0.99295 | -0.038831 | 0.10611 | 0.051393
156 | 0.99343 | -0.031988 | 0.14013 | 0.067869
157 | 0.99343 | -0.03201 | 0 | 0
158 | 0.99344 | -0.032085 | 0 | 0
159 | 0.99344 | -0.032105 | 0 | 0
160 | 0.99343 | -0.032019 | 0.13663 | 0.066173
161 | 0.99342 | -0.031968 | 0.25783 | 0.12487
162 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.19609 | -0.094971 | 0.19609 | 0.093648 | 3.0131e-06 | -0.0013229 | 0.0063389 | 0.0063222 | 0.0063389 | 0.99222 | -0.19331 | 0.99224 | -0.19345 | 2.8813
1 | -0.19609 | -0.093648 | 0.19611 | 0.085707 | 1.7759e-05 | -0.0079411 | 0.0063222 | 0.0062261 | 0.0063222 | 0.99224 | -0.19345 | 0.99232 | -0.19414 | 2.8737
2 | 0.26044 | 0.12524 | -0.26043 | -0.12613 | 3.617e-06 | -0.000899 | 0.0084068 | 0.0084182 | 0.0084182 | 0.99232 | -0.19414 | 0.99231 | -0.19402 | 3.8265
3 | -0.45655 | -0.21094 | 0.45661 | 0.21079 | 6.016e-05 | -0.0001478 | 0.014631 | 0.014628 | 0.014631 | 0.99232 | -0.19414 | 0.99246 | -0.19311 | 6.967
4 | -0.62101 | -0.29042 | 0.62104 | 0.28911 | 2.9688e-05 | -0.0013076 | 0.019941 | 0.019925 | 0.019941 | 0.99246 | -0.19311 | 0.9925 | -0.19349 | 9.064
5 | -0.78958 | -0.37074 | 0.78962 | 0.36964 | 4.0482e-05 | -0.0010966 | 0.025371 | 0.025357 | 0.025371 | 0.9925 | -0.19349 | 0.99255 | -0.19391 | 11.5323
6 | 3.0171 | 1.2556 | -3.0149 | -1.2534 | 0.0022753 | 0.0022521 | 0.094859 | 0.094902 | 0.094902 | 0.99451 | -0.096275 | 0.99316 | -0.18004 | 7.3568
7 | -3.4005 | -1.4413 | 3.4006 | 1.4368 | 6.4495e-05 | -0.0044801 | 0.10721 | 0.10716 | 0.10721 | 0.99451 | -0.096275 | 0.99453 | -0.096146 | 8.4018
8 | 3.0149 | 1.2534 | -3.0148 | -1.256 | 2.9265e-05 | -0.0025895 | 0.094902 | 0.094931 | 0.094931 | 0.99316 | -0.18004 | 0.99315 | -0.18011 | 7.4398
9 | -3.4006 | -1.4368 | 3.4014 | 1.3793 | 0.00082332 | -0.057586 | 0.10716 | 0.10651 | 0.10716 | 0.99453 | -0.096146 | 0.99478 | -0.094381 | 8.3978
10 | -2.6862 | -1.1477 | 2.6862 | 1.1477 | 2.8715e-05 | 1.6431e-05 | 0.084929 | 0.084929 | 0.084929 | 0.99289 | -0.18581 | 0.99291 | -0.18464 | 6.5837
11 | 2.6862 | 1.1477 | -2.686 | -1.1476 | 0.00021947 | 0.0001257 | 0.084929 | 0.084935 | 0.084935 | 0.99289 | -0.18581 | 0.99274 | -0.19476 | 6.5841
12 | -2.8053 | -1.2054 | 2.8054 | 1.1975 | 7.8469e-05 | -0.0079488 | 0.088772 | 0.08868 | 0.088772 | 0.99291 | -0.18464 | 0.99294 | -0.18446 | 6.957
13 | 0.084868 | 0.040105 | -0.084867 | -0.041103 | 4.2404e-07 | -0.00099851 | 0.0027295 | 0.002742 | 0.002742 | 0.99274 | -0.19476 | 0.99274 | -0.19472 | 1.2464
14 | 2.6011 | 1.1075 | -2.601 | -1.1234 | 0.00013492 | -0.015891 | 0.082207 | 0.08239 | 0.08239 | 0.99274 | -0.19476 | 0.99269 | -0.1951 | 6.4569
15 | 0.78968 | 0.36822 | -0.78967 | -0.36853 | 1.1335e-05 | -0.00030765 | 0.02534 | 0.025343 | 0.025343 | 0.99261 | -0.19444 | 0.9926 | -0.19433 | 11.5198
16 | -1.1436 | -0.53965 | 1.1437 | 0.53848 | 9.1804e-05 | -0.0011694 | 0.036777 | 0.036762 | 0.036777 | 0.99261 | -0.19444 | 0.99269 | -0.1951 | 16.7167
17 | 0.78967 | 0.36853 | -0.78962 | -0.36964 | 4.1191e-05 | -0.0011172 | 0.025343 | 0.025357 | 0.025357 | 0.9926 | -0.19433 | 0.99255 | -0.19391 | 11.5261
18 | 1.4572 | 0.5849 | -1.4565 | -0.6104 | 0.0007821 | -0.025506 | 0.045663 | 0.045951 | 0.045951 | 0.99269 | -0.1951 | 0.99209 | -0.20343 | 12.6936
19 | 2.8059 | 1.1548 | -2.8058 | -1.1547 | 8.2984e-05 | 6.0188e-05 | 0.088196 | 0.088198 | 0.088198 | 0.99315 | -0.18011 | 0.99309 | -0.18341 | 6.837
20 | 2.8058 | 1.1547 | -2.8054 | -1.1975 | 0.00041902 | -0.042733 | 0.088198 | 0.08868 | 0.08868 | 0.99309 | -0.18341 | 0.99294 | -0.18446 | 6.9499
21 | -0.26835 | -0.12997 | 0.26836 | 0.1268 | 1.3513e-05 | -0.0031695 | 0.0086768 | 0.0086369 | 0.0086768 | 0.99198 | -0.2024 | 0.99203 | -0.20283 | 3.944
22 | -0.38894 | -0.18519 | 0.38896 | 0.182 | 2.8516e-05 | -0.0031961 | 0.012535 | 0.012496 | 0.012535 | 0.99203 | -0.20283 | 0.99209 | -0.20343 | 5.6979
23 | 1.0675 | 0.42841 | -1.0672 | -0.44852 | 0.00032846 | -0.020117 | 0.033469 | 0.033695 | 0.033695 | 0.99209 | -0.20343 | 0.99176 | -0.2082 | 9.3079
24 | 1.0672 | 0.44852 | -1.067 | -0.45907 | 0.00017405 | -0.010543 | 0.033695 | 0.033816 | 0.033816 | 0.99176 | -0.2082 | 0.99158 | -0.21058 | 9.3415
25 | 0.9181 | 0.38695 | -0.91797 | -0.39696 | 0.0001221 | -0.010005 | 0.029005 | 0.029121 | 0.029121 | 0.99158 | -0.21058 | 0.99143 | -0.21252 | 8.0444
26 | 0.91797 | 0.39696 | -0.9177 | -0.4188 | 0.0002702 | -0.021846 | 0.029121 | 0.029381 | 0.029381 | 0.99143 | -0.21252 | 0.99111 | -0.21649 | 8.1164
27 | -0.94659 | -0.39558 | 0.94663 | 0.39495 | 3.3802e-05 | -0.00063514 | 0.030111 | 0.030104 | 0.030111 | 0.98355 | -0.19712 | 0.98358 | -0.19733 | 13.687
28 | 0.8602 | 0.35374 | -0.86017 | -0.35444 | 3.0416e-05 | -0.00069689 | 0.027299 | 0.027307 | 0.027307 | 0.98355 | -0.19712 | 0.98351 | -0.19692 | 12.4121
29 | -0.94663 | -0.39495 | 0.9483 | 0.36308 | 0.0016723 | -0.031871 | 0.030104 | 0.029752 | 0.030104 | 0.98358 | -0.19733 | 0.98525 | -0.20635 | 13.6837
30 | 0.86017 | 0.35444 | -0.85951 | -0.36927 | 0.00065214 | -0.014832 | 0.027307 | 0.027478 | 0.027478 | 0.98351 | -0.19692 | 0.9828 | -0.19234 | 12.4898
31 | -0.9483 | -0.36308 | 0.94835 | 0.36205 | 5.314e-05 | -0.0010269 | 0.029752 | 0.029741 | 0.029752 | 0.98525 | -0.20635 | 0.98531 | -0.20659 | 13.5235
32 | 0.5513 | 0.2567 | -0.55129 | -0.25709 | 7.3808e-06 | -0.00039731 | 0.017862 | 0.017867 | 0.017867 | 0.9828 | -0.19234 | 0.98279 | -0.19223 | 8.1215
33 | 0.30822 | 0.11257 | -0.30818 | -0.11957 | 3.7955e-05 | -0.006994 | 0.0096381 | 0.0097107 | 0.0097107 | 0.9828 | -0.19234 | 0.98268 | -0.19184 | 4.4139
34 | -1.032 | -0.40256 | 1.0336 | 0.40257 | 0.0016262 | 1.2236e-05 | 0.032454 | 0.032444 | 0.032454 | 0.98531 | -0.20659 | 0.98699 | -0.18806 | 15.4544
35 | 0.067866 | 0.0032164 | -0.06786 | -0.029128 | 6.303e-06 | -0.025911 | 0.0019959 | 0.0021696 | 0.0021696 | 0.98268 | -0.19184 | 0.98259 | -0.19214 | 0.98616
36 | 0.24031 | 0.11635 | -0.24031 | -0.11639 | 3.5312e-06 | -3.4925e-05 | 0.0078434 | 0.0078439 | 0.0078439 | 0.98268 | -0.19184 | 0.98267 | -0.19194 | 3.7352
37 | 0.06786 | 0.029128 | -0.067859 | -0.032866 | 1.0401e-06 | -0.003738 | 0.0021696 | 0.0022152 | 0.0022152 | 0.98259 | -0.19214 | 0.98258 | -0.19202 | 1.0069
38 | 0.2027 | 0.088262 | -0.20269 | -0.08844 | 1.2091e-05 | -0.00017791 | 0.0064938 | 0.006496 | 0.006496 | 0.98279 | -0.19223 | 0.98272 | -0.19278 | 3.0933
39 | 0.20269 | 0.08844 | -0.20266 | -0.096683 | 2.0462e-05 | -0.0082427 | 0.006496 | 0.0065966 | 0.0065966 | 0.98272 | -0.19278 | 0.98263 | -0.19201 | 2.9985
40 | -1.3288 | -0.54552 | 1.3304 | 0.54614 | 0.0015921 | 0.00061596 | 0.042012 | 0.041999 | 0.042012 | 0.98699 | -0.18806 | 0.98847 | -0.14501 | 12.0034
41 | 0.20266 | 0.096683 | -0.20266 | -0.098153 | 3.7192e-06 | -0.0014707 | 0.0065966 | 0.0066154 | 0.0066154 | 0.98263 | -0.19201 | 0.98261 | -0.19185 | 3.007
42 | 0.37312 | 0.16035 | -0.37311 | -0.16125 | 7.2161e-06 | -0.00089884 | 0.011843 | 0.011853 | 0.011853 | 0.98994 | -0.24724 | 0.98992 | -0.24711 | 5.3878
43 | -0.64664 | -0.29283 | 0.64724 | 0.29162 | 0.00060391 | -0.0012043 | 0.0207 | 0.020677 | 0.0207 | 0.98994 | -0.24724 | 0.99111 | -0.21649 | 5.9142
44 | 0.37311 | 0.16125 | -0.37297 | -0.17875 | 0.00014312 | -0.017496 | 0.011853 | 0.012065 | 0.012065 | 0.98992 | -0.24711 | 0.98957 | -0.24421 | 5.4842
45 | 0.27046 | 0.12718 | -0.27044 | -0.13098 | 1.6501e-05 | -0.0037997 | 0.0087051 | 0.0087528 | 0.0087528 | 0.99111 | -0.21649 | 0.99105 | -0.21598 | 3.9785
46 | 0.37297 | 0.17875 | -0.37295 | -0.18063 | 1.5706e-05 | -0.0018812 | 0.012065 | 0.012089 | 0.012089 | 0.98957 | -0.24421 | 0.98953 | -0.24385 | 5.495
47 | -0.40686 | -0.19705 | 0.40689 | 0.19697 | 2.5079e-05 | -8.0756e-05 | 0.013125 | 0.013123 | 0.013125 | 0.99433 | -0.091409 | 0.99439 | -0.091003 | 6.2498
48 | 0.26965 | 0.12447 | -0.26963 | -0.13019 | 2.4255e-05 | -0.0057159 | 0.0086218 | 0.0086927 | 0.0086927 | 0.99439 | -0.091003 | 0.99431 | -0.090263 | 3.9512
49 | -0.67654 | -0.32145 | 0.67682 | 0.3108 | 0.000285 | -0.010645 | 0.021744 | 0.021613 | 0.021744 | 0.99439 | -0.091003 | 0.99478 | -0.094381 | 9.8838
50 | -0.63868 | -0.29726 | 0.63883 | 0.29064 | 0.00015365 | -0.0066199 | 0.020342 | 0.020261 | 0.020342 | 0.99972 | 0.0022668 | 0.99995 | 0.00040643 | 9.2462
51 | 0.43418 | 0.19918 | -0.43406 | -0.21017 | 0.00011854 | -0.010991 | 0.013793 | 0.013929 | 0.013929 | 0.99972 | 0.0022668 | 0.99947 | 0.0045048 | 6.3315
52 | 0.2045 | 0.098075 | -0.20449 | -0.09904 | 2.3224e-06 | -0.00096544 | 0.0065489 | 0.006561 | 0.006561 | 0.99972 | 0.0022668 | 0.99971 | 0.0023646 | 2.9823
53 | -0.63883 | -0.29064 | 0.63885 | 0.28982 | 1.8797e-05 | -0.00081367 | 0.020261 | 0.020251 | 0.020261 | 0.99995 | 0.00040643 | 0.99998 | 0.00018609 | 9.2097
54 | 0.19049 | 0.092219 | -0.19049 | -0.092257 | 7.8503e-08 | -3.749e-05 | 0.0061126 | 0.0061131 | 0.0061131 | 0.99947 | 0.0045048 | 0.99947 | 0.0045084 | 2.7787
55 | 0.24357 | 0.11795 | -0.24357 | -0.11797 | 1.3523e-06 | -1.3967e-05 | 0.0078166 | 0.0078168 | 0.0078168 | 0.99947 | 0.0045048 | 0.99946 | 0.0044682 | 3.7223
56 | 0.26963 | 0.13019 | -0.26962 | -0.13058 | 1.6916e-06 | -0.00039509 | 0.0086927 | 0.0086977 | 0.0086977 | 0.99431 | -0.090263 | 0.9943 | -0.090208 | 3.9535
57 | -4.0782 | -1.6901 | 4.0784 | 1.6904 | 0.00022154 | 0.00038881 | 0.12811 | 0.1281 | 0.12811 | 0.99478 | -0.094381 | 0.99488 | -0.088339 | 9.9307
58 | -4.3071 | -1.8012 | 4.3072 | 1.8003 | 2.063e-05 | -0.0008935 | 0.13546 | 0.13545 | 0.13546 | 0.99488 | -0.088339 | 0.99489 | -0.088305 | 10.6164
59 | 0.099894 | 0.048088 | -0.099894 | -0.048381 | 1.7014e-07 | -0.00029283 | 0.0032109 | 0.0032146 | 0.0032146 | 0.99674 | -0.019009 | 0.99674 | -0.018995 | 1.4612
60 | -18.7478 | -8.2297 | 18.7553 | 8.2167 | 0.0074504 | -0.012939 | 0.59298 | 0.59278 | 0.59298 | 0.99674 | -0.019009 | 0.99715 | -0.016631 | 46.4721
61 | 18.6479 | 8.1816 | -18.6452 | -8.1864 | 0.0027369 | -0.0048152 | 0.58977 | 0.58985 | 0.58985 | 0.99674 | -0.019009 | 0.99659 | -0.019885 | 46.2264
62 | -19.1093 | -8.3878 | 19.1294 | 8.3545 | 0.020131 | -0.033355 | 0.60416 | 0.60364 | 0.60416 | 0.99715 | -0.016631 | 0.99825 | -0.010289 | 47.3479
63 | 0.35402 | 0.17111 | -0.35401 | -0.17146 | 2.544e-06 | -0.00034825 | 0.011383 | 0.011388 | 0.011388 | 0.99715 | -0.016631 | 0.99715 | -0.016568 | 5.1761
64 | 18.5578 | 8.1441 | -18.555 | -8.149 | 0.0028004 | -0.0049856 | 0.58704 | 0.58711 | 0.58711 | 0.99659 | -0.019885 | 0.99643 | -0.020785 | 46.0121
65 | -19.1294 | -8.3545 | 19.1324 | 8.3495 | 0.003019 | -0.0050173 | 0.60364 | 0.60356 | 0.60364 | 0.99825 | -0.010289 | 0.99842 | -0.0093285 | 47.3073
66 | -19.2118 | -8.3879 | 19.2142 | 8.3838 | 0.0024756 | -0.0040709 | 0.60611 | 0.60605 | 0.60611 | 0.99842 | -0.0093285 | 0.99855 | -0.0085432 | 47.5008
67 | -0.18552 | -0.08985 | 0.18552 | 0.089733 | 6.5154e-06 | -0.00011677 | 0.0059808 | 0.0059793 | 0.0059808 | 0.99493 | -0.087165 | 0.99497 | -0.086933 | 2.848
68 | -0.18552 | -0.089733 | 0.18553 | 0.084637 | 1.0188e-05 | -0.0050967 | 0.0059793 | 0.0059163 | 0.0059793 | 0.99497 | -0.086933 | 0.99502 | -0.08738 | 2.7178
69 | 4.3077 | 1.7764 | -4.3072 | -1.8003 | 0.00055119 | -0.023926 | 0.13518 | 0.13545 | 0.13545 | 0.99502 | -0.08738 | 0.99489 | -0.088305 | 10.6156
70 | -4.4933 | -1.861 | 4.4935 | 1.8616 | 0.00027864 | 0.00053464 | 0.1411 | 0.1411 | 0.1411 | 0.99502 | -0.08738 | 0.99513 | -0.080481 | 10.9378
71 | -4.74 | -1.9809 | 4.7411 | 1.9831 | 0.0011107 | 0.0022194 | 0.14903 | 0.14902 | 0.14903 | 0.99513 | -0.080481 | 0.99555 | -0.05453 | 11.5524
72 | 13.0167 | 5.8328 | -13.0099 | -5.8612 | 0.0068114 | -0.028329 | 0.41324 | 0.41362 | 0.41362 | 0.99643 | -0.020785 | 0.99588 | -0.023624 | 32.4152
73 | 5.5383 | 2.3162 | -5.5376 | -2.3344 | 0.00069508 | -0.018142 | 0.17392 | 0.17413 | 0.17413 | 0.99643 | -0.020785 | 0.9963 | -0.02166 | 13.6462
74 | -19.2142 | -8.3838 | 19.2147 | 8.383 | 0.00049772 | -0.00081877 | 0.60605 | 0.60603 | 0.60605 | 0.99855 | -0.0085432 | 0.99858 | -0.0083851 | 47.4958
75 | -0.36498 | -0.17677 | 0.365 | 0.1767 | 1.7614e-05 | -7.217e-05 | 0.011808 | 0.011807 | 0.011808 | 0.9914 | -0.067018 | 0.99145 | -0.066699 | 5.623
76 | -2.1705 | -0.93774 | 2.1713 | 0.92574 | 0.00085426 | -0.011996 | 0.068842 | 0.068697 | 0.068842 | 0.99145 | -0.066699 | 0.99188 | -0.061035 | 19.0172
77 | 1.8055 | 0.76104 | -1.802 | -0.7585 | 0.0034835 | 0.002548 | 0.057048 | 0.057064 | 0.057064 | 0.99145 | -0.066699 | 0.98904 | -0.1346 | 16.3041
78 | 0.27145 | 0.1292 | -0.27144 | -0.13147 | 9.8933e-06 | -0.0022635 | 0.0087495 | 0.0087781 | 0.0087781 | 0.99188 | -0.061035 | 0.99185 | -0.060724 | 3.99
79 | -2.4428 | -1.0549 | 2.4439 | 1.056 | 0.0011389 | 0.0010468 | 0.07744 | 0.077437 | 0.07744 | 0.99188 | -0.061035 | 0.99246 | -0.045014 | 22.1258
80 | 1.5521 | 0.63747 | -1.5519 | -0.63735 | 0.00021172 | 0.00012399 | 0.048974 | 0.048975 | 0.048975 | 0.98904 | -0.1346 | 0.98887 | -0.13951 | 13.9928
81 | -2.728 | -1.1936 | 2.7282 | 1.1917 | 0.00021653 | -0.0018628 | 0.086611 | 0.086588 | 0.086611 | 0.99246 | -0.045014 | 0.99255 | -0.043908 | 23.9258
82 | 1.5519 | 0.63735 | -1.5514 | -0.65187 | 0.00051639 | -0.014522 | 0.048975 | 0.049142 | 0.049142 | 0.98887 | -0.13951 | 0.98851 | -0.14457 | 13.5751
83 | 1.5514 | 0.65187 | -1.5513 | -0.65315 | 4.5723e-05 | -0.0012804 | 0.049142 | 0.049157 | 0.049157 | 0.98851 | -0.14457 | 0.98847 | -0.14501 | 13.5792
84 | -0.48867 | -0.2349 | 0.48872 | 0.2314 | 4.941e-05 | -0.0034975 | 0.015768 | 0.015724 | 0.015768 | 0.99263 | -0.040874 | 0.99272 | -0.041726 | 7.1673
85 | 0.48867 | 0.2349 | -0.48865 | -0.23609 | 1.6975e-05 | -0.0011969 | 0.015768 | 0.015783 | 0.015783 | 0.99263 | -0.040874 | 0.9926 | -0.040575 | 7.1742
86 | -3.3388 | -1.4784 | 3.339 | 1.4772 | 0.00020942 | -0.0011483 | 0.10618 | 0.10617 | 0.10618 | 0.99272 | -0.041726 | 0.99279 | -0.040872 | 29.3321
87 | 2.8501 | 1.247 | -2.8499 | -1.2488 | 0.00022996 | -0.0017991 | 0.090464 | 0.090487 | 0.090487 | 0.99272 | -0.041726 | 0.99263 | -0.042846 | 24.9964
88 | 0.14559 | 0.069944 | -0.14559 | -0.070514 | 7.1487e-07 | -0.00056974 | 0.0046976 | 0.0047048 | 0.0047048 | 0.9926 | -0.040575 | 0.99259 | -0.040533 | 2.1385
89 | -2.7282 | -1.1917 | 2.7282 | 1.1917 | 8.1188e-06 | -6.9873e-05 | 0.086588 | 0.086587 | 0.086588 | 0.99255 | -0.043908 | 0.99255 | -0.043867 | 23.9193
90 | -3.5845 | -1.5961 | 3.5847 | 1.595 | 0.00022613 | -0.0010521 | 0.11409 | 0.11408 | 0.11409 | 0.99279 | -0.040872 | 0.99286 | -0.040023 | 31.5173
91 | 2.7284 | 1.1899 | -2.7282 | -1.1917 | 0.00019932 | -0.0017161 | 0.086565 | 0.086587 | 0.086587 | 0.99263 | -0.042846 | 0.99255 | -0.043867 | 23.919
92 | 4.9854 | 2.0666 | -4.9852 | -2.0728 | 0.00019207 | -0.0062209 | 0.15643 | 0.1565 | 0.1565 | 0.99592 | -0.044166 | 0.99588 | -0.044444 | 12.2648
93 | -5.1573 | -2.1498 | 5.1584 | 2.152 | 0.0010439 | 0.0021955 | 0.16196 | 0.16195 | 0.16196 | 0.99592 | -0.044166 | 0.99629 | -0.021721 | 12.5547
94 | 4.9852 | 2.0728 | -4.9845 | -2.0968 | 0.00074404 | -0.02404 | 0.1565 | 0.15677 | 0.15677 | 0.99588 | -0.044444 | 0.99573 | -0.045499 | 12.2863
95 | -5.1584 | -2.152 | 5.1584 | 2.1512 | 2.6799e-05 | -0.00080989 | 0.16195 | 0.16194 | 0.16195 | 0.99629 | -0.021721 | 0.99629 | -0.021684 | 12.6919
96 | 4.9845 | 2.0968 | -4.9843 | -2.1015 | 0.00014605 | -0.004708 | 0.15677 | 0.15683 | 0.15683 | 0.99573 | -0.045499 | 0.9957 | -0.045701 | 12.2905
97 | -5.5376 | -2.3349 | 5.5376 | 2.3344 | 1.9221e-05 | -0.00050096 | 0.17413 | 0.17413 | 0.17413 | 0.99629 | -0.021684 | 0.9963 | -0.02166 | 13.6466
98 | 4.7415 | 1.9839 | -4.7411 | -1.9831 | 0.00037807 | 0.00075527 | 0.14901 | 0.14902 | 0.14902 | 0.9957 | -0.045701 | 0.99555 | -0.05453 | 11.5517
99 | -0.96293 | -0.44678 | 0.96295 | 0.44636 | 2.2738e-05 | -0.00042636 | 0.030644 | 0.030639 | 0.030644 | 0.99998 | 0.00018609 | 1 | 0 | 13.9293
100 | 19.3512 | 8.3921 | -19.3249 | -8.4349 | 0.026289 | -0.042725 | 0.60889 | 0.60955 | 0.60955 | 1 | 0 | 0.99858 | -0.0083851 | 47.7707
101 | -12.3786 | -5.6443 | 12.3787 | 5.6438 | 0.00011662 | -0.00053635 | 0.39483 | 0.39482 | 0.39483 | 0.99469 | -0.029686 | 0.9947 | -0.029638 | 30.9429
102 | 11.7706 | 5.3512 | -11.7697 | -5.3556 | 0.00085721 | -0.0044151 | 0.37525 | 0.37531 | 0.37531 | 0.99469 | -0.029686 | 0.99461 | -0.03006 | 29.4128
103 | 0.22516 | 0.10767 | -0.22516 | -0.10771 | 3.7461e-06 | -4.4984e-05 | 0.0072432 | 0.0072438 | 0.0072438 | 0.99469 | -0.029686 | 0.99467 | -0.029801 | 3.4494
104 | 0.17062 | 0.072903 | -0.17061 | -0.082089 | 1.5363e-05 | -0.0091859 | 0.0053848 | 0.005495 | 0.005495 | 0.9947 | -0.029638 | 0.99461 | -0.028964 | 2.4977
105 | -12.5493 | -5.7167 | 12.5616 | 5.6615 | 0.012329 | -0.055186 | 0.40021 | 0.39946 | 0.40021 | 0.9947 | -0.029638 | 0.99571 | -0.024504 | 31.3642
106 | 11.7697 | 5.3556 | -11.768 | -5.3647 | 0.0017529 | -0.0090216 | 0.37531 | 0.37543 | 0.37543 | 0.99461 | -0.03006 | 0.99446 | -0.030821 | 29.4222
107 | 0.22516 | 0.10771 | -0.22515 | -0.10805 | 9.9144e-07 | -0.00033384 | 0.0072438 | 0.007248 | 0.007248 | 0.99467 | -0.029801 | 0.99466 | -0.029763 | 3.2945
108 | 0.17061 | 0.082089 | -0.17061 | -0.082628 | 9.2175e-07 | -0.00053915 | 0.005495 | 0.0055018 | 0.0055018 | 0.99461 | -0.028964 | 0.99461 | -0.028917 | 2.5008
109 | -12.5616 | -5.6615 | 12.5624 | 5.658 | 0.00077115 | -0.0034635 | 0.39946 | 0.39942 | 0.39946 | 0.99571 | -0.024504 | 0.99578 | -0.024175 | 31.3059
110 | 11.2668 | 5.1229 | -11.2586 | -5.169 | 0.0081486 | -0.046065 | 0.35928 | 0.35989 | 0.35989 | 0.99446 | -0.030821 | 0.99371 | -0.034464 | 28.2045
111 | 0.50121 | 0.24176 | -0.50118 | -0.24181 | 2.9387e-05 | -5.6211e-05 | 0.016154 | 0.016154 | 0.016154 | 0.99446 | -0.030821 | 0.9944 | -0.031214 | 7.6926
112 | 0.22515 | 0.10805 | -0.22515 | -0.10873 | 2.0197e-06 | -0.00067888 | 0.007248 | 0.0072565 | 0.0072565 | 0.99466 | -0.029763 | 0.99466 | -0.029686 | 3.2984
113 | 0.12364 | 0.059561 | -0.12364 | -0.059607 | 1.1182e-06 | -4.6019e-05 | 0.0039829 | 0.0039835 | 0.0039835 | 0.99466 | -0.029686 | 0.99465 | -0.029747 | 1.8969
114 | -12.9326 | -5.8373 | 12.9339 | 5.8317 | 0.0013352 | -0.0056143 | 0.41134 | 0.41126 | 0.41134 | 0.99578 | -0.024175 | 0.99588 | -0.023624 | 32.2364
115 | 10.615 | 4.87 | -10.6141 | -4.876 | 0.00093566 | -0.0059995 | 0.33927 | 0.33935 | 0.33935 | 0.99371 | -0.034464 | 0.99362 | -0.034897 | 26.5951
116 | 0.64359 | 0.29901 | -0.64357 | -0.29992 | 2.2026e-05 | -0.00090818 | 0.020616 | 0.020627 | 0.020627 | 0.99371 | -0.034464 | 0.99368 | -0.034192 | 9.3759
117 | 0.18712 | 0.089704 | -0.18712 | -0.090625 | 1.8946e-06 | -0.00092095 | 0.006024 | 0.0060356 | 0.0060356 | 0.9944 | -0.031214 | 0.99439 | -0.031126 | 2.7435
118 | 0.12364 | 0.059607 | -0.12364 | -0.059879 | 2.4455e-07 | -0.00027237 | 0.0039835 | 0.003987 | 0.003987 | 0.99465 | -0.029747 | 0.99464 | -0.02973 | 1.8123
119 | 10.6141 | 4.876 | -10.6134 | -4.8805 | 0.00070927 | -0.0045451 | 0.33935 | 0.33941 | 0.33941 | 0.99362 | -0.034897 | 0.99355 | -0.035225 | 26.5998
120 | 0.53473 | 0.24721 | -0.53472 | -0.24836 | 1.9271e-05 | -0.0011552 | 0.017114 | 0.017129 | 0.017129 | 0.99368 | -0.034192 | 0.99364 | -0.033908 | 7.7857
121 | 0.075937 | 0.029478 | -0.075935 | -0.036118 | 2.1524e-06 | -0.0066403 | 0.0023612 | 0.0024375 | 0.0024375 | 0.99588 | -0.023624 | 0.99586 | -0.023439 | 1.1079
122 | 10.498 | 4.8246 | -10.498 | -4.8247 | 1.1417e-05 | -7.4932e-05 | 0.33569 | 0.33569 | 0.33569 | 0.99355 | -0.035225 | 0.99355 | -0.03523 | 26.308
123 | 0.53472 | 0.24836 | -0.5346 | -0.25538 | 0.00011786 | -0.0070211 | 0.017129 | 0.017216 | 0.017216 | 0.99364 | -0.033908 | 0.99344 | -0.032105 | 7.8254
124 | 0.1102 | 0.051878 | -0.1102 | -0.05337 | 1.0429e-06 | -0.0014921 | 0.003521 | 0.0035396 | 0.0035396 | 0.99858 | -0.0083851 | 0.99857 | -0.0083052 | 1.6089
125 | -3.8012 | -1.6999 | 3.8015 | 1.6986 | 0.00032428 | -0.0013138 | 0.12107 | 0.12105 | 0.12107 | 0.99286 | -0.040023 | 0.99295 | -0.038883 | 33.4443
126 | -0.96265 | -0.4645 | 0.96272 | 0.4631 | 7.7694e-05 | -0.0013965 | 0.031075 | 0.031057 | 0.031075 | 0.99291 | -0.037064 | 0.99299 | -0.037759 | 14.1252
127 | 0.070875 | 0.032594 | -0.070874 | -0.034014 | 4.1754e-07 | -0.0014202 | 0.002268 | 0.0022856 | 0.0022856 | 0.99291 | -0.037064 | 0.99291 | -0.037016 | 1.0389
128 | -4.8608 | -2.3388 | 4.8609 | 2.3387 | 5.0159e-05 | -0.0001064 | 0.15682 | 0.15682 | 0.15682 | 0.99299 | -0.037759 | 0.993 | -0.037641 | 43.3198
129 | 3.8981 | 1.8757 | -3.8974 | -1.8762 | 0.00070025 | -0.00057289 | 0.12576 | 0.12577 | 0.12577 | 0.99299 | -0.037759 | 0.99282 | -0.036216 | 57.1682
130 | 0.070874 | 0.034014 | -0.070874 | -0.034326 | 9.2653e-08 | -0.00031216 | 0.0022856 | 0.0022895 | 0.0022895 | 0.99291 | -0.037016 | 0.99291 | -0.037005 | 1.0407
131 | 0.12267 | 0.05652 | -0.12267 | -0.059411 | 2.5513e-06 | -0.0028912 | 0.0039265 | 0.0039624 | 0.0039624 | 0.993 | -0.037641 | 0.99298 | -0.03747 | 1.8011
132 | -4.9836 | -2.3952 | 4.9846 | 2.3625 | 0.0010677 | -0.032635 | 0.16074 | 0.16033 | 0.16074 | 0.993 | -0.037641 | 0.99322 | -0.036783 | 12.5973
133 | 3.8974 | 1.8762 | -3.8963 | -1.8772 | 0.0011693 | -0.00095581 | 0.12577 | 0.12579 | 0.12579 | 0.99282 | -0.036216 | 0.99254 | -0.033634 | 57.1757
134 | 0.14713 | 0.070855 | -0.14713 | -0.07126 | 5.1749e-07 | -0.00040468 | 0.0047464 | 0.0047515 | 0.0047515 | 0.99322 | -0.036783 | 0.99321 | -0.036753 | 2.1598
135 | 0.37872 | 0.17851 | -0.37868 | -0.1824 | 3.2822e-05 | -0.003885 | 0.012169 | 0.012217 | 0.012217 | 0.99322 | -0.036783 | 0.99314 | -0.036055 | 5.5534
136 | 4.0232 | 1.7716 | -4.0226 | -1.8032 | 0.00065276 | -0.031615 | 0.12777 | 0.12815 | 0.12815 | 0.99322 | -0.036783 | 0.99305 | -0.037705 | 10.0428
137 | 0.58456 | 0.28179 | -0.58454 | -0.2831 | 2.6723e-05 | -0.0013162 | 0.018861 | 0.018878 | 0.018878 | 0.99322 | -0.036783 | 0.99318 | -0.036387 | 8.5809
138 | -10.1183 | -4.6653 | 10.1196 | 4.6564 | 0.0012504 | -0.0088671 | 0.32384 | 0.32372 | 0.32384 | 0.99322 | -0.036783 | 0.99335 | -0.036184 | 25.3793
139 | 2.692 | 1.2939 | -2.6915 | -1.295 | 0.00051191 | -0.001043 | 0.086869 | 0.086884 | 0.086884 | 0.99254 | -0.033634 | 0.99237 | -0.032003 | 39.4928
140 | 0.26189 | 0.12644 | -0.26189 | -0.12684 | 1.6253e-06 | -0.00040085 | 0.0084515 | 0.0084565 | 0.0084565 | 0.99335 | -0.036184 | 0.99334 | -0.03613 | 3.8439
141 | -10.3814 | -4.7829 | 10.3827 | 4.7747 | 0.0012228 | -0.0082098 | 0.33217 | 0.33206 | 0.33217 | 0.99335 | -0.036184 | 0.99347 | -0.035612 | 26.0324
142 | -10.3827 | -4.7747 | 10.3835 | 4.7692 | 0.00080964 | -0.0054401 | 0.33206 | 0.33199 | 0.33206 | 0.99347 | -0.035612 | 0.99355 | -0.03523 | 26.0239
143 | 0.37868 | 0.1824 | -0.37867 | -0.1834 | 8.5065e-06 | -0.0010017 | 0.012217 | 0.01223 | 0.01223 | 0.99314 | -0.036055 | 0.99312 | -0.035861 | 5.5592
144 | 4.0226 | 1.8032 | -4.0223 | -1.8042 | 0.00028595 | -0.0010116 | 0.12815 | 0.12816 | 0.12816 | 0.99305 | -0.037705 | 0.99297 | -0.038649 | 35.4036
145 | 3.9077 | 1.7487 | -3.9076 | -1.749 | 6.8633e-05 | -0.0002604 | 0.12446 | 0.12446 | 0.12446 | 0.99297 | -0.038649 | 0.99295 | -0.038883 | 34.3825
146 | 2.6915 | 1.295 | -2.6908 | -1.2963 | 0.00064105 | -0.0013049 | 0.086884 | 0.086903 | 0.086903 | 0.99237 | -0.032003 | 0.99215 | -0.029956 | 39.5013
147 | 0.10611 | 0.050411 | -0.10611 | -0.051393 | 6.5203e-07 | -0.00098189 | 0.0034154 | 0.0034278 | 0.0034278 | 0.99295 | -0.038883 | 0.99295 | -0.038831 | 1.5581
148 | 0.9208 | 0.43921 | -0.92074 | -0.44038 | 5.9352e-05 | -0.0011676 | 0.029683 | 0.029698 | 0.029698 | 0.99215 | -0.029956 | 0.99209 | -0.029411 | 13.4992
149 | 1.77 | 0.85706 | -1.77 | -0.85724 | 3.4921e-05 | -0.0001774 | 0.05722 | 0.057222 | 0.057222 | 0.99215 | -0.029956 | 0.99213 | -0.029784 | 26.0102
150 | 0.54004 | 0.256 | -0.54002 | -0.25685 | 1.4841e-05 | -0.00085892 | 0.01739 | 0.017401 | 0.017401 | 0.99209 | -0.029411 | 0.99207 | -0.029182 | 7.9094
151 | 0.16097 | 0.073487 | -0.16096 | -0.077859 | 6.6577e-06 | -0.0043726 | 0.0051489 | 0.0052031 | 0.0052031 | 0.99207 | -0.029182 | 0.99203 | -0.028846 | 2.365
152 | 0.37906 | 0.18337 | -0.37902 | -0.18349 | 3.1878e-05 | -0.00012003 | 0.012253 | 0.012255 | 0.012255 | 0.99207 | -0.029182 | 0.99198 | -0.029738 | 5.8355
153 | 0.16096 | 0.077859 | -0.16096 | -0.077957 | 1.5092e-07 | -9.8034e-05 | 0.0052031 | 0.0052043 | 0.0052043 | 0.99203 | -0.028846 | 0.99203 | -0.028837 | 2.3656
154 | 0.2943 | 0.14245 | -0.29429 | -0.14253 | 1.1429e-05 | -7.6059e-05 | 0.009515 | 0.009516 | 0.009516 | 0.99198 | -0.029738 | 0.99194 | -0.029995 | 4.5315
155 | 0.075935 | 0.036118 | -0.075934 | -0.036777 | 2.214e-07 | -0.00065866 | 0.0024375 | 0.0024457 | 0.0024457 | 0.99586 | -0.023439 | 0.99585 | -0.023414 | 1.1117
156 | -0.14013 | -0.067869 | 0.14013 | 0.067572 | 3.4425e-07 | -0.00029696 | 0.0045245 | 0.0045207 | 0.0045245 | 0.99343 | -0.031988 | 0.99343 | -0.03201 | 2.0566
157 | -0.14013 | -0.067572 | 0.14013 | 0.066493 | 1.2468e-06 | -0.0010797 | 0.0045207 | 0.0045072 | 0.0045207 | 0.99343 | -0.03201 | 0.99344 | -0.032085 | 2.0549
158 | -0.27676 | -0.1317 | 0.27677 | 0.13156 | 6.522e-07 | -0.00014496 | 0.0089064 | 0.0089046 | 0.0089064 | 0.99344 | -0.032085 | 0.99344 | -0.032105 | 4.0484
159 | 0.13663 | 0.065209 | -0.13663 | -0.066173 | 1.0595e-06 | -0.00096334 | 0.0043992 | 0.0044114 | 0.0044114 | 0.99344 | -0.032085 | 0.99343 | -0.032019 | 2.0052
160 | 0.25783 | 0.12383 | -0.25783 | -0.12487 | 4.0984e-06 | -0.0010443 | 0.0083114 | 0.0083246 | 0.0083246 | 0.99344 | -0.032105 | 0.99342 | -0.031968 | 3.7839

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 20.3282 | 8.849

## res_load
| p_mw | q_mvar
0 | 0.19609 | 0.094971
1 | 0.1644 | 0.079621
2 | 0.16855 | 0.081631
3 | 0.38339 | 0.18568
4 | 0.26043 | 0.12613
5 | 0.1191 | 0.057684
6 | 0.35396 | 0.17143
7 | 0.20892 | 0.10118
8 | 0.084867 | 0.041103
9 | 0.26835 | 0.12997
10 | 0.12058 | 0.058398
11 | 0.1489 | 0.072113
12 | 0.086396 | 0.041844
13 | 0.083643 | 0.04051
14 | 0.24031 | 0.11639
15 | 0.34859 | 0.16883
16 | 0.067859 | 0.032866
17 | 0.29515 | 0.14295
18 | 0.20266 | 0.098153
19 | 0.27352 | 0.13247
20 | 0.27044 | 0.13098
21 | 0.40686 | 0.19705
22 | 0.37295 | 0.18063
23 | 0.20449 | 0.09904
24 | 0.26962 | 0.13058
25 | 0.2287 | 0.11076
26 | 0.099894 | 0.048381
27 | 0.087382 | 0.042321
28 | 0.35401 | 0.17146
29 | 0.079331 | 0.038422
30 | 0.18552 | 0.08985
31 | 0.24645 | 0.11936
32 | 0.36498 | 0.17677
33 | 0.24988 | 0.12102
34 | 0.27144 | 0.13147
35 | 0.2841 | 0.13759
36 | 0.34306 | 0.16615
37 | 0.24545 | 0.11888
38 | 0.12146 | 0.058827
39 | 0.14559 | 0.070514
40 | 0.1719 | 0.083254
41 | 0.37922 | 0.18367
42 | 0.24286 | 0.11762
43 | 0.32408 | 0.15696
44 | 0.19049 | 0.092257
45 | 0.24357 | 0.11797
46 | 0.38282 | 0.18541
47 | 0.10152 | 0.049166
48 | 0.17061 | 0.082628
49 | 0.37017 | 0.17928
50 | 0.31407 | 0.15211
51 | 0.12364 | 0.059879
52 | 0.10883 | 0.052709
53 | 0.18712 | 0.090625
54 | 0.11538 | 0.05588
55 | 0.22095 | 0.10701
56 | 0.1102 | 0.05337
57 | 0.21649 | 0.10485
58 | 0.89177 | 0.43191
59 | 0.070874 | 0.034326
60 | 0.12267 | 0.059411
61 | 1.2043 | 0.58326
62 | 0.26189 | 0.12684
63 | 0.14713 | 0.07126
64 | 0.58454 | 0.2831
65 | 0.1146 | 0.055504
66 | 0.37867 | 0.1834
67 | 0.11453 | 0.055469
68 | 0.3807 | 0.18438
69 | 1.77 | 0.85724
70 | 0.084724 | 0.041034
71 | 0.16096 | 0.077957
72 | 0.29429 | 0.14253
73 | 0.075934 | 0.036777
74 | 0.10611 | 0.051393
75 | 0.14013 | 0.067869
76 | 0.13663 | 0.066173
77 | 0.25783 | 0.12487

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1