## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_100_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_100_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_100_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_100_0_node_146 | 20 | n |  | TRUE
4 | bus_MV_100_0_node_156 | 20 | n |  | TRUE
5 | bus_MV_100_0_node_120 | 20 | n |  | TRUE
6 | bus_MV_100_0_node_155 | 20 | n |  | TRUE
7 | bus_MV_100_0_node_5 | 20 | n |  | TRUE
8 | bus_MV_100_0_node_4 | 20 | n |  | TRUE
9 | bus_MV_100_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_100_0_node_282 | 20 | n |  | TRUE
11 | bus_MV_100_0_node_3 | 20 | n |  | TRUE
12 | bus_MV_100_0_node_22 | 20 | n |  | TRUE
13 | bus_MV_100_0_node_23 | 20 | n |  | TRUE
14 | bus_MV_100_0_node_24 | 20 | n |  | TRUE
15 | bus_MV_100_0_node_25 | 20 | n |  | TRUE
16 | bus_MV_100_0_node_26 | 20 | n |  | TRUE
17 | bus_MV_100_0_node_28 | 20 | n |  | TRUE
18 | bus_MV_100_0_node_35 | 20 | n |  | TRUE
19 | bus_MV_100_0_node_261 | 20 | n |  | TRUE
20 | bus_MV_100_0_node_170 | 20 | n |  | TRUE
21 | bus_MV_100_0_node_107 | 20 | n |  | TRUE
22 | bus_MV_100_0_node_106 | 20 | n |  | TRUE
23 | bus_MV_100_0_node_36 | 20 | n |  | TRUE
24 | bus_MV_100_0_node_37 | 20 | n |  | TRUE
25 | bus_MV_100_0_node_39 | 20 | n |  | TRUE
26 | bus_MV_100_0_node_285 | 20 | n |  | TRUE
27 | bus_MV_100_0_node_38 | 20 | n |  | TRUE
28 | bus_MV_100_0_node_284 | 20 | n |  | TRUE
29 | bus_MV_100_0_node_178 | 20 | n |  | TRUE
30 | bus_MV_100_0_node_177 | 20 | n |  | TRUE
31 | bus_MV_100_0_node_121 | 20 | n |  | TRUE
32 | bus_MV_100_0_node_185 | 20 | n |  | TRUE
33 | bus_MV_100_0_node_186 | 20 | n |  | TRUE
34 | bus_MV_100_0_node_40 | 20 | n |  | TRUE
35 | bus_MV_100_0_node_42 | 20 | n |  | TRUE
36 | bus_MV_100_0_node_41 | 20 | n |  | TRUE
37 | bus_MV_100_0_node_87 | 20 | n |  | TRUE
38 | bus_MV_100_0_node_258 | 20 | n |  | TRUE
39 | bus_MV_100_0_node_43 | 20 | n |  | TRUE
40 | bus_MV_100_0_node_68 | 20 | n |  | TRUE
41 | bus_MV_100_0_node_166 | 20 | n |  | TRUE
42 | bus_MV_100_0_node_89 | 20 | n |  | TRUE
43 | bus_MV_100_0_node_91 | 20 | n |  | TRUE
44 | bus_MV_100_0_node_67 | 20 | n |  | TRUE
45 | bus_MV_100_0_node_154 | 20 | n |  | TRUE
46 | bus_MV_100_0_node_44 | 20 | n |  | TRUE
47 | bus_MV_100_0_node_45 | 20 | n |  | TRUE
48 | bus_MV_100_0_node_46 | 20 | n |  | TRUE
49 | bus_MV_100_0_node_51 | 20 | n |  | TRUE
50 | bus_MV_100_0_node_48 | 20 | n |  | TRUE
51 | bus_MV_100_0_node_50 | 20 | n |  | TRUE
52 | bus_MV_100_0_node_47 | 20 | n |  | TRUE
53 | bus_MV_100_0_node_49 | 20 | n |  | TRUE
54 | bus_MV_100_0_node_59 | 20 | n |  | TRUE
55 | bus_MV_100_0_node_58 | 20 | n |  | TRUE
56 | bus_MV_100_0_node_60 | 20 | n |  | TRUE
57 | bus_MV_100_0_node_52 | 20 | n |  | TRUE
58 | bus_MV_100_0_node_53 | 20 | n |  | TRUE
59 | bus_MV_100_0_node_55 | 20 | n |  | TRUE
60 | bus_MV_100_0_node_56 | 20 | n |  | TRUE
61 | bus_MV_100_0_node_57 | 20 | n |  | TRUE
62 | bus_MV_100_0_node_99 | 20 | n |  | TRUE
63 | bus_MV_100_0_node_98 | 20 | n |  | TRUE
64 | bus_MV_100_0_node_63 | 20 | n |  | TRUE
65 | bus_MV_100_0_node_61 | 20 | n |  | TRUE
66 | bus_MV_100_0_node_267 | 20 | n |  | TRUE
67 | bus_MV_100_0_node_62 | 20 | n |  | TRUE
68 | bus_MV_100_0_node_71 | 20 | n |  | TRUE
69 | bus_MV_100_0_node_72 | 20 | n |  | TRUE
70 | bus_MV_100_0_node_70 | 20 | n |  | TRUE
71 | bus_MV_100_0_node_250 | 20 | n |  | TRUE
72 | bus_MV_100_0_node_96 | 20 | n |  | TRUE
73 | bus_MV_100_0_node_95 | 20 | n |  | TRUE
74 | bus_MV_100_0_node_69 | 20 | n |  | TRUE
75 | bus_MV_100_0_node_64 | 20 | n |  | TRUE
76 | bus_MV_100_0_node_66 | 20 | n |  | TRUE
77 | bus_MV_100_0_node_86 | 20 | n |  | TRUE
78 | bus_MV_100_0_node_275 | 20 | n |  | TRUE
79 | bus_MV_100_0_node_76 | 20 | n |  | TRUE
80 | bus_MV_100_0_node_92 | 20 | n |  | TRUE
81 | bus_MV_100_0_node_73 | 20 | n |  | TRUE
82 | bus_MV_100_0_node_93 | 20 | n |  | TRUE
83 | bus_MV_100_0_node_94 | 20 | n |  | TRUE
84 | bus_MV_100_0_node_77 | 20 | n |  | TRUE
85 | bus_MV_100_0_node_74 | 20 | n |  | TRUE
86 | bus_MV_100_0_node_75 | 20 | n |  | TRUE
87 | bus_MV_100_0_node_90 | 20 | n |  | TRUE
88 | bus_MV_100_0_node_277 | 20 | n |  | TRUE
89 | bus_MV_100_0_node_78 | 20 | n |  | TRUE
90 | bus_MV_100_0_node_80 | 20 | n |  | TRUE
91 | bus_MV_100_0_node_83 | 20 | n |  | TRUE
92 | bus_MV_100_0_node_82 | 20 | n |  | TRUE
93 | bus_MV_100_0_node_287 | 20 | n |  | TRUE
94 | bus_MV_100_0_node_157 | 20 | n |  | TRUE
95 | bus_MV_100_0_node_158 | 20 | n |  | TRUE
96 | bus_MV_100_0_node_159 | 20 | n |  | TRUE
97 | bus_MV_100_0_node_84 | 20 | n |  | TRUE
98 | bus_MV_100_0_node_85 | 20 | n |  | TRUE
99 | bus_MV_100_0_node_97 | 20 | n |  | TRUE
100 | bus_MV_100_0_node_276 | 20 | n |  | TRUE
101 | bus_MV_100_0_node_102 | 20 | n |  | TRUE
102 | bus_MV_100_0_node_104 | 20 | n |  | TRUE
103 | bus_MV_100_0_node_101 | 20 | n |  | TRUE
104 | bus_MV_100_0_node_100 | 20 | n |  | TRUE
105 | bus_MV_100_0_node_103 | 20 | n |  | TRUE
106 | bus_MV_100_0_node_167 | 20 | n |  | TRUE
107 | bus_MV_100_0_node_105 | 20 | n |  | TRUE
108 | bus_MV_100_0_node_251 | 20 | n |  | TRUE
109 | bus_MV_100_0_node_168 | 20 | n |  | TRUE
110 | bus_MV_100_0_node_112 | 20 | n |  | TRUE
111 | bus_MV_100_0_node_113 | 20 | n |  | TRUE
112 | bus_MV_100_0_node_114 | 20 | n |  | TRUE
113 | bus_MV_100_0_node_115 | 20 | n |  | TRUE
114 | bus_MV_100_0_node_118 | 20 | n |  | TRUE
115 | bus_MV_100_0_node_128 | 20 | n |  | TRUE
116 | bus_MV_100_0_node_280 | 20 | n |  | TRUE
117 | bus_MV_100_0_node_141 | 20 | n |  | TRUE
118 | bus_MV_100_0_node_119 | 20 | n |  | TRUE
119 | bus_MV_100_0_node_117 | 20 | n |  | TRUE
120 | bus_MV_100_0_node_126 | 20 | n |  | TRUE
121 | bus_MV_100_0_node_138 | 20 | n |  | TRUE
122 | bus_MV_100_0_node_135 | 20 | n |  | TRUE
123 | bus_MV_100_0_node_148 | 20 | n |  | TRUE
124 | bus_MV_100_0_node_149 | 20 | n |  | TRUE
125 | bus_MV_100_0_node_147 | 20 | n |  | TRUE
126 | bus_MV_100_0_node_153 | 20 | n |  | TRUE
127 | bus_MV_100_0_node_151 | 20 | n |  | TRUE
128 | bus_MV_100_0_node_279 | 20 | n |  | TRUE
129 | bus_MV_100_0_node_143 | 20 | n |  | TRUE
130 | bus_MV_100_0_node_123 | 20 | n |  | TRUE
131 | bus_MV_100_0_node_127 | 20 | n |  | TRUE
132 | bus_MV_100_0_node_130 | 20 | n |  | TRUE
133 | bus_MV_100_0_node_129 | 20 | n |  | TRUE
134 | bus_MV_100_0_node_132 | 20 | n |  | TRUE
135 | bus_MV_100_0_node_131 | 20 | n |  | TRUE
136 | bus_MV_100_0_node_133 | 20 | n |  | TRUE
137 | bus_MV_100_0_node_134 | 20 | n |  | TRUE
138 | bus_MV_100_0_node_160 | 20 | n |  | TRUE
139 | bus_MV_100_0_node_162 | 20 | n |  | TRUE
140 | bus_MV_100_0_node_161 | 20 | n |  | TRUE
141 | bus_MV_100_0_node_137 | 20 | n |  | TRUE
142 | bus_MV_100_0_node_140 | 20 | n |  | TRUE
143 | bus_MV_100_0_node_136 | 20 | n |  | TRUE
144 | bus_MV_100_0_node_139 | 20 | n |  | TRUE
145 | bus_MV_100_0_node_142 | 20 | n |  | TRUE
146 | bus_MV_100_0_node_145 | 20 | n |  | TRUE
147 | bus_MV_100_0_node_144 | 20 | n |  | TRUE
148 | bus_MV_100_0_node_257 | 20 | n |  | TRUE
149 | bus_MV_100_0_node_252 | 20 | n |  | TRUE
150 | bus_MV_100_0_node_278 | 20 | n |  | TRUE
151 | bus_MV_100_0_node_150 | 20 | n |  | TRUE
152 | bus_MV_100_0_node_152 | 20 | n |  | TRUE
153 | bus_MV_100_0_node_165 | 20 | n |  | TRUE
154 | bus_MV_100_0_node_288 | 20 | n |  | TRUE
155 | bus_MV_100_0_node_169 | 20 | n |  | TRUE
156 | bus_MV_100_0_node_179 | 20 | n |  | TRUE
157 | bus_MV_100_0_node_180 | 20 | n |  | TRUE
158 | bus_MV_100_0_node_286 | 20 | n |  | TRUE
159 | bus_MV_100_0_node_182 | 20 | n |  | TRUE
160 | bus_MV_100_0_node_181 | 20 | n |  | TRUE
161 | bus_HV_100_0_node_166 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_100_0_load_0 | 0 | 0.24673 | 0.1195 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_100_0_load_146 | 3 | 0.10003 | 0.048446 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_100_0_load_156 | 4 | 0.12729 | 0.061648 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_100_0_load_120 | 5 | 0.056043 | 0.027143 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_100_0_load_6 | 9 | 0.29378 | 0.14228 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_100_0_load_282 | 10 | 0.40659 | 0.19692 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_100_0_load_3 | 11 | 0.28558 | 0.13831 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_100_0_load_22 | 12 | 0.14693 | 0.071164 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_100_0_load_28 | 17 | 0.14659 | 0.070999 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_100_0_load_35 | 18 | 0.12144 | 0.058818 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_100_0_load_261 | 19 | 0.098966 | 0.047931 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_100_0_load_170 | 20 | 0.12854 | 0.062253 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_100_0_load_36 | 23 | 0.11008 | 0.053312 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_100_0_load_285 | 26 | 0.14876 | 0.07205 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_100_0_load_284 | 28 | 0.078434 | 0.037987 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_100_0_load_177 | 30 | 0.11592 | 0.05614 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_100_0_load_186 | 33 | 0.085729 | 0.041521 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_100_0_load_40 | 34 | 0.13206 | 0.063959 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_100_0_load_42 | 35 | 0.14228 | 0.068907 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_100_0_load_258 | 38 | 0.16465 | 0.079742 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_100_0_load_68 | 40 | 0.11257 | 0.054521 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_100_0_load_67 | 44 | 0.11312 | 0.054787 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_100_0_load_44 | 46 | 0.077674 | 0.037619 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_100_0_load_51 | 49 | 0.10883 | 0.052707 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_100_0_load_47 | 52 | 0.13044 | 0.063174 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_100_0_load_49 | 53 | 0.13227 | 0.064062 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_100_0_load_59 | 54 | 0.14341 | 0.069455 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_100_0_load_58 | 55 | 0.13242 | 0.064133 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_100_0_load_56 | 60 | 0.12972 | 0.062827 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_100_0_load_98 | 63 | 0.11664 | 0.056489 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_100_0_load_63 | 64 | 0.13915 | 0.067392 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_100_0_load_61 | 65 | 0.12524 | 0.060657 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_100_0_load_267 | 66 | 0.096529 | 0.046751 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_100_0_load_62 | 67 | 0.13064 | 0.063272 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_100_0_load_71 | 68 | 0.070898 | 0.034337 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_100_0_load_95 | 73 | 0.076539 | 0.037069 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_100_0_load_69 | 74 | 0.15773 | 0.076393 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_100_0_load_64 | 75 | 0.13134 | 0.06361 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_100_0_load_86 | 77 | 0.16465 | 0.079744 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_100_0_load_275 | 78 | 0.15267 | 0.07394 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_100_0_load_92 | 80 | 0.11397 | 0.055196 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_100_0_load_73 | 81 | 0.15333 | 0.074263 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_100_0_load_77 | 84 | 0.11906 | 0.057664 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_100_0_load_277 | 88 | 0.083361 | 0.040374 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_100_0_load_78 | 89 | 0.10039 | 0.048621 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_100_0_load_287 | 93 | 0.10368 | 0.050214 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_100_0_load_157 | 94 | 0.11257 | 0.054522 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_100_0_load_84 | 97 | 0.13305 | 0.064438 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_100_0_load_97 | 99 | 0.12805 | 0.062017 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_100_0_load_276 | 100 | 0.093795 | 0.045427 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_100_0_load_102 | 101 | 0.12223 | 0.0592 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_100_0_load_104 | 102 | 0.11937 | 0.057812 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_100_0_load_100 | 104 | 0.088403 | 0.042815 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_100_0_load_167 | 106 | 0.099727 | 0.0483 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_100_0_load_251 | 108 | 0.10967 | 0.053115 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_100_0_load_112 | 110 | 0.12476 | 0.060424 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_100_0_load_128 | 115 | 0.11593 | 0.056149 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_100_0_load_280 | 116 | 0.11384 | 0.055134 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_100_0_load_117 | 119 | 0.11218 | 0.054333 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_100_0_load_135 | 122 | 0.11828 | 0.057286 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_100_0_load_149 | 124 | 0.07401 | 0.035845 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_100_0_load_147 | 125 | 0.12395 | 0.060032 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_100_0_load_153 | 126 | 0.14101 | 0.068295 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_100_0_load_279 | 128 | 0.11853 | 0.057405 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_100_0_load_143 | 129 | 0.12233 | 0.059249 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_100_0_load_123 | 130 | 0.12332 | 0.059726 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_100_0_load_127 | 131 | 0.16188 | 0.078402 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_100_0_load_130 | 132 | 0.10987 | 0.053214 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_100_0_load_129 | 133 | 0.070966 | 0.03437 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_100_0_load_160 | 138 | 0.14029 | 0.067948 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_100_0_load_162 | 139 | 0.084556 | 0.040952 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_100_0_load_161 | 140 | 0.071299 | 0.034532 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_100_0_load_137 | 141 | 0.12187 | 0.059025 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_100_0_load_257 | 148 | 0.091479 | 0.044305 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_100_0_load_252 | 149 | 0.067061 | 0.032479 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_100_0_load_278 | 150 | 0.12727 | 0.061641 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_100_0_load_152 | 152 | 0.081319 | 0.039385 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_100_0_load_165 | 153 | 0.10887 | 0.05273 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_100_0_load_288 | 154 | 0.116 | 0.056179 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_100_0_load_179 | 156 | 0.13942 | 0.067522 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_100_0_load_286 | 158 | 0.14987 | 0.072583 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_100_0_load_182 | 159 | 0.058268 | 0.02822 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_100_0_line_0 |  | 0 | 1 | 0.1045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_100_0_line_1 |  | 1 | 2 | 0.59076 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_100_0_line_2 |  | 1 | 3 | 1.1021 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_100_0_line_3 |  | 2 | 7 | 0.28133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_100_0_line_4 |  | 2 | 8 | 0.38771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_100_0_line_5 |  | 2 | 9 | 0.010172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_100_0_line_6 |  | 3 | 4 | 0.11392 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_100_0_line_7 |  | 4 | 5 | 0.56604 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_100_0_line_8 |  | 4 | 6 | 0.15701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_100_0_line_9 |  | 5 | 31 | 0.065969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_100_0_line_10 |  | 6 | 129 | 0.038555 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_100_0_line_11 |  | 6 | 128 | 0.077307 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_100_0_line_12 |  | 7 | 10 | 0.040453 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_100_0_line_13 |  | 8 | 11 | 0.12798 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_100_0_line_14 |  | 12 | 13 | 0.12761 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_100_0_line_15 |  | 13 | 14 | 0.17126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_100_0_line_16 |  | 13 | 15 | 0.33769 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_100_0_line_17 |  | 13 | 16 | 0.36279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_100_0_line_18 |  | 14 | 17 | 0.088949 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_100_0_line_19 |  | 15 | 18 | 0.15938 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_100_0_line_20 |  | 16 | 19 | 0.054034 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_100_0_line_21 |  | 18 | 20 | 0.53543 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_100_0_line_22 |  | 20 | 21 | 0.066926 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_100_0_line_23 |  | 21 | 22 | 0.73442 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_100_0_line_24 |  | 22 | 108 | 0.018735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_100_0_line_25 |  | 22 | 107 | 0.15663 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_100_0_line_26 |  | 23 | 24 | 0.080384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_100_0_line_27 |  | 24 | 25 | 0.97497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_100_0_line_28 |  | 24 | 26 | 1.8677 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_100_0_line_29 |  | 25 | 29 | 0.17951 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_100_0_line_30 |  | 25 | 30 | 0.047544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_100_0_line_31 |  | 25 | 27 | 0.54976 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_100_0_line_32 |  | 26 | 31 | 1.3821 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_100_0_line_33 |  | 27 | 28 | 0.10224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_100_0_line_34 |  | 29 | 32 | 0.41455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_100_0_line_35 |  | 29 | 33 | 0.13301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_100_0_line_36 |  | 32 | 158 | 0.035901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_100_0_line_37 |  | 34 | 35 | 0.007697 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
38 | MV_100_0_line_38 |  | 34 | 36 | 0.01922 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
39 | MV_100_0_line_39 |  | 35 | 37 | 0.089612 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
40 | MV_100_0_line_40 |  | 35 | 38 | 0.1976 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_100_0_line_41 |  | 36 | 39 | 0.09263 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
42 | MV_100_0_line_42 |  | 37 | 42 | 0.35829 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_100_0_line_43 |  | 37 | 43 | 0.24458 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
44 | MV_100_0_line_44 |  | 39 | 40 | 0.061539 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_100_0_line_45 |  | 39 | 41 | 0.69052 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
46 | MV_100_0_line_46 |  | 40 | 44 | 0.059305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_100_0_line_47 |  | 41 | 45 | 0.1347 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
48 | MV_100_0_line_48 |  | 42 | 100 | 0.024277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_100_0_line_49 |  | 43 | 80 | 0.023163 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
50 | MV_100_0_line_50 |  | 43 | 87 | 0.065598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_100_0_line_51 |  | 45 | 153 | 0.063525 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_100_0_line_52 |  | 45 | 152 | 0.13786 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
53 | MV_100_0_line_53 |  | 46 | 47 | 0.084588 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_100_0_line_54 |  | 47 | 48 | 0.097179 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_100_0_line_55 |  | 47 | 49 | 0.046193 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_100_0_line_56 |  | 48 | 50 | 0.074008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_100_0_line_57 |  | 50 | 51 | 0.054609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_100_0_line_58 |  | 50 | 52 | 0.042684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_100_0_line_59 |  | 51 | 54 | 0.071559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_100_0_line_60 |  | 51 | 55 | 0.050199 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_100_0_line_61 |  | 52 | 53 | 0.066058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_100_0_line_62 |  | 54 | 56 | 0.050055 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_100_0_line_63 |  | 56 | 68 | 0.023631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_100_0_line_64 |  | 56 | 69 | 0.15577 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_100_0_line_65 |  | 56 | 70 | 0.053428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_100_0_line_66 |  | 57 | 58 | 0.073701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_100_0_line_67 |  | 57 | 59 | 1.4732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_100_0_line_68 |  | 58 | 60 | 0.030984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_100_0_line_69 |  | 58 | 61 | 0.16517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_100_0_line_70 |  | 59 | 62 | 0.65921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_100_0_line_71 |  | 59 | 63 | 0.00321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_100_0_line_72 |  | 61 | 64 | 0.093774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_100_0_line_73 |  | 61 | 65 | 0.096194 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_100_0_line_74 |  | 62 | 66 | 0.039068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_100_0_line_75 |  | 64 | 67 | 0.056844 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_100_0_line_76 |  | 67 | 75 | 0.11512 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_100_0_line_77 |  | 68 | 71 | 0.022436 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_100_0_line_78 |  | 69 | 72 | 0.04431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_100_0_line_79 |  | 69 | 73 | 0.064312 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_100_0_line_80 |  | 70 | 74 | 0.059058 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_100_0_line_81 |  | 71 | 77 | 0.067032 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_100_0_line_82 |  | 72 | 78 | 0.035301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_100_0_line_83 |  | 73 | 79 | 0.075647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_100_0_line_84 |  | 73 | 80 | 0.13142 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
85 | MV_100_0_line_85 |  | 74 | 76 | 0.052863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_100_0_line_86 |  | 75 | 76 | 0.006246 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_100_0_line_87 |  | 77 | 98 | 0.065994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_100_0_line_88 |  | 79 | 85 | 0.087156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_100_0_line_89 |  | 81 | 82 | 0.12519 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_100_0_line_90 |  | 82 | 83 | 0.094717 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_100_0_line_91 |  | 82 | 84 | 0.042201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_100_0_line_92 |  | 83 | 103 | 0.032042 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_100_0_line_93 |  | 83 | 104 | 0.034169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_100_0_line_94 |  | 84 | 86 | 0.037613 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_100_0_line_95 |  | 85 | 86 | 0.023948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_100_0_line_96 |  | 87 | 88 | 0.046988 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
97 | MV_100_0_line_97 |  | 89 | 90 | 0.037742 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_100_0_line_98 |  | 90 | 91 | 0.21814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_100_0_line_99 |  | 91 | 94 | 0.13908 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_100_0_line_100 |  | 91 | 92 | 0.21713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_100_0_line_101 |  | 92 | 93 | 0.099997 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_100_0_line_102 |  | 94 | 95 | 0.021932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_100_0_line_103 |  | 95 | 96 | 0.13831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_100_0_line_104 |  | 96 | 154 | 0.055139 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_100_0_line_105 |  | 97 | 98 | 0.047748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_100_0_line_106 |  | 98 | 99 | 0.10208 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_100_0_line_107 |  | 101 | 102 | 0.21018 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_100_0_line_108 |  | 101 | 103 | 0.16037 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_100_0_line_109 |  | 102 | 107 | 0.036088 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_100_0_line_110 |  | 103 | 105 | 0.091383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_100_0_line_111 |  | 105 | 106 | 0.079102 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_100_0_line_112 |  | 106 | 109 | 0.074505 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_100_0_line_113 |  | 109 | 155 | 0.39468 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_100_0_line_114 |  | 110 | 111 | 0.00207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_100_0_line_115 |  | 111 | 112 | 0.13969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_100_0_line_116 |  | 111 | 113 | 0.1426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_100_0_line_117 |  | 111 | 114 | 0.1003 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
118 | MV_100_0_line_118 |  | 112 | 115 | 0.041493 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_100_0_line_119 |  | 113 | 116 | 0.035864 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_100_0_line_120 |  | 113 | 117 | 0.067252 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
121 | MV_100_0_line_121 |  | 114 | 118 | 0.093792 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
122 | MV_100_0_line_122 |  | 114 | 119 | 0.063946 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_100_0_line_123 |  | 115 | 120 | 0.037902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_100_0_line_124 |  | 117 | 121 | 0.055814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_100_0_line_125 |  | 118 | 123 | 0.048536 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
126 | MV_100_0_line_126 |  | 120 | 133 | 0.028444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_100_0_line_127 |  | 121 | 122 | 0.045849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_100_0_line_128 |  | 122 | 141 | 0.041141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_100_0_line_129 |  | 123 | 124 | 0.081502 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_100_0_line_130 |  | 123 | 125 | 0.010721 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
131 | MV_100_0_line_131 |  | 125 | 126 | 0.089217 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
132 | MV_100_0_line_132 |  | 126 | 127 | 0.06074 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
133 | MV_100_0_line_133 |  | 127 | 151 | 0.018948 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
134 | MV_100_0_line_134 |  | 129 | 144 | 0.007177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_100_0_line_135 |  | 130 | 131 | 0.022753 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_100_0_line_136 |  | 131 | 132 | 0.028517 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_100_0_line_137 |  | 132 | 134 | 0.016537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_100_0_line_138 |  | 133 | 134 | 0.03176 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
139 | MV_100_0_line_139 |  | 135 | 136 | 0.039426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_100_0_line_140 |  | 135 | 137 | 0.024902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_100_0_line_141 |  | 136 | 138 | 0.04504 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
142 | MV_100_0_line_142 |  | 137 | 139 | 0.035433 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_100_0_line_143 |  | 138 | 140 | 0.038479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_100_0_line_144 |  | 140 | 150 | 0.073741 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_100_0_line_145 |  | 141 | 142 | 0.02956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_100_0_line_146 |  | 142 | 146 | 0.12895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_100_0_line_147 |  | 142 | 143 | 0.08931 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
148 | MV_100_0_line_148 |  | 143 | 144 | 0.0989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_100_0_line_149 |  | 144 | 145 | 0.094406 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_100_0_line_150 |  | 145 | 149 | 0.021457 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_100_0_line_151 |  | 146 | 147 | 0.10333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_100_0_line_152 |  | 147 | 148 | 0.028547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_100_0_line_153 |  | 149 | 150 | 0.028969 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
154 | MV_100_0_line_154 |  | 151 | 152 | 0.041813 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
155 | MV_100_0_line_155 |  | 154 | 155 | 0.045602 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_100_0_line_156 |  | 156 | 157 | 0.092654 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_100_0_line_157 |  | 157 | 160 | 0.043831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_100_0_line_158 |  | 158 | 159 | 0.19325 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
159 | MV_100_0_line_159 |  | 159 | 160 | 0.073781 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_100_0_trafo_166 | 25 MVA 110/20 kV | 161 | 41 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2613474.1399 | 1129997.6155
1 | 2613572.4973 | 1129999.3892
2 | 2613129.9031 | 1129744.5473
3 | 2614641.7226 | 1129732.1204
4 | 2614720.3476 | 1129814.562
5 | 2614719.9833 | 1130380.6047
6 | 2614873.0302 | 1129822.916
7 | 2612960.2521 | 1129575.6005
8 | 2612830.7407 | 1129780.7814
9 | 2613136.7721 | 1129752.0497
10 | 2612967.9285 | 1129613.024
11 | 2612703.2069 | 1129770.1304
12 | 2617298.3653 | 1127329.5328
13 | 2617171.2191 | 1127318.6997
14 | 2617098.092 | 1127213.2415
15 | 2617105.5338 | 1127481.6387
16 | 2616856.383 | 1127272.5612
17 | 2617181.1011 | 1127181.2827
18 | 2617022.7834 | 1127617.8506
19 | 2616811.9545 | 1127241.6339
20 | 2616830.0904 | 1128117.4027
21 | 2616800.1089 | 1128177.2379
22 | 2616324.0818 | 1128307.4582
23 | 2616514.2181 | 1130361.5906
24 | 2616447.5524 | 1130322.4792
25 | 2617184.2518 | 1129957.6757
26 | 2615219.6942 | 1131729.8308
27 | 2617186.4493 | 1130114.4032
28 | 2617267.7417 | 1130057.6396
29 | 2617360.1508 | 1129981.5994
30 | 2617180.3956 | 1129910.5528
31 | 2614716.7296 | 1130442.4493
32 | 2617750.9035 | 1130089.1164
33 | 2617493.2731 | 1129986.4397
34 | 2615664.1427 | 1128853.0088
35 | 2615671.536 | 1128850.7935
36 | 2615645.6641 | 1128858.2971
37 | 2615760.3638 | 1128838.9621
38 | 2615854.2722 | 1128925.9715
39 | 2615634.044 | 1128925.3555
40 | 2615576.055 | 1128945.8066
41 | 2615450.1122 | 1129103.8609
42 | 2616110.4409 | 1128782.6981
43 | 2615840.4417 | 1128720.6126
44 | 2615530.4205 | 1128927.8463
45 | 2615386.5144 | 1129165.0849
46 | 2615373.8263 | 1128399.4333
47 | 2615439.4151 | 1128346.0181
48 | 2615467.6535 | 1128438.5019
49 | 2615480.7641 | 1128366.6112
50 | 2615479.4931 | 1128511.4901
51 | 2615489.9722 | 1128565.0764
52 | 2615438.2361 | 1128518.7441
53 | 2615373.6716 | 1128527.3845
54 | 2615499.8372 | 1128635.814
55 | 2615442.7434 | 1128582.0866
56 | 2615550.0322 | 1128636.6539
57 | 2615283.198 | 1128542.6858
58 | 2615286.1788 | 1128616.3071
59 | 2615278.5596 | 1127282.1455
60 | 2615317.1251 | 1128619.1309
61 | 2615255.5497 | 1128778.3983
62 | 2615419.7918 | 1127136.5756
63 | 2615281.6288 | 1127281.175
64 | 2615349.2578 | 1128786.3829
65 | 2615164.1457 | 1128748.4213
66 | 2615398.3567 | 1127169.2706
67 | 2615400.5328 | 1128761.8452
68 | 2615553.5262 | 1128613.2826
69 | 2615676.8242 | 1128679.4343
70 | 2615541.4871 | 1128688.4463
71 | 2615556.8435 | 1128591.0935
72 | 2615656.7867 | 1128718.4128
73 | 2615716.2291 | 1128628.5335
74 | 2615523.771 | 1128744.7841
75 | 2615508.4646 | 1128801.8729
76 | 2615510.0823 | 1128795.8408
77 | 2615577.6138 | 1128527.6712
78 | 2615621.794 | 1128722.5913
79 | 2615769.4476 | 1128574.634
80 | 2615821.4719 | 1128707.2454
81 | 2615775.6398 | 1128338.212
82 | 2615874.1343 | 1128415.4844
83 | 2615920.69 | 1128333.0215
84 | 2615853.4301 | 1128452.2817
85 | 2615820.2911 | 1128504.2096
86 | 2615833.1861 | 1128484.0111
87 | 2615890.0249 | 1128687.0924
88 | 2615923.8062 | 1128654.4316
89 | 2616349.021 | 1127223.4716
90 | 2616311.2344 | 1127223.0586
91 | 2616160.3333 | 1127331.8862
92 | 2615979.1386 | 1127283.5273
93 | 2615880.5611 | 1127266.7382
94 | 2616146.057 | 1127470.2272
95 | 2616147.9343 | 1127491.5537
96 | 2616158.3704 | 1127623.3795
97 | 2615607.138 | 1128418.5936
98 | 2615596.1021 | 1128465.0436
99 | 2615690.327 | 1128504.3167
100 | 2616131.2737 | 1128770.1362
101 | 2616043.0744 | 1128418.3745
102 | 2616217.0368 | 1128300.4234
103 | 2615931.4622 | 1128302.9239
104 | 2615947.5161 | 1128354.1298
105 | 2615959.4951 | 1128215.9438
106 | 2615988.9677 | 1128144.2862
107 | 2616243.4193 | 1128324.9615
108 | 2616335.0549 | 1128292.2731
109 | 2616047.9649 | 1128098.5751
110 | 2615124.3965 | 1129449.5432
111 | 2615122.3924 | 1129450.0829
112 | 2615095.113 | 1129535.468
113 | 2615025.066 | 1129495.13
114 | 2615059.9726 | 1129371.5671
115 | 2615092.2999 | 1129576.3699
116 | 2615042.126 | 1129526.6766
117 | 2614976.1332 | 1129541.265
118 | 2615134.7678 | 1129327.6872
119 | 2615009.3607 | 1129401.6009
120 | 2615098.77 | 1129613.5264
121 | 2614925.0693 | 1129561.6603
122 | 2614922.8876 | 1129606.2768
123 | 2615181.7696 | 1129327.9269
124 | 2615257.3519 | 1129323.8366
125 | 2615189.7599 | 1129320.7545
126 | 2615156.128 | 1129238.1189
127 | 2615216.6591 | 1129231.2781
128 | 2614851.3519 | 1129897.1215
129 | 2614889.706 | 1129788.1399
130 | 2615179.9043 | 1129577.8001
131 | 2615177.9989 | 1129600.4731
132 | 2615155.326 | 1129617.7694
133 | 2615115.7048 | 1129636.3019
134 | 2615139.0429 | 1129614.7606
135 | 2615175.539 | 1129660.1184
136 | 2615139.0695 | 1129675.0902
137 | 2615173.4556 | 1129683.2023
138 | 2615104.0074 | 1129703.3612
139 | 2615195.2369 | 1129657.6263
140 | 2615084.5618 | 1129736.4815
141 | 2614895.2716 | 1129636.2195
142 | 2614875.5528 | 1129657.9192
143 | 2614943.1282 | 1129716.3138
144 | 2614896.6099 | 1129790.1689
145 | 2614988.9921 | 1129808.0384
146 | 2614788.9073 | 1129693.3582
147 | 2614830.9133 | 1129599.826
148 | 2614840.1837 | 1129572.8243
149 | 2615010.2355 | 1129804.6114
150 | 2615024.6622 | 1129779.4904
151 | 2615234.9642 | 1129236.2264
152 | 2615261.3125 | 1129203.7914
153 | 2615339.5573 | 1129122.3007
154 | 2616141.5571 | 1127675.8938
155 | 2616122.8854 | 1127717.4979
156 | 2617603.5233 | 1130377.5061
157 | 2617687.1185 | 1130347.2789
158 | 2617780.7015 | 1130107.6461
159 | 2617781.9985 | 1130300.8891
160 | 2617729.633 | 1130351.783
161 | 2615450.1122 | 1129103.8609

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99129 | -0.053488 | 0.24673 | 0.1195
1 | 0.99132 | -0.053793 | 0 | 0
2 | 0.99058 | -0.047614 | 0 | 0
3 | 0.99394 | -0.033872 | 0.10003 | 0.048446
4 | 0.99423 | -0.031672 | 0.12729 | 0.061648
5 | 0.99323 | -0.041598 | 0.056043 | 0.027143
6 | 0.99471 | -0.035186 | 0 | 0
7 | 0.99043 | -0.046297 | 0 | 0
8 | 0.99044 | -0.046382 | 0 | 0
9 | 0.99057 | -0.047578 | 0.29378 | 0.14228
10 | 0.99041 | -0.046097 | 0.40659 | 0.19692
11 | 0.99037 | -0.046833 | 0.28558 | 0.13831
12 | 0.99271 | -0.06462 | 0.14693 | 0.071164
13 | 0.99274 | -0.064389 | 0 | 0
14 | 0.99271 | -0.06413 | 0 | 0
15 | 0.99291 | -0.06556 | 0 | 0
16 | 0.9927 | -0.064083 | 0 | 0
17 | 0.99269 | -0.063977 | 0.14659 | 0.070999
18 | 0.99303 | -0.064461 | 0.12144 | 0.058818
19 | 0.99269 | -0.06402 | 0.098966 | 0.047931
20 | 0.99355 | -0.059957 | 0.12854 | 0.062253
21 | 0.99364 | -0.059287 | 0 | 0
22 | 0.99423 | -0.063415 | 0 | 0
23 | 0.98824 | -0.091676 | 0.11008 | 0.053312
24 | 0.98825 | -0.091779 | 0 | 0
25 | 0.98748 | -0.087494 | 0 | 0
26 | 0.99084 | -0.064221 | 0.14876 | 0.07205
27 | 0.98743 | -0.08728 | 0 | 0
28 | 0.98742 | -0.08719 | 0.078434 | 0.037987
29 | 0.98738 | -0.086783 | 0 | 0
30 | 0.98747 | -0.087428 | 0.11592 | 0.05614
31 | 0.99315 | -0.041175 | 0 | 0
32 | 0.9872 | -0.085307 | 0 | 0
33 | 0.98737 | -0.086657 | 0.085729 | 0.041521
34 | 0.99767 | -0.030164 | 0.13206 | 0.063959
35 | 0.99765 | -0.030414 | 0.14228 | 0.068907
36 | 0.99778 | -0.027146 | 0 | 0
37 | 0.99717 | -0.043348 | 0 | 0
38 | 0.99759 | -0.030811 | 0.16465 | 0.079742
39 | 0.99803 | -0.024063 | 0 | 0
40 | 0.99802 | -0.023905 | 0.11257 | 0.054521
41 | 1 | 0 | -10.3163 | -4.6183
42 | 0.99712 | -0.043055 | 0 | 0
43 | 0.99657 | -0.05069 | 0 | 0
44 | 0.99801 | -0.023827 | 0.11312 | 0.054787
45 | 0.99964 | -0.004216 | 0 | 0
46 | 0.99502 | -0.062807 | 0.077674 | 0.037619
47 | 0.99504 | -0.062727 | 0 | 0
48 | 0.99506 | -0.062937 | 0 | 0
49 | 0.99503 | -0.062788 | 0.10883 | 0.052707
50 | 0.99508 | -0.063088 | 0 | 0
51 | 0.99511 | -0.063359 | 0 | 0
52 | 0.99506 | -0.062958 | 0.13044 | 0.063174
53 | 0.99505 | -0.062856 | 0.13227 | 0.064062
54 | 0.99516 | -0.06382 | 0.14341 | 0.069455
55 | 0.9951 | -0.06344 | 0.13242 | 0.064133
56 | 0.99521 | -0.064225 | 0 | 0
57 | 0.99459 | -0.06658 | 0 | 0
58 | 0.99461 | -0.066522 | 0 | 0
59 | 0.99421 | -0.066004 | 0 | 0
60 | 0.99461 | -0.066474 | 0.12972 | 0.062827
61 | 0.99468 | -0.066614 | 0 | 0
62 | 0.99413 | -0.065603 | 0 | 0
63 | 0.99421 | -0.065999 | 0.11664 | 0.056489
64 | 0.99474 | -0.066789 | 0.13915 | 0.067392
65 | 0.99466 | -0.066761 | 0.12524 | 0.060657
66 | 0.99413 | -0.065559 | 0.096529 | 0.046751
67 | 0.9948 | -0.066073 | 0.13064 | 0.063272
68 | 0.99519 | -0.064091 | 0.070898 | 0.034337
69 | 0.99565 | -0.067641 | 0 | 0
70 | 0.99514 | -0.063776 | 0 | 0
71 | 0.99518 | -0.063982 | 0 | 0
72 | 0.99564 | -0.067563 | 0 | 0
73 | 0.99585 | -0.06915 | 0.076539 | 0.037069
74 | 0.99502 | -0.06483 | 0.15773 | 0.076393
75 | 0.99496 | -0.06444 | 0.13134 | 0.06361
76 | 0.99497 | -0.064482 | 0 | 0
77 | 0.99514 | -0.063653 | 0.16465 | 0.079744
78 | 0.99564 | -0.067499 | 0.15267 | 0.07394
79 | 0.99567 | -0.067875 | 0 | 0
80 | 0.99651 | -0.051371 | 0.11397 | 0.055196
81 | 0.99518 | -0.064914 | 0.15333 | 0.074263
82 | 0.99522 | -0.064679 | 0 | 0
83 | 0.99503 | -0.063353 | 0 | 0
84 | 0.99531 | -0.065343 | 0.11906 | 0.057664
85 | 0.99546 | -0.066396 | 0 | 0
86 | 0.9954 | -0.065987 | 0 | 0
87 | 0.99656 | -0.050627 | 0 | 0
88 | 0.99655 | -0.050675 | 0.083361 | 0.040374
89 | 0.99438 | -0.060273 | 0.10039 | 0.048621
90 | 0.99439 | -0.060318 | 0 | 0
91 | 0.99442 | -0.060534 | 0 | 0
92 | 0.99439 | -0.0603 | 0 | 0
93 | 0.99437 | -0.060427 | 0.10368 | 0.050214
94 | 0.99447 | -0.060052 | 0.11257 | 0.054522
95 | 0.99448 | -0.060119 | 0 | 0
96 | 0.99453 | -0.060528 | 0 | 0
97 | 0.99511 | -0.063379 | 0.13305 | 0.064438
98 | 0.99512 | -0.063454 | 0 | 0
99 | 0.9951 | -0.063614 | 0.12805 | 0.062017
100 | 0.99712 | -0.043028 | 0.093795 | 0.045427
101 | 0.99476 | -0.061515 | 0.12223 | 0.0592
102 | 0.99441 | -0.064612 | 0.11937 | 0.057812
103 | 0.99496 | -0.062933 | 0 | 0
104 | 0.99502 | -0.063317 | 0.088403 | 0.042815
105 | 0.9949 | -0.062525 | 0 | 0
106 | 0.99485 | -0.062162 | 0.099727 | 0.0483
107 | 0.99438 | -0.064392 | 0 | 0
108 | 0.99423 | -0.063391 | 0.10967 | 0.053115
109 | 0.99481 | -0.061901 | 0 | 0
110 | 0.99763 | -0.042056 | 0.12476 | 0.060424
111 | 0.99763 | -0.042059 | 0 | 0
112 | 0.99753 | -0.041124 | 0 | 0
113 | 0.99698 | -0.037075 | 0 | 0
114 | 0.99813 | -0.028907 | 0 | 0
115 | 0.9975 | -0.04084 | 0.11593 | 0.056149
116 | 0.99697 | -0.037125 | 0.11384 | 0.055134
117 | 0.99653 | -0.040663 | 0 | 0
118 | 0.99835 | -0.026275 | 0 | 0
119 | 0.99812 | -0.028824 | 0.11218 | 0.054333
120 | 0.99747 | -0.040632 | 0 | 0
121 | 0.99629 | -0.038778 | 0 | 0
122 | 0.99609 | -0.037225 | 0.11828 | 0.057286
123 | 0.99847 | -0.024911 | 0 | 0
124 | 0.99846 | -0.024844 | 0.07401 | 0.035845
125 | 0.9985 | -0.024605 | 0.12395 | 0.060032
126 | 0.99897 | -0.012087 | 0.14101 | 0.068295
127 | 0.99913 | -0.010263 | 0 | 0
128 | 0.99469 | -0.035298 | 0.11853 | 0.057405
129 | 0.99484 | -0.036098 | 0.12233 | 0.059249
130 | 0.9974 | -0.040682 | 0.12332 | 0.059726
131 | 0.99741 | -0.040648 | 0.16188 | 0.078402
132 | 0.99742 | -0.040549 | 0.10987 | 0.053214
133 | 0.99746 | -0.040474 | 0.070966 | 0.03437
134 | 0.99743 | -0.040628 | 0 | 0
135 | 0.9947 | -0.035995 | 0 | 0
136 | 0.9947 | -0.036031 | 0 | 0
137 | 0.9947 | -0.035972 | 0 | 0
138 | 0.99471 | -0.035975 | 0.14029 | 0.067948
139 | 0.99469 | -0.035937 | 0.084556 | 0.040952
140 | 0.99472 | -0.036073 | 0.071299 | 0.034532
141 | 0.99591 | -0.035887 | 0.12187 | 0.059025
142 | 0.99579 | -0.034968 | 0 | 0
143 | 0.99525 | -0.039296 | 0 | 0
144 | 0.99486 | -0.036278 | 0 | 0
145 | 0.9948 | -0.035749 | 0 | 0
146 | 0.99578 | -0.034864 | 0 | 0
147 | 0.99576 | -0.034762 | 0 | 0
148 | 0.99576 | -0.034731 | 0.091479 | 0.044305
149 | 0.99479 | -0.035626 | 0.067061 | 0.032479
150 | 0.99476 | -0.035785 | 0.12727 | 0.061641
151 | 0.99918 | -0.0096927 | 0 | 0
152 | 0.99928 | -0.0084346 | 0.081319 | 0.039385
153 | 0.99963 | -0.0042998 | 0.10887 | 0.05273
154 | 0.99456 | -0.060682 | 0.116 | 0.056179
155 | 0.99459 | -0.060376 | 0 | 0
156 | 0.98707 | -0.085398 | 0.13942 | 0.067522
157 | 0.98709 | -0.085551 | 0 | 0
158 | 0.98718 | -0.085167 | 0.14987 | 0.072583
159 | 0.98711 | -0.085725 | 0.058268 | 0.02822
160 | 0.98709 | -0.085618 | 0 | 0
161 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.24673 | -0.1195 | 0.24674 | 0.11705 | 8.8569e-06 | -0.0024491 | 0.0079836 | 0.0079527 | 0.0079836 | 0.99129 | -0.053488 | 0.99132 | -0.053793 | 3.6289
1 | 0.98688 | 0.44694 | -0.98609 | -0.46056 | 0.00078911 | -0.013617 | 0.031548 | 0.031717 | 0.031717 | 0.99132 | -0.053793 | 0.99058 | -0.047614 | 14.4166
2 | -1.2336 | -0.56399 | 1.2367 | 0.56461 | 0.0030625 | 0.00062186 | 0.0395 | 0.039484 | 0.0395 | 0.99132 | -0.053793 | 0.99394 | -0.033872 | 18.8093
3 | 0.40667 | 0.18941 | -0.4066 | -0.19598 | 6.4595e-05 | -0.0065711 | 0.013074 | 0.013156 | 0.013156 | 0.99058 | -0.047614 | 0.99043 | -0.046297 | 5.9799
4 | 0.28564 | 0.12911 | -0.2856 | -0.13817 | 4.3716e-05 | -0.009069 | 0.009135 | 0.0092472 | 0.0092472 | 0.99058 | -0.047614 | 0.99044 | -0.046382 | 4.2033
5 | 0.29378 | 0.14204 | -0.29378 | -0.14228 | 1.2284e-06 | -0.00023795 | 0.0095095 | 0.0095126 | 0.0095126 | 0.99058 | -0.047614 | 0.99057 | -0.047578 | 4.3239
6 | -1.3367 | -0.61306 | 1.3371 | 0.61316 | 0.00037026 | 9.7523e-05 | 0.042711 | 0.042709 | 0.042711 | 0.99394 | -0.033872 | 0.99423 | -0.031672 | 20.3386
7 | 0.94785 | 0.38981 | -0.94696 | -0.38992 | 0.00089326 | -0.00010779 | 0.029757 | 0.029765 | 0.029765 | 0.99423 | -0.031672 | 0.99323 | -0.041598 | 14.1736
8 | -2.4122 | -1.0646 | 2.4134 | 1.0613 | 0.0012278 | -0.0033432 | 0.076557 | 0.076513 | 0.076557 | 0.99423 | -0.031672 | 0.99471 | -0.035186 | 34.7984
9 | 0.89091 | 0.36277 | -0.89085 | -0.36431 | 6.8882e-05 | -0.0015333 | 0.027958 | 0.027975 | 0.027975 | 0.99323 | -0.041598 | 0.99315 | -0.041175 | 12.7161
10 | -2.532 | -1.1186 | 2.5323 | 1.1178 | 0.00033211 | -0.00081243 | 0.080332 | 0.080321 | 0.080332 | 0.99471 | -0.035186 | 0.99484 | -0.036098 | 36.5144
11 | 0.11853 | 0.057315 | -0.11853 | -0.057405 | 2.0114e-06 | -9.0055e-05 | 0.0038209 | 0.003822 | 0.003822 | 0.99471 | -0.035186 | 0.99469 | -0.035298 | 1.82
12 | 0.4066 | 0.19598 | -0.40659 | -0.19692 | 9.3554e-06 | -0.00094467 | 0.013156 | 0.013168 | 0.013168 | 0.99043 | -0.046297 | 0.99041 | -0.046097 | 5.9854
13 | 0.2856 | 0.13817 | -0.28558 | -0.13831 | 1.9502e-05 | -0.00013765 | 0.0092472 | 0.0092491 | 0.0092491 | 0.99044 | -0.046382 | 0.99037 | -0.046833 | 4.4043
14 | -0.14693 | -0.071164 | 0.14694 | 0.071017 | 5.1224e-06 | -0.00014692 | 0.0047476 | 0.0047457 | 0.0047476 | 0.99271 | -0.06462 | 0.99274 | -0.064389 | 2.2607
15 | 0.1466 | 0.064879 | -0.1466 | -0.068907 | 5.0199e-06 | -0.0040282 | 0.0046618 | 0.0047104 | 0.0047104 | 0.99274 | -0.064389 | 0.99271 | -0.06413 | 2.1411
16 | -0.39251 | -0.17402 | 0.39258 | 0.16609 | 6.9751e-05 | -0.0079267 | 0.012485 | 0.012393 | 0.012485 | 0.99274 | -0.064389 | 0.99291 | -0.06556 | 5.6751
17 | 0.098971 | 0.038125 | -0.098966 | -0.04666 | 4.7475e-06 | -0.008535 | 0.0030841 | 0.0031818 | 0.0031818 | 0.99274 | -0.064389 | 0.9927 | -0.064083 | 1.4463
18 | 0.1466 | 0.068907 | -0.14659 | -0.070999 | 2.6493e-06 | -0.0020921 | 0.0047104 | 0.0047366 | 0.0047366 | 0.99271 | -0.06413 | 0.99269 | -0.063977 | 2.153
19 | -0.39258 | -0.16609 | 0.39263 | 0.16593 | 4.3608e-05 | -0.00016029 | 0.012393 | 0.012391 | 0.012393 | 0.99291 | -0.06556 | 0.99303 | -0.064461 | 5.9016
20 | 0.098966 | 0.04666 | -0.098966 | -0.047931 | 7.3391e-07 | -0.0012711 | 0.0031818 | 0.0031977 | 0.0031977 | 0.9927 | -0.064083 | 0.99269 | -0.06402 | 1.4535
21 | -0.51407 | -0.22475 | 0.51432 | 0.22428 | 0.00025366 | -0.00047177 | 0.01631 | 0.016303 | 0.01631 | 0.99303 | -0.064461 | 0.99355 | -0.059957 | 7.7666
22 | -0.64286 | -0.28653 | 0.64291 | 0.28648 | 4.9863e-05 | -4.7644e-05 | 0.02045 | 0.020449 | 0.02045 | 0.99355 | -0.059957 | 0.99364 | -0.059287 | 9.7379
23 | -0.64291 | -0.28648 | 0.64332 | 0.26928 | 0.00040593 | -0.017202 | 0.020449 | 0.020249 | 0.020449 | 0.99364 | -0.059287 | 0.99423 | -0.063415 | 9.2948
24 | 0.10967 | 0.052673 | -0.10967 | -0.053115 | 3.1258e-07 | -0.00044208 | 0.0035325 | 0.003538 | 0.003538 | 0.99423 | -0.063415 | 0.99423 | -0.063391 | 1.6082
25 | -0.75298 | -0.32196 | 0.7531 | 0.31829 | 0.00011801 | -0.0036622 | 0.023778 | 0.023736 | 0.023778 | 0.99423 | -0.063415 | 0.99438 | -0.064392 | 10.808
26 | -0.11008 | -0.053312 | 0.11008 | 0.051438 | 1.3607e-06 | -0.001874 | 0.0035727 | 0.0035492 | 0.0035727 | 0.98824 | -0.091676 | 0.98825 | -0.091779 | 1.6239
27 | 0.62829 | 0.2423 | -0.62778 | -0.26486 | 0.00050986 | -0.022566 | 0.01967 | 0.019919 | 0.019919 | 0.98825 | -0.091779 | 0.98748 | -0.087494 | 9.0539
28 | -0.73836 | -0.29373 | 0.74015 | 0.29267 | 0.0017911 | -0.0010614 | 0.023212 | 0.023189 | 0.023212 | 0.98825 | -0.091779 | 0.99084 | -0.064221 | 11.0534
29 | 0.43342 | 0.18702 | -0.43337 | -0.19118 | 4.5797e-05 | -0.0041654 | 0.0138 | 0.013848 | 0.013848 | 0.98748 | -0.087494 | 0.98738 | -0.086783 | 6.2948
30 | 0.11592 | 0.055034 | -0.11592 | -0.05614 | 8.9643e-07 | -0.0011066 | 0.0037512 | 0.0037651 | 0.0037651 | 0.98748 | -0.087494 | 0.98747 | -0.087428 | 1.7114
31 | 0.07844 | 0.02281 | -0.078435 | -0.035608 | 4.3942e-06 | -0.012797 | 0.0023881 | 0.0025183 | 0.0025183 | 0.98748 | -0.087494 | 0.98743 | -0.08728 | 1.1447
32 | -0.88892 | -0.36472 | 0.89085 | 0.36431 | 0.0019285 | -0.00041576 | 0.027993 | 0.027975 | 0.027993 | 0.99084 | -0.064221 | 0.99315 | -0.041175 | 13.3301
33 | 0.078435 | 0.035608 | -0.078434 | -0.037987 | 8.7565e-07 | -0.0023798 | 0.0025183 | 0.0025478 | 0.0025478 | 0.98743 | -0.08728 | 0.98742 | -0.08719 | 1.1581
34 | 0.34764 | 0.15276 | -0.34758 | -0.16239 | 6.8919e-05 | -0.0096274 | 0.011102 | 0.011218 | 0.011218 | 0.98738 | -0.086783 | 0.9872 | -0.085307 | 5.0992
35 | 0.08573 | 0.038425 | -0.085729 | -0.041521 | 1.358e-06 | -0.0030956 | 0.0027467 | 0.0027849 | 0.0027849 | 0.98738 | -0.086783 | 0.98737 | -0.086657 | 1.2659
36 | 0.34758 | 0.16239 | -0.34757 | -0.16322 | 6.0373e-06 | -0.00083356 | 0.011218 | 0.011229 | 0.011229 | 0.9872 | -0.085307 | 0.98718 | -0.085167 | 5.1039
37 | 4.9754 | 2.2119 | -4.9753 | -2.2121 | 9.228e-05 | -0.00019576 | 0.15755 | 0.15755 | 0.15755 | 0.99767 | -0.030164 | 0.99765 | -0.030414 | 43.5227
38 | -5.1075 | -2.2759 | 5.1079 | 2.2764 | 0.00046187 | 0.00050424 | 0.16179 | 0.16179 | 0.16179 | 0.99767 | -0.030164 | 0.99778 | -0.027146 | 46.2264
39 | 4.6684 | 2.0637 | -4.6666 | -2.0618 | 0.0017944 | 0.0019404 | 0.14769 | 0.14769 | 0.14769 | 0.99765 | -0.030414 | 0.99717 | -0.043348 | 42.1982
40 | 0.16466 | 0.079513 | -0.16465 | -0.079742 | 9.8607e-06 | -0.00022859 | 0.0052909 | 0.0052938 | 0.0052938 | 0.99765 | -0.030414 | 0.99759 | -0.030811 | 2.5209
41 | -5.1079 | -2.2764 | 5.1091 | 2.2741 | 0.0011709 | -0.0023136 | 0.16179 | 0.16175 | 0.16179 | 0.99778 | -0.027146 | 0.99803 | -0.024063 | 44.694
42 | 0.093799 | 0.036346 | -0.093795 | -0.044851 | 4.1877e-06 | -0.0085045 | 0.0029122 | 0.0030099 | 0.0030099 | 0.99717 | -0.043348 | 0.99712 | -0.043055 | 1.3681
43 | 4.5728 | 2.0254 | -4.5703 | -2.032 | 0.0024781 | -0.0065374 | 0.14478 | 0.14488 | 0.14488 | 0.99717 | -0.043348 | 0.99657 | -0.05069 | 40.0228
44 | 0.2257 | 0.10644 | -0.22569 | -0.1079 | 4.2906e-06 | -0.0014623 | 0.0072177 | 0.0072358 | 0.0072358 | 0.99803 | -0.024063 | 0.99802 | -0.023905 | 3.289
45 | -5.3348 | -2.3805 | 5.3443 | 2.3638 | 0.0095068 | -0.016734 | 0.16897 | 0.16869 | 0.16897 | 0.99803 | -0.024063 | 1 | 0 | 46.6771
46 | 0.11312 | 0.053377 | -0.11312 | -0.054787 | 1.0414e-06 | -0.0014101 | 0.003618 | 0.0036356 | 0.0036356 | 0.99802 | -0.023905 | 0.99801 | -0.023827 | 1.6526
47 | 4.958 | 2.244 | -4.9564 | -2.2475 | 0.0016063 | -0.0034522 | 0.1571 | 0.15716 | 0.15716 | 1 | 0 | 0.99964 | -0.004216 | 43.4133
48 | 0.093795 | 0.044851 | -0.093795 | -0.045427 | 2.9432e-07 | -0.00057622 | 0.0030099 | 0.0030172 | 0.0030172 | 0.99712 | -0.043055 | 0.99712 | -0.043028 | 1.3714
49 | 4.4869 | 1.9932 | -4.4867 | -1.9938 | 0.0002263 | -0.00062469 | 0.14222 | 0.14223 | 0.14223 | 0.99657 | -0.05069 | 0.99651 | -0.051371 | 39.2898
50 | 0.083363 | 0.038763 | -0.083362 | -0.040318 | 6.2553e-07 | -0.0015553 | 0.0026631 | 0.0026824 | 0.0026824 | 0.99657 | -0.05069 | 0.99656 | -0.050627 | 1.2193
51 | 0.10888 | 0.052655 | -0.10887 | -0.05273 | 1.3809e-06 | -7.4917e-05 | 0.0034925 | 0.0034934 | 0.0034934 | 0.99964 | -0.004216 | 0.99963 | -0.0042998 | 1.6635
52 | 4.8475 | 2.1948 | -4.8459 | -2.1984 | 0.0015728 | -0.0035813 | 0.15366 | 0.15372 | 0.15372 | 0.99964 | -0.004216 | 0.99928 | -0.0084346 | 42.4644
53 | -0.077674 | -0.037619 | 0.077675 | 0.03752 | 9.4436e-07 | -9.9389e-05 | 0.0025038 | 0.0025026 | 0.0025038 | 0.99502 | -0.062807 | 0.99504 | -0.062727 | 1.1923
54 | -0.1865 | -0.090173 | 0.18651 | 0.087877 | 4.6634e-06 | -0.0022959 | 0.0060099 | 0.0059812 | 0.0060099 | 0.99504 | -0.062727 | 0.99506 | -0.062937 | 2.7318
55 | 0.10883 | 0.052653 | -0.10883 | -0.052707 | 1.0126e-06 | -5.3965e-05 | 0.0035073 | 0.003508 | 0.003508 | 0.99504 | -0.062727 | 0.99503 | -0.062788 | 1.6705
56 | -0.18651 | -0.087877 | 0.18651 | 0.086128 | 3.5219e-06 | -0.0017486 | 0.0059812 | 0.0059598 | 0.0059812 | 0.99506 | -0.062937 | 0.99508 | -0.063088 | 2.7187
57 | -0.44923 | -0.2108 | 0.44924 | 0.20951 | 1.5091e-05 | -0.0012866 | 0.014396 | 0.01438 | 0.014396 | 0.99508 | -0.063088 | 0.99511 | -0.063359 | 6.5435
58 | 0.26272 | 0.12467 | -0.26271 | -0.12568 | 4.0614e-06 | -0.0010079 | 0.008436 | 0.0084486 | 0.0084486 | 0.99508 | -0.063088 | 0.99506 | -0.062958 | 3.8403
59 | -0.58166 | -0.27358 | 0.58169 | 0.2719 | 3.318e-05 | -0.0016821 | 0.018647 | 0.018626 | 0.018647 | 0.99511 | -0.063359 | 0.99516 | -0.06382 | 8.4759
60 | 0.13242 | 0.064074 | -0.13242 | -0.064133 | 1.6291e-06 | -5.8322e-05 | 0.0042675 | 0.0042682 | 0.0042682 | 0.99511 | -0.063359 | 0.9951 | -0.06344 | 2.0325
61 | 0.13227 | 0.062501 | -0.13227 | -0.064062 | 1.5958e-06 | -0.0015612 | 0.0042442 | 0.0042637 | 0.0042637 | 0.99506 | -0.062958 | 0.99505 | -0.062856 | 1.938
62 | -0.7251 | -0.34136 | 0.72514 | 0.34018 | 3.6093e-05 | -0.0011729 | 0.023248 | 0.023233 | 0.023248 | 0.99516 | -0.06382 | 0.99521 | -0.064225 | 10.5672
63 | 0.49668 | 0.23506 | -0.49668 | -0.23562 | 8.0183e-06 | -0.00055644 | 0.015939 | 0.015946 | 0.015946 | 0.99521 | -0.064225 | 0.99519 | -0.064091 | 7.2482
64 | -2.2493 | -1.0099 | 2.2504 | 1.0065 | 0.0010631 | -0.00337 | 0.07152 | 0.071476 | 0.07152 | 0.99521 | -0.064225 | 0.99565 | -0.067641 | 32.5092
65 | 1.0275 | 0.43467 | -1.0274 | -0.43591 | 7.4733e-05 | -0.0012412 | 0.032362 | 0.032376 | 0.032376 | 0.99521 | -0.064225 | 0.99514 | -0.063776 | 14.7165
66 | -0.21326 | -0.051933 | 0.21326 | 0.050193 | 3.9856e-06 | -0.0017396 | 0.0063705 | 0.0063588 | 0.0063705 | 0.99459 | -0.06658 | 0.99461 | -0.066522 | 2.8957
67 | 0.21326 | 0.051933 | -0.21317 | -0.086689 | 8.3309e-05 | -0.034756 | 0.0063705 | 0.0066818 | 0.0066818 | 0.99459 | -0.06658 | 0.99421 | -0.066004 | 3.0372
68 | 0.12972 | 0.062095 | -0.12972 | -0.062827 | 7.2229e-07 | -0.00073161 | 0.0041741 | 0.0041834 | 0.0041834 | 0.99461 | -0.066522 | 0.99461 | -0.066474 | 1.9015
69 | -0.34298 | -0.11229 | 0.34301 | 0.10839 | 2.4113e-05 | -0.0038945 | 0.010475 | 0.01044 | 0.010475 | 0.99461 | -0.066522 | 0.99468 | -0.066614 | 4.7612
70 | 0.096538 | 0.030275 | -0.09653 | -0.045829 | 7.9889e-06 | -0.015554 | 0.0029376 | 0.0031029 | 0.0031029 | 0.99421 | -0.066004 | 0.99413 | -0.065603 | 1.4104
71 | 0.11664 | 0.056413 | -0.11664 | -0.056489 | 6.0663e-08 | -7.5739e-05 | 0.0037619 | 0.0037629 | 0.0037629 | 0.99421 | -0.066004 | 0.99421 | -0.065999 | 1.7104
72 | -0.46825 | -0.16894 | 0.46828 | 0.16673 | 2.6089e-05 | -0.0022076 | 0.014447 | 0.014425 | 0.014447 | 0.99468 | -0.066614 | 0.99474 | -0.066789 | 6.5668
73 | 0.12524 | 0.060545 | -0.12524 | -0.060657 | 2.7945e-06 | -0.00011187 | 0.0040373 | 0.0040387 | 0.0040387 | 0.99468 | -0.066614 | 0.99466 | -0.066761 | 1.9232
74 | 0.09653 | 0.045829 | -0.096529 | -0.046751 | 5.0402e-07 | -0.00092172 | 0.0031029 | 0.0031145 | 0.0031145 | 0.99413 | -0.065603 | 0.99413 | -0.065559 | 1.4157
75 | -0.60742 | -0.23412 | 0.60746 | 0.23408 | 3.6145e-05 | -4.4513e-05 | 0.018892 | 0.018891 | 0.018892 | 0.99474 | -0.066789 | 0.9948 | -0.066073 | 8.996
76 | -0.7381 | -0.29735 | 0.73821 | 0.29728 | 0.00010935 | -6.7526e-05 | 0.023091 | 0.02309 | 0.023091 | 0.9948 | -0.066073 | 0.99496 | -0.06444 | 10.9958
77 | 0.42578 | 0.20128 | -0.42577 | -0.20181 | 5.5925e-06 | -0.00052888 | 0.013661 | 0.013668 | 0.013668 | 0.99519 | -0.064091 | 0.99518 | -0.063982 | 6.2126
78 | 0.15267 | 0.072056 | -0.15267 | -0.073104 | 1.421e-06 | -0.0010483 | 0.0048947 | 0.0049077 | 0.0049077 | 0.99565 | -0.067641 | 0.99564 | -0.067563 | 2.2308
79 | -2.4031 | -1.0786 | 2.4036 | 1.0772 | 0.00050063 | -0.001374 | 0.07637 | 0.076352 | 0.07637 | 0.99565 | -0.067641 | 0.99585 | -0.06915 | 34.7137
80 | 1.0274 | 0.43591 | -1.0273 | -0.43591 | 0.0001103 | -7.2339e-07 | 0.032376 | 0.032377 | 0.032377 | 0.99514 | -0.063776 | 0.99502 | -0.06483 | 15.4176
81 | 0.42577 | 0.20181 | -0.42576 | -0.20339 | 1.6741e-05 | -0.0015801 | 0.013668 | 0.013687 | 0.013687 | 0.99518 | -0.063982 | 0.99514 | -0.063653 | 6.2216
82 | 0.15267 | 0.073104 | -0.15267 | -0.07394 | 1.1375e-06 | -0.00083518 | 0.0049077 | 0.0049182 | 0.0049182 | 0.99564 | -0.067563 | 0.99564 | -0.067499 | 2.2356
83 | 1.8903 | 0.82186 | -1.89 | -0.82354 | 0.00036068 | -0.0016839 | 0.059751 | 0.059772 | 0.059772 | 0.99585 | -0.06915 | 0.99567 | -0.067875 | 27.1691
84 | -4.3704 | -1.9362 | 4.3727 | 1.9386 | 0.0023164 | 0.0024856 | 0.13856 | 0.13856 | 0.13856 | 0.99585 | -0.06915 | 0.99651 | -0.051371 | 39.59
85 | 0.86961 | 0.35951 | -0.86955 | -0.36075 | 5.2623e-05 | -0.001234 | 0.0273 | 0.027314 | 0.027314 | 0.99502 | -0.06483 | 0.99497 | -0.064482 | 12.4154
86 | -0.86955 | -0.36089 | 0.86955 | 0.36075 | 6.2212e-06 | -0.00014579 | 0.027315 | 0.027314 | 0.027315 | 0.99496 | -0.06444 | 0.99497 | -0.064482 | 12.4161
87 | 0.26111 | 0.12365 | -0.2611 | -0.12521 | 6.2022e-06 | -0.0015585 | 0.0083807 | 0.0084001 | 0.0084001 | 0.99514 | -0.063653 | 0.99512 | -0.063454 | 3.8182
88 | 1.89 | 0.82354 | -1.8895 | -0.82548 | 0.00041586 | -0.0019392 | 0.059772 | 0.059796 | 0.059796 | 0.99567 | -0.067875 | 0.99546 | -0.066396 | 27.1799
89 | -0.15333 | -0.074263 | 0.15334 | 0.074118 | 5.4455e-06 | -0.00014461 | 0.004942 | 0.0049401 | 0.004942 | 0.99518 | -0.064914 | 0.99522 | -0.064679 | 2.3533
90 | 1.6167 | 0.69602 | -1.6163 | -0.69816 | 0.00032976 | -0.0021416 | 0.051055 | 0.05108 | 0.05108 | 0.99522 | -0.064679 | 0.99503 | -0.063353 | 23.2184
91 | -1.77 | -0.77014 | 1.7702 | 0.76919 | 0.00017658 | -0.0009457 | 0.05599 | 0.055979 | 0.05599 | 0.99522 | -0.064679 | 0.99531 | -0.065343 | 25.4502
92 | 1.5279 | 0.65615 | -1.5278 | -0.65688 | 9.9573e-05 | -0.00072786 | 0.048243 | 0.048251 | 0.048251 | 0.99503 | -0.063353 | 0.99496 | -0.062933 | 21.9325
93 | 0.088403 | 0.042008 | -0.088403 | -0.042815 | 3.6912e-07 | -0.00080762 | 0.0028396 | 0.0028497 | 0.0028497 | 0.99503 | -0.063353 | 0.99502 | -0.063317 | 1.2953
94 | -1.8892 | -0.82685 | 1.8894 | 0.82602 | 0.00017961 | -0.00083646 | 0.059813 | 0.059802 | 0.059813 | 0.99531 | -0.065343 | 0.9954 | -0.065987 | 27.1876
95 | 1.8895 | 0.82548 | -1.8894 | -0.82602 | 0.00011432 | -0.00053266 | 0.059796 | 0.059802 | 0.059802 | 0.99546 | -0.066396 | 0.9954 | -0.065987 | 27.1829
96 | 0.083362 | 0.040318 | -0.083361 | -0.040374 | 6.0252e-07 | -5.5332e-05 | 0.0026824 | 0.0026831 | 0.0026831 | 0.99656 | -0.050627 | 0.99655 | -0.050675 | 1.2777
97 | -0.10039 | -0.048621 | 0.10039 | 0.047731 | 5.2652e-07 | -0.00089088 | 0.0032382 | 0.003227 | 0.0032382 | 0.99438 | -0.060273 | 0.99439 | -0.060318 | 1.4719
98 | -0.10039 | -0.047731 | 0.10039 | 0.042581 | 2.974e-06 | -0.0051493 | 0.003227 | 0.0031657 | 0.003227 | 0.99439 | -0.060318 | 0.99442 | -0.060534 | 1.4668
99 | -0.20408 | -0.087553 | 0.20409 | 0.087395 | 1.0295e-05 | -0.00015774 | 0.0064465 | 0.0064446 | 0.0064465 | 0.99442 | -0.060534 | 0.99447 | -0.060052 | 3.0698
100 | 0.10368 | 0.044972 | -0.10368 | -0.050097 | 3.178e-06 | -0.0051254 | 0.0032808 | 0.0033429 | 0.0033429 | 0.99442 | -0.060534 | 0.99439 | -0.0603 | 1.5195
101 | 0.10368 | 0.050097 | -0.10368 | -0.050214 | 1.9918e-06 | -0.00011679 | 0.0033429 | 0.0033443 | 0.0033443 | 0.99439 | -0.0603 | 0.99437 | -0.060427 | 1.5925
102 | -0.31666 | -0.14192 | 0.31667 | 0.1414 | 2.969e-06 | -0.000517 | 0.010073 | 0.010067 | 0.010073 | 0.99447 | -0.060052 | 0.99448 | -0.060119 | 4.5787
103 | -0.31667 | -0.1414 | 0.31668 | 0.13814 | 1.8641e-05 | -0.0032606 | 0.010067 | 0.010029 | 0.010067 | 0.99448 | -0.060119 | 0.99453 | -0.060528 | 4.5759
104 | -0.31668 | -0.13814 | 0.31669 | 0.13684 | 7.3921e-06 | -0.0013 | 0.010029 | 0.010014 | 0.010029 | 0.99453 | -0.060528 | 0.99456 | -0.060682 | 4.5585
105 | -0.13305 | -0.064438 | 0.13305 | 0.06331 | 1.1684e-06 | -0.0011286 | 0.0042885 | 0.0042743 | 0.0042885 | 0.99511 | -0.063379 | 0.99512 | -0.063454 | 1.9493
106 | 0.12805 | 0.061898 | -0.12805 | -0.062017 | 3.0972e-06 | -0.00011874 | 0.0041259 | 0.0041274 | 0.0041274 | 0.99512 | -0.063454 | 0.9951 | -0.063614 | 1.9654
107 | 0.87278 | 0.37519 | -0.8725 | -0.37526 | 0.00028464 | -6.9912e-05 | 0.027569 | 0.027572 | 0.027572 | 0.99476 | -0.061515 | 0.99441 | -0.064612 | 13.1293
108 | -0.99501 | -0.43439 | 0.99522 | 0.43066 | 0.00021223 | -0.0037269 | 0.031506 | 0.031463 | 0.031506 | 0.99476 | -0.061515 | 0.99496 | -0.062933 | 14.3211
109 | 0.75313 | 0.31745 | -0.7531 | -0.31829 | 2.7131e-05 | -0.00084397 | 0.023726 | 0.023736 | 0.023736 | 0.99441 | -0.064612 | 0.99438 | -0.064392 | 10.7889
110 | 0.53261 | 0.22622 | -0.53258 | -0.22837 | 3.4438e-05 | -0.0021496 | 0.016789 | 0.016814 | 0.016814 | 0.99496 | -0.062933 | 0.9949 | -0.062525 | 7.6426
111 | 0.53258 | 0.22837 | -0.53255 | -0.23023 | 2.9891e-05 | -0.0018605 | 0.016814 | 0.016835 | 0.016835 | 0.9949 | -0.062525 | 0.99485 | -0.062162 | 7.6523
112 | 0.43282 | 0.18193 | -0.4328 | -0.18368 | 1.8487e-05 | -0.0017551 | 0.013623 | 0.013643 | 0.013643 | 0.99485 | -0.062162 | 0.99481 | -0.061901 | 6.2015
113 | 0.4328 | 0.18368 | -0.4327 | -0.19298 | 9.8847e-05 | -0.0092945 | 0.013643 | 0.013751 | 0.013751 | 0.99481 | -0.061901 | 0.99459 | -0.060376 | 6.2506
114 | -0.12476 | -0.060424 | 0.12476 | 0.060375 | 4.4468e-08 | -4.9176e-05 | 0.0040112 | 0.0040106 | 0.0040112 | 0.99763 | -0.042056 | 0.99763 | -0.042059 | 1.8233
115 | 0.58209 | 0.27553 | -0.58203 | -0.27883 | 6.4906e-05 | -0.0033 | 0.018635 | 0.018676 | 0.018676 | 0.99763 | -0.042059 | 0.99753 | -0.041124 | 8.4893
116 | 3.6003 | 1.6117 | -3.5978 | -1.6143 | 0.002481 | -0.0026504 | 0.11414 | 0.11418 | 0.11418 | 0.99763 | -0.042059 | 0.99698 | -0.037075 | 51.9
117 | -4.3071 | -1.9476 | 4.3089 | 1.9494 | 0.0017227 | 0.0018449 | 0.13678 | 0.13678 | 0.13678 | 0.99763 | -0.042059 | 0.99813 | -0.028907 | 39.0802
118 | 0.58203 | 0.27883 | -0.58201 | -0.27981 | 1.9334e-05 | -0.00098003 | 0.018676 | 0.018689 | 0.018689 | 0.99753 | -0.041124 | 0.9975 | -0.04084 | 8.4949
119 | 0.11384 | 0.055092 | -0.11384 | -0.055134 | 8.5698e-07 | -4.2019e-05 | 0.0036619 | 0.0036624 | 0.0036624 | 0.99698 | -0.037075 | 0.99697 | -0.037125 | 1.744
120 | 3.484 | 1.5592 | -3.4825 | -1.5584 | 0.0014636 | 0.00083699 | 0.11052 | 0.11052 | 0.11052 | 0.99698 | -0.037075 | 0.99653 | -0.040663 | 52.6289
121 | -4.4211 | -2.0022 | 4.4219 | 1.9997 | 0.0008923 | -0.0025579 | 0.14036 | 0.14033 | 0.14036 | 0.99813 | -0.028907 | 0.99835 | -0.026275 | 38.7748
122 | 0.11219 | 0.052813 | -0.11218 | -0.054333 | 1.1036e-06 | -0.0015207 | 0.0035861 | 0.0036051 | 0.0036051 | 0.99813 | -0.028907 | 0.99812 | -0.028824 | 1.6387
123 | 0.46608 | 0.22366 | -0.46606 | -0.22456 | 1.1334e-05 | -0.00089704 | 0.014961 | 0.014972 | 0.014972 | 0.9975 | -0.04084 | 0.99747 | -0.040632 | 6.8055
124 | 3.4825 | 1.5584 | -3.4816 | -1.5594 | 0.00091028 | -0.0010531 | 0.11052 | 0.11054 | 0.11054 | 0.99653 | -0.040663 | 0.99629 | -0.038778 | 50.2438
125 | -4.4219 | -1.9997 | 4.4224 | 1.9983 | 0.00046156 | -0.0013244 | 0.14033 | 0.14031 | 0.14033 | 0.99835 | -0.026275 | 0.99847 | -0.024911 | 38.7643
126 | 0.46606 | 0.22456 | -0.46606 | -0.22523 | 8.517e-06 | -0.00067317 | 0.014972 | 0.014981 | 0.014981 | 0.99747 | -0.040632 | 0.99746 | -0.040474 | 6.8094
127 | 3.4816 | 1.5594 | -3.4808 | -1.5603 | 0.00074795 | -0.0008645 | 0.11054 | 0.11055 | 0.11055 | 0.99629 | -0.038778 | 0.99609 | -0.037225 | 50.2497
128 | 3.3626 | 1.503 | -3.3619 | -1.5038 | 0.00062585 | -0.00078879 | 0.10674 | 0.10675 | 0.10675 | 0.99609 | -0.037225 | 0.99591 | -0.035887 | 48.5244
129 | 0.07401 | 0.033905 | -0.07401 | -0.035845 | 6.0879e-07 | -0.0019398 | 0.0023536 | 0.0023775 | 0.0023775 | 0.99847 | -0.024911 | 0.99846 | -0.024844 | 1.0807
130 | -4.4964 | -2.0322 | 4.4965 | 2.0319 | 0.00010538 | -0.0002901 | 0.14266 | 0.14266 | 0.14266 | 0.99847 | -0.024911 | 0.9985 | -0.024605 | 39.409
131 | -4.6205 | -2.092 | 4.6222 | 2.0939 | 0.0017611 | 0.0019024 | 0.14664 | 0.14664 | 0.14664 | 0.9985 | -0.024605 | 0.99897 | -0.012087 | 41.8961
132 | -4.7632 | -2.1622 | 4.7639 | 2.1606 | 0.00067024 | -0.0015927 | 0.15116 | 0.15114 | 0.15116 | 0.99897 | -0.012087 | 0.99913 | -0.010263 | 41.7573
133 | -4.7639 | -2.1606 | 4.7641 | 2.1601 | 0.00020904 | -0.00049702 | 0.15114 | 0.15113 | 0.15114 | 0.99913 | -0.010263 | 0.99918 | -0.0096927 | 41.7504
134 | -2.6546 | -1.177 | 2.6547 | 1.1769 | 6.8028e-05 | -0.00014942 | 0.084263 | 0.084261 | 0.084263 | 0.99484 | -0.036098 | 0.99486 | -0.036278 | 38.3013
135 | -0.12332 | -0.059726 | 0.12332 | 0.0597 | 6.3752e-07 | -2.6622e-05 | 0.0039658 | 0.0039654 | 0.0039658 | 0.9974 | -0.040682 | 0.99741 | -0.040648 | 1.8885
136 | -0.2852 | -0.1381 | 0.2852 | 0.13807 | 4.2734e-06 | -3.1191e-05 | 0.0091712 | 0.0091708 | 0.0091712 | 0.99741 | -0.040648 | 0.99742 | -0.040549 | 4.3673
137 | -0.39508 | -0.19128 | 0.39508 | 0.19089 | 3.5617e-06 | -0.00039175 | 0.012704 | 0.012699 | 0.012704 | 0.99742 | -0.040549 | 0.99743 | -0.040628 | 5.7746
138 | 0.39509 | 0.19086 | -0.39508 | -0.19089 | 9.1253e-06 | -3.2006e-05 | 0.012699 | 0.012699 | 0.012699 | 0.99746 | -0.040474 | 0.99743 | -0.040628 | 6.0472
139 | -0.084556 | -0.039527 | 0.084557 | 0.038596 | 3.846e-07 | -0.00093128 | 0.0027088 | 0.0026975 | 0.0027088 | 0.9947 | -0.035995 | 0.9947 | -0.036031 | 1.2313
140 | 0.084556 | 0.039527 | -0.084556 | -0.040115 | 2.4459e-07 | -0.0005882 | 0.0027088 | 0.0027161 | 0.0027161 | 0.9947 | -0.035995 | 0.9947 | -0.035972 | 1.2346
141 | -0.084557 | -0.038596 | 0.084557 | 0.038543 | 5.8378e-07 | -5.2836e-05 | 0.0026975 | 0.0026968 | 0.0026975 | 0.9947 | -0.036031 | 0.99471 | -0.035975 | 1.2845
142 | 0.084556 | 0.040115 | -0.084556 | -0.040952 | 3.5031e-07 | -0.00083695 | 0.0027161 | 0.0027266 | 0.0027266 | 0.9947 | -0.035972 | 0.99469 | -0.035937 | 1.2394
143 | -0.22485 | -0.10649 | 0.22485 | 0.10558 | 2.6738e-06 | -0.00090825 | 0.0072203 | 0.007209 | 0.0072203 | 0.99471 | -0.035975 | 0.99472 | -0.036073 | 3.2819
144 | -0.29615 | -0.14011 | 0.29617 | 0.14003 | 1.1876e-05 | -7.967e-05 | 0.0095079 | 0.0095069 | 0.0095079 | 0.99472 | -0.036073 | 0.99476 | -0.035785 | 4.5276
145 | 3.2401 | 1.4448 | -3.2397 | -1.4453 | 0.00041731 | -0.00057614 | 0.10283 | 0.10284 | 0.10284 | 0.99591 | -0.035887 | 0.99579 | -0.034968 | 46.7449
146 | 0.091482 | 0.038131 | -0.091481 | -0.041184 | 1.4383e-06 | -0.0030525 | 0.0028732 | 0.0029084 | 0.0029084 | 0.99579 | -0.034968 | 0.99578 | -0.034864 | 1.322
147 | 3.1482 | 1.4072 | -3.1466 | -1.4063 | 0.0015902 | 0.00089038 | 0.099967 | 0.099968 | 0.099968 | 0.99579 | -0.034968 | 0.99525 | -0.039296 | 47.6037
148 | 3.1466 | 1.4063 | -3.1453 | -1.4083 | 0.0013198 | -0.0019466 | 0.099968 | 0.099995 | 0.099995 | 0.99525 | -0.039296 | 0.99486 | -0.036278 | 45.4525
149 | 0.49055 | 0.2314 | -0.49052 | -0.23362 | 3.1272e-05 | -0.0022215 | 0.015738 | 0.015766 | 0.015766 | 0.99486 | -0.036278 | 0.9948 | -0.035749 | 7.1663
150 | 0.49052 | 0.23362 | -0.49051 | -0.23413 | 7.123e-06 | -0.00050488 | 0.015766 | 0.015772 | 0.015772 | 0.9948 | -0.035749 | 0.99479 | -0.035626 | 7.1692
151 | 0.091481 | 0.041184 | -0.09148 | -0.04363 | 1.1787e-06 | -0.0024461 | 0.0029084 | 0.0029382 | 0.0029382 | 0.99578 | -0.034864 | 0.99576 | -0.034762 | 1.3355
152 | 0.09148 | 0.04363 | -0.091479 | -0.044305 | 3.2995e-07 | -0.00067573 | 0.0029382 | 0.0029467 | 0.0029467 | 0.99576 | -0.034762 | 0.99576 | -0.034731 | 1.3394
153 | 0.42345 | 0.20165 | -0.42344 | -0.20168 | 9.561e-06 | -2.8234e-05 | 0.01361 | 0.013611 | 0.013611 | 0.99479 | -0.035626 | 0.99476 | -0.035785 | 6.4812
154 | -4.7641 | -2.1601 | 4.7646 | 2.159 | 0.00046121 | -0.0010971 | 0.15113 | 0.15111 | 0.15113 | 0.99918 | -0.0096927 | 0.99928 | -0.0084346 | 41.7483
155 | -0.43269 | -0.19302 | 0.4327 | 0.19298 | 1.5365e-05 | -4.4227e-05 | 0.013752 | 0.013751 | 0.013752 | 0.99456 | -0.060682 | 0.99459 | -0.060376 | 6.5486
156 | -0.13942 | -0.067522 | 0.13942 | 0.065368 | 2.5234e-06 | -0.0021547 | 0.0045304 | 0.0045032 | 0.0045304 | 0.98707 | -0.085398 | 0.98709 | -0.085551 | 2.0593
157 | -0.13942 | -0.065368 | 0.13942 | 0.064348 | 1.1833e-06 | -0.0010193 | 0.0045032 | 0.0044907 | 0.0045032 | 0.98709 | -0.085551 | 0.98709 | -0.085618 | 2.0469
158 | 0.1977 | 0.090637 | -0.19769 | -0.090853 | 1.3933e-05 | -0.00021608 | 0.0063599 | 0.0063627 | 0.0063627 | 0.98718 | -0.085167 | 0.98711 | -0.085725 | 3.0298
159 | 0.13942 | 0.062633 | -0.13942 | -0.064348 | 1.9771e-06 | -0.0017159 | 0.0044699 | 0.0044907 | 0.0044907 | 0.98711 | -0.085725 | 0.98709 | -0.085618 | 2.0412

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 10.3163 | 4.6183

## res_load
| p_mw | q_mvar
0 | 0.24673 | 0.1195
1 | 0.10003 | 0.048446
2 | 0.12729 | 0.061648
3 | 0.056043 | 0.027143
4 | 0.29378 | 0.14228
5 | 0.40659 | 0.19692
6 | 0.28558 | 0.13831
7 | 0.14693 | 0.071164
8 | 0.14659 | 0.070999
9 | 0.12144 | 0.058818
10 | 0.098966 | 0.047931
11 | 0.12854 | 0.062253
12 | 0.11008 | 0.053312
13 | 0.14876 | 0.07205
14 | 0.078434 | 0.037987
15 | 0.11592 | 0.05614
16 | 0.085729 | 0.041521
17 | 0.13206 | 0.063959
18 | 0.14228 | 0.068907
19 | 0.16465 | 0.079742
20 | 0.11257 | 0.054521
21 | 0.11312 | 0.054787
22 | 0.077674 | 0.037619
23 | 0.10883 | 0.052707
24 | 0.13044 | 0.063174
25 | 0.13227 | 0.064062
26 | 0.14341 | 0.069455
27 | 0.13242 | 0.064133
28 | 0.12972 | 0.062827
29 | 0.11664 | 0.056489
30 | 0.13915 | 0.067392
31 | 0.12524 | 0.060657
32 | 0.096529 | 0.046751
33 | 0.13064 | 0.063272
34 | 0.070898 | 0.034337
35 | 0.076539 | 0.037069
36 | 0.15773 | 0.076393
37 | 0.13134 | 0.06361
38 | 0.16465 | 0.079744
39 | 0.15267 | 0.07394
40 | 0.11397 | 0.055196
41 | 0.15333 | 0.074263
42 | 0.11906 | 0.057664
43 | 0.083361 | 0.040374
44 | 0.10039 | 0.048621
45 | 0.10368 | 0.050214
46 | 0.11257 | 0.054522
47 | 0.13305 | 0.064438
48 | 0.12805 | 0.062017
49 | 0.093795 | 0.045427
50 | 0.12223 | 0.0592
51 | 0.11937 | 0.057812
52 | 0.088403 | 0.042815
53 | 0.099727 | 0.0483
54 | 0.10967 | 0.053115
55 | 0.12476 | 0.060424
56 | 0.11593 | 0.056149
57 | 0.11384 | 0.055134
58 | 0.11218 | 0.054333
59 | 0.11828 | 0.057286
60 | 0.07401 | 0.035845
61 | 0.12395 | 0.060032
62 | 0.14101 | 0.068295
63 | 0.11853 | 0.057405
64 | 0.12233 | 0.059249
65 | 0.12332 | 0.059726
66 | 0.16188 | 0.078402
67 | 0.10987 | 0.053214
68 | 0.070966 | 0.03437
69 | 0.14029 | 0.067948
70 | 0.084556 | 0.040952
71 | 0.071299 | 0.034532
72 | 0.12187 | 0.059025
73 | 0.091479 | 0.044305
74 | 0.067061 | 0.032479
75 | 0.12727 | 0.061641
76 | 0.081319 | 0.039385
77 | 0.10887 | 0.05273
78 | 0.116 | 0.056179
79 | 0.13942 | 0.067522
80 | 0.14987 | 0.072583
81 | 0.058268 | 0.02822

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1