## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_105_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_105_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_105_0_node_5 | 20 | n |  | TRUE
3 | bus_MV_105_0_node_17 | 20 | n |  | TRUE
4 | bus_MV_105_0_node_8 | 20 | n |  | TRUE
5 | bus_MV_105_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_105_0_node_14 | 20 | n |  | TRUE
7 | bus_MV_105_0_node_10 | 20 | n |  | TRUE
8 | bus_MV_105_0_node_11 | 20 | n |  | TRUE
9 | bus_MV_105_0_node_9 | 20 | n |  | TRUE
10 | bus_MV_105_0_node_130 | 20 | n |  | TRUE
11 | bus_MV_105_0_node_12 | 20 | n |  | TRUE
12 | bus_MV_105_0_node_13 | 20 | n |  | TRUE
13 | bus_MV_105_0_node_111 | 20 | n |  | TRUE
14 | bus_MV_105_0_node_110 | 20 | n |  | TRUE
15 | bus_MV_105_0_node_112 | 20 | n |  | TRUE
16 | bus_MV_105_0_node_113 | 20 | n |  | TRUE
17 | bus_MV_105_0_node_101 | 20 | n |  | TRUE
18 | bus_MV_105_0_node_6 | 20 | n |  | TRUE
19 | bus_MV_105_0_node_7 | 20 | n |  | TRUE
20 | bus_MV_105_0_node_25 | 20 | n |  | TRUE
21 | bus_MV_105_0_node_102 | 20 | n |  | TRUE
22 | bus_MV_105_0_node_26 | 20 | n |  | TRUE
23 | bus_MV_105_0_node_34 | 20 | n |  | TRUE
24 | bus_MV_105_0_node_132 | 20 | n |  | TRUE
25 | bus_MV_105_0_node_24 | 20 | n |  | TRUE
26 | bus_MV_105_0_node_103 | 20 | n |  | TRUE
27 | bus_MV_105_0_node_27 | 20 | n |  | TRUE
28 | bus_MV_105_0_node_15 | 20 | n |  | TRUE
29 | bus_MV_105_0_node_16 | 20 | n |  | TRUE
30 | bus_MV_105_0_node_21 | 20 | n |  | TRUE
31 | bus_MV_105_0_node_91 | 20 | n |  | TRUE
32 | bus_MV_105_0_node_18 | 20 | n |  | TRUE
33 | bus_MV_105_0_node_19 | 20 | n |  | TRUE
34 | bus_MV_105_0_node_20 | 20 | n |  | TRUE
35 | bus_MV_105_0_node_128 | 20 | n |  | TRUE
36 | bus_MV_105_0_node_22 | 20 | n |  | TRUE
37 | bus_MV_105_0_node_100 | 20 | n |  | TRUE
38 | bus_MV_105_0_node_89 | 20 | n |  | TRUE
39 | bus_MV_105_0_node_28 | 20 | n |  | TRUE
40 | bus_MV_105_0_node_107 | 20 | n |  | TRUE
41 | bus_MV_105_0_node_108 | 20 | n |  | TRUE
42 | bus_MV_105_0_node_29 | 20 | n |  | TRUE
43 | bus_MV_105_0_node_30 | 20 | n |  | TRUE
44 | bus_MV_105_0_node_31 | 20 | n |  | TRUE
45 | bus_MV_105_0_node_32 | 20 | n |  | TRUE
46 | bus_MV_105_0_node_106 | 20 | n |  | TRUE
47 | bus_MV_105_0_node_105 | 20 | n |  | TRUE
48 | bus_MV_105_0_node_131 | 20 | n |  | TRUE
49 | bus_MV_105_0_node_116 | 20 | n |  | TRUE
50 | bus_MV_105_0_node_104 | 20 | n |  | TRUE
51 | bus_MV_105_0_node_115 | 20 | n |  | TRUE
52 | bus_MV_105_0_node_114 | 20 | n |  | TRUE
53 | bus_MV_105_0_node_85 | 20 | n |  | TRUE
54 | bus_MV_105_0_node_86 | 20 | n |  | TRUE
55 | bus_MV_105_0_node_87 | 20 | n |  | TRUE
56 | bus_MV_105_0_node_88 | 20 | n |  | TRUE
57 | bus_MV_105_0_node_90 | 20 | n |  | TRUE
58 | bus_MV_105_0_node_129 | 20 | n |  | TRUE
59 | bus_MV_105_0_node_95 | 20 | n |  | TRUE
60 | bus_MV_105_0_node_94 | 20 | n |  | TRUE
61 | bus_MV_105_0_node_97 | 20 | n |  | TRUE
62 | bus_MV_105_0_node_93 | 20 | n |  | TRUE
63 | bus_MV_105_0_node_98 | 20 | n |  | TRUE
64 | bus_MV_105_0_node_99 | 20 | n |  | TRUE
65 | bus_MV_105_0_node_109 | 20 | n |  | TRUE
66 | bus_HV_105_0_node_17 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_105_0_load_0 | 0 | 0.28262 | 0.13688 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_105_0_load_17 | 3 | 0.39251 | 0.1901 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_105_0_load_8 | 4 | 0.36257 | 0.1756 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_105_0_load_9 | 9 | 0.34431 | 0.16676 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_105_0_load_130 | 10 | 0.2737 | 0.13256 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_105_0_load_12 | 11 | 0.25018 | 0.12117 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_105_0_load_13 | 12 | 0.26196 | 0.12687 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_105_0_load_110 | 14 | 0.34587 | 0.16751 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_105_0_load_113 | 16 | 0.073301 | 0.035501 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_105_0_load_102 | 21 | 0.61032 | 0.29559 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_105_0_load_26 | 22 | 0.36276 | 0.17569 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_105_0_load_34 | 23 | 0.061703 | 0.029884 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_105_0_load_132 | 24 | 0.41515 | 0.20107 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_105_0_load_24 | 25 | 0.4003 | 0.19387 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_105_0_load_103 | 26 | 0.10409 | 0.050415 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_105_0_load_15 | 28 | 0.11457 | 0.05549 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_105_0_load_91 | 31 | 0.14493 | 0.070192 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_105_0_load_18 | 32 | 0.24572 | 0.11901 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_105_0_load_128 | 35 | 0.16845 | 0.081582 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_105_0_load_22 | 36 | 0.2388 | 0.11566 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_105_0_load_107 | 40 | 0.15592 | 0.075518 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_105_0_load_29 | 42 | 0.26464 | 0.12817 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_105_0_load_30 | 43 | 0.31575 | 0.15292 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_105_0_load_105 | 47 | 0.09805 | 0.047488 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_105_0_load_131 | 48 | 0.29107 | 0.14097 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_105_0_load_104 | 50 | 1.5135 | 0.73301 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_105_0_load_115 | 51 | 0.098699 | 0.047802 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_105_0_load_114 | 52 | 0.093161 | 0.04512 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_105_0_load_85 | 53 | 0.1787 | 0.086549 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_105_0_load_90 | 57 | 0.14519 | 0.070319 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_105_0_load_129 | 58 | 0.25017 | 0.12116 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_105_0_load_94 | 60 | 0.13903 | 0.067337 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_105_0_load_93 | 62 | 0.15408 | 0.074624 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_105_0_load_98 | 63 | 0.20409 | 0.098848 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_105_0_load_99 | 64 | 0.16243 | 0.078669 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_105_0_load_109 | 65 | 0.29869 | 0.14466 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_105_0_line_0 |  | 0 | 1 | 0.041086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_105_0_line_1 |  | 0 | 2 | 0.36062 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
2 | MV_105_0_line_2 |  | 0 | 3 | 0.12438 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
3 | MV_105_0_line_3 |  | 1 | 4 | 0.11903 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_105_0_line_4 |  | 2 | 7 | 0.35057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_105_0_line_5 |  | 2 | 8 | 0.38407 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
6 | MV_105_0_line_6 |  | 2 | 9 | 0.054715 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_105_0_line_7 |  | 3 | 5 | 0.039775 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_105_0_line_8 |  | 5 | 6 | 0.65823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_105_0_line_9 |  | 6 | 13 | 0.074108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_105_0_line_10 |  | 6 | 12 | 0.084676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_105_0_line_11 |  | 7 | 10 | 0.045057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_105_0_line_12 |  | 8 | 24 | 0.015758 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
13 | MV_105_0_line_13 |  | 11 | 12 | 0.06089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_105_0_line_14 |  | 13 | 15 | 0.10872 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_105_0_line_15 |  | 13 | 14 | 0.053893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_105_0_line_16 |  | 15 | 16 | 0.031171 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_105_0_line_17 |  | 16 | 17 | 1.0981 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_105_0_line_18 |  | 17 | 35 | 0.004211 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_105_0_line_19 |  | 17 | 37 | 0.99042 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_105_0_line_20 |  | 18 | 19 | 0.19687 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_105_0_line_21 |  | 18 | 20 | 0.22842 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
22 | MV_105_0_line_22 |  | 18 | 21 | 0.1287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_105_0_line_23 |  | 19 | 22 | 0.02713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_105_0_line_24 |  | 19 | 23 | 1.7303 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_105_0_line_25 |  | 20 | 25 | 0.012096 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
26 | MV_105_0_line_26 |  | 21 | 26 | 0.036568 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_105_0_line_27 |  | 22 | 27 | 0.057122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_105_0_line_28 |  | 24 | 25 | 0.33005 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
29 | MV_105_0_line_29 |  | 26 | 50 | 0.060878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_105_0_line_30 |  | 27 | 39 | 0.063053 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_105_0_line_31 |  | 28 | 29 | 0.077681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_105_0_line_32 |  | 29 | 30 | 0.50196 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_105_0_line_33 |  | 30 | 31 | 0.058411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_105_0_line_34 |  | 31 | 38 | 0.050492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_105_0_line_35 |  | 32 | 33 | 0.15944 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_105_0_line_36 |  | 33 | 34 | 0.35381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_105_0_line_37 |  | 33 | 35 | 0.68157 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_105_0_line_38 |  | 34 | 36 | 0.063708 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_105_0_line_39 |  | 37 | 64 | 0.030816 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_105_0_line_40 |  | 38 | 56 | 0.31233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_105_0_line_41 |  | 39 | 40 | 0.0096355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_105_0_line_42 |  | 40 | 41 | 0.022382 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_105_0_line_43 |  | 41 | 65 | 0.0015943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_105_0_line_44 |  | 42 | 43 | 0.020969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_105_0_line_45 |  | 42 | 44 | 0.11065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_105_0_line_46 |  | 44 | 45 | 0.13361 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_105_0_line_47 |  | 45 | 46 | 0.081815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_105_0_line_48 |  | 45 | 47 | 0.011565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_105_0_line_49 |  | 46 | 48 | 0.055049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_105_0_line_50 |  | 46 | 49 | 1.0342 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_105_0_line_51 |  | 47 | 50 | 0.011377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_105_0_line_52 |  | 49 | 52 | 0.11127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_105_0_line_53 |  | 51 | 52 | 0.017727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_105_0_line_54 |  | 53 | 54 | 0.059301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_105_0_line_55 |  | 54 | 55 | 0.034953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_105_0_line_56 |  | 54 | 56 | 0.035247 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_105_0_line_57 |  | 55 | 57 | 0.02606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_105_0_line_58 |  | 56 | 58 | 0.038275 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_105_0_line_59 |  | 57 | 59 | 0.061302 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_105_0_line_60 |  | 59 | 61 | 0.16359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_105_0_line_61 |  | 59 | 60 | 0.046707 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_105_0_line_62 |  | 61 | 63 | 0.084158 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_105_0_line_63 |  | 61 | 62 | 0.058277 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_105_0_line_64 |  | 63 | 64 | 0.018153 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_105_0_trafo_17 | 25 MVA 110/20 kV | 66 | 3 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2558513.4982 | 1128885.1443
1 | 2558548.3842 | 1128863.2822
2 | 2558697.568 | 1129195.2504
3 | 2558442.7673 | 1128987.4501
4 | 2558639.505 | 1128939.8624
5 | 2558466.5597 | 1129019.3247
6 | 2558343.8085 | 1129653.1056
7 | 2558655.1976 | 1129467.8352
8 | 2558880.0985 | 1128995.5903
9 | 2558665.046 | 1129239.2511
10 | 2558614.7959 | 1129447.6575
11 | 2558250.1332 | 1129559.2721
12 | 2558273.6852 | 1129605.6494
13 | 2558302.9502 | 1129714.9973
14 | 2558307.3919 | 1129675.3031
15 | 2558239.708 | 1129765.6052
16 | 2558214.6303 | 1129747.0956
17 | 2557147.3873 | 1129488.5255
18 | 2558944.7301 | 1128665.1261
19 | 2559106.1799 | 1128701.2144
20 | 2558727.5282 | 1128685.83
21 | 2559031.9697 | 1128570.5143
22 | 2559121.4276 | 1128678.7552
23 | 2560480.664 | 1129752.2751
24 | 2558866.052 | 1128988.3713
25 | 2558718.0707 | 1128693.3585
26 | 2559054.8492 | 1128542.0415
27 | 2559150.5156 | 1128629.5553
28 | 2555264.6128 | 1129547.8368
29 | 2555324.2318 | 1129592.3623
30 | 2555786.8518 | 1129397.5536
31 | 2555842.6401 | 1129410.6553
32 | 2556764.8958 | 1130161.533
33 | 2556708.6007 | 1130012.3604
34 | 2556547.7112 | 1129869.5998
35 | 2557143.3123 | 1129487.4206
36 | 2556584.8248 | 1129921.3813
37 | 2556388.1011 | 1129411.7505
38 | 2555892.5108 | 1129412.8101
39 | 2559094.1899 | 1128600.9002
40 | 2559085.5843 | 1128596.5658
41 | 2559065.595 | 1128586.4979
42 | 2559003.3802 | 1128349.556
43 | 2559006.982 | 1128370.2132
44 | 2559112.4333 | 1128333.9738
45 | 2559086.1257 | 1128464.9523
46 | 2559167.3993 | 1128474.3508
47 | 2559083.1708 | 1128476.1329
48 | 2559190.6053 | 1128424.4128
49 | 2559253.4221 | 1127682.8104
50 | 2559080.2637 | 1128487.1323
51 | 2559124.6217 | 1127689.9319
52 | 2559142.322 | 1127688.9532
53 | 2556052.572 | 1129368.0424
54 | 2556106.0705 | 1129389.6293
55 | 2556140.7268 | 1129384.3634
56 | 2556098.2647 | 1129410.4301
57 | 2556141.5325 | 1129410.4043
58 | 2556098.8284 | 1129448.7012
59 | 2556185.3738 | 1129453.2521
60 | 2556229.2412 | 1129440.7423
61 | 2556294.5753 | 1129500.5619
62 | 2556331.8048 | 1129545.397
63 | 2556360.8405 | 1129452.4296
64 | 2556370.9462 | 1129437.3496
65 | 2559066.4023 | 1128585.1231
66 | 2558442.7673 | 1128987.4501

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99921 | -0.026337 | 0.28262 | 0.13688
1 | 0.99919 | -0.026161 | 0 | 0
2 | 0.99677 | -0.087465 | 0 | 0
3 | 1 | 0 | -9.4953 | -4.4473
4 | 0.9991 | -0.026684 | 0.36257 | 0.1756
5 | 0.99976 | -0.0017779 | 0 | 0
6 | 0.99718 | 0.019479 | 0 | 0
7 | 0.99665 | -0.086427 | 0 | 0
8 | 0.99571 | -0.099068 | 0 | 0
9 | 0.99673 | -0.087694 | 0.34431 | 0.16676
10 | 0.99663 | -0.08628 | 0.2737 | 0.13256
11 | 0.99711 | 0.020168 | 0.25018 | 0.12117
12 | 0.99713 | 0.019988 | 0.26196 | 0.12687
13 | 0.99694 | 0.02148 | 0 | 0
14 | 0.99692 | 0.021702 | 0.34587 | 0.16751
15 | 0.99663 | 0.023989 | 0 | 0
16 | 0.99655 | 0.024711 | 0.073301 | 0.035501
17 | 0.992 | -0.0096382 | 0 | 0
18 | 0.99328 | -0.15166 | 0 | 0
19 | 0.99306 | -0.14967 | 0 | 0
20 | 0.99381 | -0.14583 | 0 | 0
21 | 0.99272 | -0.14671 | 0.61032 | 0.29559
22 | 0.99303 | -0.14941 | 0.36276 | 0.17569
23 | 0.99285 | -0.15113 | 0.061703 | 0.029884
24 | 0.99566 | -0.099542 | 0.41515 | 0.20107
25 | 0.99384 | -0.14552 | 0.4003 | 0.19387
26 | 0.99259 | -0.14557 | 0.10409 | 0.050415
27 | 0.993 | -0.1491 | 0 | 0
28 | 0.98927 | 0.009905 | 0.11457 | 0.05549
29 | 0.98928 | 0.0098008 | 0 | 0
30 | 0.98939 | 0.010603 | 0 | 0
31 | 0.9894 | 0.010533 | 0.14493 | 0.070192
32 | 0.99128 | -0.014677 | 0.24572 | 0.11901
33 | 0.99136 | -0.014194 | 0 | 0
34 | 0.99125 | -0.013262 | 0 | 0
35 | 0.99199 | -0.0096073 | 0.16845 | 0.081582
36 | 0.99122 | -0.01345 | 0.2388 | 0.11566
37 | 0.99011 | 0.0060837 | 0 | 0
38 | 0.98942 | 0.010387 | 0 | 0
39 | 0.99296 | -0.14876 | 0 | 0
40 | 0.99295 | -0.14871 | 0.15592 | 0.075518
41 | 0.99294 | -0.14863 | 0 | 0
42 | 0.99217 | -0.14182 | 0.26464 | 0.12817
43 | 0.99216 | -0.14174 | 0.31575 | 0.15292
44 | 0.99225 | -0.14258 | 0 | 0
45 | 0.99235 | -0.14349 | 0 | 0
46 | 0.9923 | -0.14316 | 0 | 0
47 | 0.99237 | -0.14361 | 0.09805 | 0.047488
48 | 0.99228 | -0.14297 | 0.29107 | 0.14097
49 | 0.99205 | -0.14177 | 0 | 0
50 | 0.99238 | -0.14374 | 1.5135 | 0.73301
51 | 0.99202 | -0.1415 | 0.098699 | 0.047802
52 | 0.99202 | -0.14152 | 0.093161 | 0.04512
53 | 0.98953 | 0.0095077 | 0.1787 | 0.086549
54 | 0.98954 | 0.0093808 | 0 | 0
55 | 0.98957 | 0.0091208 | 0 | 0
56 | 0.98952 | 0.0095712 | 0 | 0
57 | 0.9896 | 0.0089281 | 0.14519 | 0.070319
58 | 0.9895 | 0.009453 | 0.25017 | 0.12116
59 | 0.98969 | 0.0096438 | 0 | 0
60 | 0.98969 | 0.0097214 | 0.13903 | 0.067337
61 | 0.9899 | 0.0079028 | 0 | 0
62 | 0.98988 | 0.0077919 | 0.15408 | 0.074624
63 | 0.99002 | 0.0068653 | 0.20409 | 0.098848
64 | 0.99005 | 0.0065978 | 0.16243 | 0.078669
65 | 0.99294 | -0.14862 | 0.29869 | 0.14466
66 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.3626 | 0.1745 | -0.36259 | -0.17547 | 7.4211e-06 | -0.0009772 | 0.011626 | 0.011638 | 0.011638 | 0.99921 | -0.026337 | 0.99919 | -0.026161 | 5.29
1 | 5.7307 | 2.7028 | -5.7196 | -2.6905 | 0.011093 | 0.012237 | 0.18305 | 0.18306 | 0.18306 | 0.99921 | -0.026337 | 0.99677 | -0.087465 | 52.3019
2 | -6.3759 | -3.0141 | 6.3796 | 3.0193 | 0.0036803 | 0.0051676 | 0.20375 | 0.20375 | 0.20375 | 0.99921 | -0.026337 | 1 | 0 | 49.6947
3 | 0.36259 | 0.17547 | -0.36257 | -0.1756 | 2.8728e-05 | -0.00012386 | 0.011638 | 0.01164 | 0.01164 | 0.99919 | -0.026161 | 0.9991 | -0.026684 | 5.5427
4 | 0.27374 | 0.12318 | -0.2737 | -0.13149 | 3.5779e-05 | -0.0083046 | 0.0086934 | 0.008795 | 0.008795 | 0.99677 | -0.087465 | 0.99665 | -0.086427 | 3.9977
5 | 5.1015 | 2.4006 | -5.0966 | -2.4101 | 0.0049509 | -0.0094792 | 0.16329 | 0.16345 | 0.16345 | 0.99677 | -0.087465 | 0.99571 | -0.099068 | 45.1513
6 | 0.34432 | 0.1667 | -0.34431 | -0.16676 | 1.1967e-05 | -5.74e-05 | 0.011079 | 0.01108 | 0.01108 | 0.99677 | -0.087465 | 0.99673 | -0.087694 | 5.2762
7 | 3.1017 | 1.4175 | -3.101 | -1.4171 | 0.00068682 | 0.00038273 | 0.098445 | 0.098446 | 0.098446 | 1 | 0 | 0.99976 | -0.0017779 | 46.879
8 | 3.101 | 1.4171 | -3.0925 | -1.4302 | 0.0085327 | -0.013137 | 0.098446 | 0.098635 | 0.098635 | 0.99976 | -0.0017779 | 0.99718 | 0.019479 | 44.8342
9 | 2.5803 | 1.1856 | -2.5796 | -1.1872 | 0.00066875 | -0.0015607 | 0.082206 | 0.082227 | 0.082227 | 0.99718 | 0.019479 | 0.99694 | 0.02148 | 37.3759
10 | 0.51217 | 0.24459 | -0.51214 | -0.2466 | 3.0565e-05 | -0.0020012 | 0.016431 | 0.016456 | 0.016456 | 0.99718 | 0.019479 | 0.99713 | 0.019988 | 7.48
11 | 0.2737 | 0.13149 | -0.2737 | -0.13256 | 4.6599e-06 | -0.0010672 | 0.008795 | 0.0088084 | 0.0088084 | 0.99665 | -0.086427 | 0.99663 | -0.08628 | 4.0038
12 | 5.0966 | 2.4101 | -5.0964 | -2.4105 | 0.00020334 | -0.00038817 | 0.16345 | 0.16345 | 0.16345 | 0.99571 | -0.099068 | 0.99566 | -0.099542 | 45.1531
13 | -0.25018 | -0.12117 | 0.25018 | 0.11972 | 5.2529e-06 | -0.0014439 | 0.0080478 | 0.0080296 | 0.0080478 | 0.99711 | 0.020168 | 0.99713 | 0.019988 | 3.6581
14 | 2.2338 | 1.021 | -2.233 | -1.0233 | 0.00073437 | -0.0023613 | 0.071117 | 0.071148 | 0.071148 | 0.99694 | 0.02148 | 0.99663 | 0.023989 | 32.3399
15 | 0.34588 | 0.16624 | -0.34587 | -0.16751 | 8.8967e-06 | -0.0012762 | 0.011112 | 0.011128 | 0.011128 | 0.99694 | 0.02148 | 0.99692 | 0.021702 | 5.0583
16 | 2.233 | 1.0233 | -2.2328 | -1.024 | 0.00021067 | -0.00067668 | 0.071148 | 0.071157 | 0.071157 | 0.99663 | 0.023989 | 0.99655 | 0.024711 | 32.344
17 | 2.1595 | 0.9885 | -2.1502 | -0.98399 | 0.0092626 | 0.0045058 | 0.068798 | 0.068814 | 0.068814 | 0.99655 | 0.024711 | 0.992 | -0.0096382 | 32.7684
18 | 0.65332 | 0.30699 | -0.65331 | -0.30709 | 2.4807e-06 | -9.8204e-05 | 0.021006 | 0.021007 | 0.021007 | 0.992 | -0.0096382 | 0.99199 | -0.0096073 | 9.5488
19 | 1.4969 | 0.677 | -1.4939 | -0.69932 | 0.00304 | -0.022324 | 0.047809 | 0.048092 | 0.048092 | 0.992 | -0.0096382 | 0.99011 | 0.0060837 | 21.8599
20 | 0.87937 | 0.41492 | -0.87916 | -0.41949 | 0.00021031 | -0.0045742 | 0.028259 | 0.028317 | 0.028317 | 0.99328 | -0.15166 | 0.99306 | -0.14967 | 12.8712
21 | -4.2719 | -2.0147 | 4.274 | 2.0085 | 0.0020774 | -0.0062257 | 0.13727 | 0.13717 | 0.13727 | 0.99328 | -0.15166 | 0.99381 | -0.14583 | 37.9195
22 | 3.3925 | 1.5998 | -3.3905 | -1.6022 | 0.0020424 | -0.0024242 | 0.10901 | 0.10905 | 0.10905 | 0.99328 | -0.15166 | 0.99272 | -0.14671 | 49.5669
23 | 0.81744 | 0.39163 | -0.81742 | -0.39227 | 2.5153e-05 | -0.00063132 | 0.026349 | 0.026357 | 0.026357 | 0.99306 | -0.14967 | 0.99303 | -0.14941 | 11.9804
24 | 0.061715 | 0.027855 | -0.061703 | -0.029884 | 1.2094e-05 | -0.0020291 | 0.0019683 | 0.0019934 | 0.0019934 | 0.99306 | -0.14967 | 0.99285 | -0.15113 | 0.94923
25 | -4.274 | -2.0085 | 4.2741 | 2.0082 | 0.00010993 | -0.00032997 | 0.13717 | 0.13717 | 0.13717 | 0.99381 | -0.14583 | 0.99384 | -0.14552 | 37.8931
26 | 2.7802 | 1.3066 | -2.7798 | -1.3074 | 0.0003896 | -0.00074476 | 0.089329 | 0.089339 | 0.089339 | 0.99272 | -0.14671 | 0.99259 | -0.14557 | 40.6089
27 | 0.45466 | 0.21657 | -0.45464 | -0.21791 | 1.6363e-05 | -0.00134 | 0.01464 | 0.014657 | 0.014657 | 0.99303 | -0.14941 | 0.993 | -0.1491 | 6.6621
28 | 4.6812 | 2.2094 | -4.6744 | -2.202 | 0.0068247 | 0.0073956 | 0.15008 | 0.15009 | 0.15009 | 0.99566 | -0.099542 | 0.99384 | -0.14552 | 42.8818
29 | 2.6757 | 1.257 | -2.6751 | -1.2582 | 0.00060087 | -0.0012535 | 0.085976 | 0.085994 | 0.085994 | 0.99259 | -0.14557 | 0.99238 | -0.14374 | 39.088
30 | 0.45464 | 0.21791 | -0.45462 | -0.21939 | 1.8106e-05 | -0.001479 | 0.014657 | 0.014675 | 0.014675 | 0.993 | -0.1491 | 0.99296 | -0.14876 | 6.6706
31 | -0.11457 | -0.05549 | 0.11457 | 0.053675 | 1.4223e-06 | -0.0018147 | 0.0037148 | 0.003692 | 0.0037148 | 0.98927 | 0.009905 | 0.98928 | 0.0098008 | 1.6885
32 | -0.11457 | -0.053675 | 0.11459 | 0.053097 | 1.2167e-05 | -0.00057891 | 0.003692 | 0.0036848 | 0.003692 | 0.98928 | 0.0098008 | 0.98939 | 0.010603 | 1.7581
33 | -0.11459 | -0.053097 | 0.11459 | 0.051732 | 1.054e-06 | -0.0013649 | 0.0036848 | 0.0036682 | 0.0036848 | 0.98939 | 0.010603 | 0.9894 | 0.010533 | 1.6749
34 | -0.25952 | -0.12192 | 0.25952 | 0.12075 | 4.7094e-06 | -0.0011787 | 0.0083659 | 0.0083513 | 0.0083659 | 0.9894 | 0.010533 | 0.98942 | 0.010387 | 3.8027
35 | -0.24572 | -0.11901 | 0.24574 | 0.11883 | 1.7953e-05 | -0.00017581 | 0.0079509 | 0.0079485 | 0.0079509 | 0.99128 | -0.014677 | 0.99136 | -0.014194 | 3.7861
36 | 0.23883 | 0.10729 | -0.23881 | -0.11559 | 2.782e-05 | -0.008293 | 0.0076242 | 0.0077264 | 0.0077264 | 0.99136 | -0.014194 | 0.99125 | -0.013262 | 3.512
37 | -0.48457 | -0.22613 | 0.48487 | 0.22551 | 0.00029425 | -0.00061586 | 0.015571 | 0.015561 | 0.015571 | 0.99136 | -0.014194 | 0.99199 | -0.0096073 | 7.4148
38 | 0.23881 | 0.11559 | -0.2388 | -0.11566 | 6.777e-06 | -7.0483e-05 | 0.0077264 | 0.0077274 | 0.0077274 | 0.99125 | -0.013262 | 0.99122 | -0.01345 | 3.6797
39 | 1.4939 | 0.69932 | -1.4938 | -0.70002 | 9.5165e-05 | -0.000693 | 0.048092 | 0.048101 | 0.048101 | 0.99011 | 0.0060837 | 0.99005 | 0.0065978 | 21.864
40 | -0.25952 | -0.12075 | 0.25955 | 0.11345 | 2.8773e-05 | -0.0072925 | 0.0083513 | 0.0082637 | 0.0083513 | 0.98942 | 0.010387 | 0.98952 | 0.0095712 | 3.796
41 | 0.45462 | 0.21939 | -0.45462 | -0.21962 | 2.7709e-06 | -0.00022601 | 0.014675 | 0.014678 | 0.014678 | 0.99296 | -0.14876 | 0.99295 | -0.14871 | 6.6719
42 | 0.2987 | 0.1441 | -0.29869 | -0.14463 | 2.7795e-06 | -0.00052605 | 0.0096415 | 0.0096482 | 0.0096482 | 0.99295 | -0.14871 | 0.99294 | -0.14863 | 4.3855
43 | 0.29869 | 0.14463 | -0.29869 | -0.14466 | 1.9817e-07 | -3.7473e-05 | 0.0096482 | 0.0096486 | 0.0096486 | 0.99294 | -0.14863 | 0.99294 | -0.14862 | 4.3857
44 | 0.31575 | 0.15243 | -0.31575 | -0.15292 | 2.915e-06 | -0.00049198 | 0.010201 | 0.010208 | 0.010208 | 0.99217 | -0.14182 | 0.99216 | -0.14174 | 4.6398
45 | -0.58039 | -0.2806 | 0.58044 | 0.27801 | 5.1875e-05 | -0.0025854 | 0.018757 | 0.018724 | 0.018757 | 0.99217 | -0.14182 | 0.99225 | -0.14258 | 8.5257
46 | -0.58044 | -0.27801 | 0.5805 | 0.27489 | 6.2402e-05 | -0.0031227 | 0.018724 | 0.018684 | 0.018724 | 0.99225 | -0.14258 | 0.99235 | -0.14349 | 8.5108
47 | 0.48302 | 0.20336 | -0.48299 | -0.20528 | 2.5423e-05 | -0.001916 | 0.015246 | 0.015267 | 0.015267 | 0.99235 | -0.14349 | 0.9923 | -0.14316 | 6.9397
48 | -1.0635 | -0.47825 | 1.0635 | 0.47799 | 1.7764e-05 | -0.00026664 | 0.033922 | 0.033919 | 0.033922 | 0.99235 | -0.14349 | 0.99237 | -0.14361 | 15.4191
49 | 0.29107 | 0.13968 | -0.29107 | -0.14097 | 6.4942e-06 | -0.0012922 | 0.0093923 | 0.0094086 | 0.0094086 | 0.9923 | -0.14316 | 0.99228 | -0.14297 | 4.2767
50 | 0.19192 | 0.065601 | -0.19187 | -0.089893 | 5.01e-05 | -0.024292 | 0.0059003 | 0.0061655 | 0.0061655 | 0.9923 | -0.14316 | 0.99205 | -0.14177 | 2.8025
51 | -1.1616 | -0.52548 | 1.1616 | 0.52521 | 2.0889e-05 | -0.00026132 | 0.037087 | 0.037083 | 0.037087 | 0.99237 | -0.14361 | 0.99238 | -0.14374 | 16.8576
52 | 0.19187 | 0.089893 | -0.19186 | -0.092506 | 5.6764e-06 | -0.0026129 | 0.0061655 | 0.0061981 | 0.0061981 | 0.99205 | -0.14177 | 0.99202 | -0.14152 | 2.8173
53 | -0.098699 | -0.047802 | 0.0987 | 0.047386 | 2.4062e-07 | -0.00041646 | 0.0031912 | 0.003186 | 0.0031912 | 0.99202 | -0.1415 | 0.99202 | -0.14152 | 1.4506
54 | -0.1787 | -0.086549 | 0.1787 | 0.085163 | 2.6482e-06 | -0.0013856 | 0.0057925 | 0.005775 | 0.0057925 | 0.98953 | 0.0095077 | 0.98954 | 0.0093808 | 2.633
55 | -0.68844 | -0.31892 | 0.68846 | 0.31811 | 2.285e-05 | -0.00081042 | 0.022134 | 0.022124 | 0.022134 | 0.98954 | 0.0093808 | 0.98957 | 0.0091208 | 10.0608
56 | 0.50974 | 0.23375 | -0.50972 | -0.23457 | 1.2601e-05 | -0.0008203 | 0.016359 | 0.016369 | 0.016369 | 0.98954 | 0.0093808 | 0.98952 | 0.0095712 | 7.4406
57 | -0.68846 | -0.31811 | 0.68848 | 0.3175 | 1.7023e-05 | -0.00060427 | 0.022124 | 0.022116 | 0.022124 | 0.98957 | 0.0091208 | 0.9896 | 0.0089281 | 10.0563
58 | 0.25017 | 0.12112 | -0.25017 | -0.12116 | 4.4842e-06 | -4.1931e-05 | 0.0081087 | 0.0081093 | 0.0081093 | 0.98952 | 0.0095712 | 0.9895 | 0.009453 | 3.8616
59 | -0.83367 | -0.38782 | 0.83375 | 0.3878 | 7.8572e-05 | -2.246e-05 | 0.026822 | 0.026821 | 0.026822 | 0.9896 | 0.0089281 | 0.98969 | 0.0096438 | 12.7722
60 | -0.97278 | -0.45404 | 0.973 | 0.45028 | 0.00021381 | -0.0037631 | 0.031313 | 0.031266 | 0.031313 | 0.98969 | 0.0096438 | 0.9899 | 0.0079028 | 14.2331
61 | 0.13903 | 0.066245 | -0.13903 | -0.067337 | 1.2621e-06 | -0.0010919 | 0.0044922 | 0.004506 | 0.004506 | 0.98969 | 0.0096438 | 0.98969 | 0.0097214 | 2.0482
62 | -1.1271 | -0.52484 | 1.1272 | 0.52291 | 0.00014759 | -0.0019254 | 0.036257 | 0.036233 | 0.036257 | 0.9899 | 0.0079028 | 0.99002 | 0.0068653 | 16.4804
63 | 0.15408 | 0.074558 | -0.15408 | -0.074624 | 2.5877e-06 | -6.6551e-05 | 0.0049918 | 0.0049926 | 0.0049926 | 0.9899 | 0.0079028 | 0.98988 | 0.0077919 | 2.3774
64 | -1.3313 | -0.62176 | 1.3314 | 0.62135 | 4.4479e-05 | -0.00041163 | 0.042844 | 0.042839 | 0.042844 | 0.99002 | 0.0068653 | 0.99005 | 0.0065978 | 19.4746

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 9.8878 | 4.6374

## res_load
| p_mw | q_mvar
0 | 0.28262 | 0.13688
1 | 0.39251 | 0.1901
2 | 0.36257 | 0.1756
3 | 0.34431 | 0.16676
4 | 0.2737 | 0.13256
5 | 0.25018 | 0.12117
6 | 0.26196 | 0.12687
7 | 0.34587 | 0.16751
8 | 0.073301 | 0.035501
9 | 0.61032 | 0.29559
10 | 0.36276 | 0.17569
11 | 0.061703 | 0.029884
12 | 0.41515 | 0.20107
13 | 0.4003 | 0.19387
14 | 0.10409 | 0.050415
15 | 0.11457 | 0.05549
16 | 0.14493 | 0.070192
17 | 0.24572 | 0.11901
18 | 0.16845 | 0.081582
19 | 0.2388 | 0.11566
20 | 0.15592 | 0.075518
21 | 0.26464 | 0.12817
22 | 0.31575 | 0.15292
23 | 0.09805 | 0.047488
24 | 0.29107 | 0.14097
25 | 1.5135 | 0.73301
26 | 0.098699 | 0.047802
27 | 0.093161 | 0.04512
28 | 0.1787 | 0.086549
29 | 0.14519 | 0.070319
30 | 0.25017 | 0.12116
31 | 0.13903 | 0.067337
32 | 0.15408 | 0.074624
33 | 0.20409 | 0.098848
34 | 0.16243 | 0.078669
35 | 0.29869 | 0.14466

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1