## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_107_1_node_9 | 20 | n |  | TRUE
1 | bus_MV_107_1_node_10 | 20 | n |  | TRUE
2 | bus_MV_107_1_node_151 | 20 | n |  | TRUE
3 | bus_MV_107_1_node_15 | 20 | n |  | TRUE
4 | bus_MV_107_1_node_16 | 20 | n |  | TRUE
5 | bus_MV_107_1_node_18 | 20 | n |  | TRUE
6 | bus_MV_107_1_node_197 | 20 | n |  | TRUE
7 | bus_MV_107_1_node_170 | 20 | n |  | TRUE
8 | bus_MV_107_1_node_21 | 20 | n |  | TRUE
9 | bus_MV_107_1_node_20 | 20 | n |  | TRUE
10 | bus_MV_107_1_node_19 | 20 | n |  | TRUE
11 | bus_MV_107_1_node_41 | 20 | n |  | TRUE
12 | bus_MV_107_1_node_149 | 20 | n |  | TRUE
13 | bus_MV_107_1_node_145 | 20 | n |  | TRUE
14 | bus_MV_107_1_node_51 | 20 | n |  | TRUE
15 | bus_MV_107_1_node_146 | 20 | n |  | TRUE
16 | bus_MV_107_1_node_147 | 20 | n |  | TRUE
17 | bus_MV_107_1_node_148 | 20 | n |  | TRUE
18 | bus_MV_107_1_node_169 | 20 | n |  | TRUE
19 | bus_MV_107_1_node_171 | 20 | n |  | TRUE
20 | bus_MV_107_1_node_150 | 20 | n |  | TRUE
21 | bus_MV_107_1_node_29 | 20 | n |  | TRUE
22 | bus_MV_107_1_node_173 | 20 | n |  | TRUE
23 | bus_MV_107_1_node_184 | 20 | n |  | TRUE
24 | bus_MV_107_1_node_43 | 20 | n |  | TRUE
25 | bus_MV_107_1_node_185 | 20 | n |  | TRUE
26 | bus_MV_107_1_node_55 | 20 | n |  | TRUE
27 | bus_MV_107_1_node_186 | 20 | n |  | TRUE
28 | bus_MV_107_1_node_63 | 20 | n |  | TRUE
29 | bus_MV_107_1_node_42 | 20 | n |  | TRUE
30 | bus_MV_107_1_node_60 | 20 | n |  | TRUE
31 | bus_MV_107_1_node_44 | 20 | n |  | TRUE
32 | bus_MV_107_1_node_58 | 20 | n |  | TRUE
33 | bus_MV_107_1_node_48 | 20 | n |  | TRUE
34 | bus_MV_107_1_node_45 | 20 | n |  | TRUE
35 | bus_MV_107_1_node_46 | 20 | n |  | TRUE
36 | bus_MV_107_1_node_47 | 20 | n |  | TRUE
37 | bus_MV_107_1_node_80 | 20 | n |  | TRUE
38 | bus_MV_107_1_node_79 | 20 | n |  | TRUE
39 | bus_MV_107_1_node_72 | 20 | n |  | TRUE
40 | bus_MV_107_1_node_49 | 20 | n |  | TRUE
41 | bus_MV_107_1_node_50 | 20 | n |  | TRUE
42 | bus_MV_107_1_node_52 | 20 | n |  | TRUE
43 | bus_MV_107_1_node_53 | 20 | n |  | TRUE
44 | bus_MV_107_1_node_65 | 20 | n |  | TRUE
45 | bus_MV_107_1_node_62 | 20 | n |  | TRUE
46 | bus_MV_107_1_node_54 | 20 | n |  | TRUE
47 | bus_MV_107_1_node_56 | 20 | n |  | TRUE
48 | bus_MV_107_1_node_57 | 20 | n |  | TRUE
49 | bus_MV_107_1_node_59 | 20 | n |  | TRUE
50 | bus_MV_107_1_node_61 | 20 | n |  | TRUE
51 | bus_MV_107_1_node_64 | 20 | n |  | TRUE
52 | bus_MV_107_1_node_192 | 20 | n |  | TRUE
53 | bus_MV_107_1_node_67 | 20 | n |  | TRUE
54 | bus_MV_107_1_node_68 | 20 | n |  | TRUE
55 | bus_MV_107_1_node_69 | 20 | n |  | TRUE
56 | bus_MV_107_1_node_70 | 20 | n |  | TRUE
57 | bus_MV_107_1_node_71 | 20 | n |  | TRUE
58 | bus_MV_107_1_node_74 | 20 | n |  | TRUE
59 | bus_MV_107_1_node_73 | 20 | n |  | TRUE
60 | bus_MV_107_1_node_182 | 20 | n |  | TRUE
61 | bus_MV_107_1_node_191 | 20 | n |  | TRUE
62 | bus_MV_107_1_node_75 | 20 | n |  | TRUE
63 | bus_MV_107_1_node_81 | 20 | n |  | TRUE
64 | bus_MV_107_1_node_82 | 20 | n |  | TRUE
65 | bus_MV_107_1_node_76 | 20 | n |  | TRUE
66 | bus_MV_107_1_node_77 | 20 | n |  | TRUE
67 | bus_MV_107_1_node_78 | 20 | n |  | TRUE
68 | bus_MV_107_1_node_123 | 20 | n |  | TRUE
69 | bus_MV_107_1_node_172 | 20 | n |  | TRUE
70 | bus_HV_107_1_node_19 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_107_1_load_9 | 0 | 0.069966 | 0.033886 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_107_1_load_151 | 2 | 0.28666 | 0.13883 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_107_1_load_15 | 3 | 0.091264 | 0.044201 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_107_1_load_197 | 6 | 0.22323 | 0.10811 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_107_1_load_20 | 9 | 0.18245 | 0.088364 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_107_1_load_41 | 11 | 0.22195 | 0.10749 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_107_1_load_149 | 12 | 0.09351 | 0.045289 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_107_1_load_145 | 13 | 0.22321 | 0.10811 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_107_1_load_146 | 15 | 0.10731 | 0.051973 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_107_1_load_171 | 19 | 0.40242 | 0.1949 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_107_1_load_29 | 21 | 0.075183 | 0.036413 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_107_1_load_173 | 22 | 0.067518 | 0.0327 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_107_1_load_184 | 23 | 0.12218 | 0.059176 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_107_1_load_185 | 25 | 0.22823 | 0.11053 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_107_1_load_186 | 27 | 0.22729 | 0.11008 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_107_1_load_44 | 31 | 0.34805 | 0.16857 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_107_1_load_45 | 34 | 0.16496 | 0.079892 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_107_1_load_79 | 38 | 0.11969 | 0.057967 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_107_1_load_72 | 39 | 0.1853 | 0.089745 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_107_1_load_49 | 40 | 0.24235 | 0.11737 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_107_1_load_65 | 44 | 0.27322 | 0.13233 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_107_1_load_54 | 46 | 0.19384 | 0.093882 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_107_1_load_56 | 47 | 0.33521 | 0.16235 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_107_1_load_59 | 49 | 0.40852 | 0.19786 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_107_1_load_61 | 50 | 0.26578 | 0.12872 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_107_1_load_192 | 52 | 0.39756 | 0.19255 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_107_1_load_67 | 53 | 0.37324 | 0.18077 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_107_1_load_73 | 59 | 0.22747 | 0.11017 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_107_1_load_182 | 60 | 0.29503 | 0.14289 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_107_1_load_191 | 61 | 0.27314 | 0.13229 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_107_1_load_81 | 63 | 0.16304 | 0.078963 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_107_1_load_82 | 64 | 0.23599 | 0.1143 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_107_1_load_76 | 65 | 0.22917 | 0.11099 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_107_1_load_172 | 69 | 0.2379 | 0.11522 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_107_1_line_0 |  | 0 | 1 | 0.057161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_107_1_line_1 |  | 1 | 2 | 10.7375 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_107_1_line_2 |  | 2 | 20 | 0.07831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_107_1_line_3 |  | 3 | 4 | 0.166 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_107_1_line_4 |  | 4 | 5 | 0.99682 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_107_1_line_5 |  | 4 | 6 | 0.82529 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_107_1_line_6 |  | 4 | 7 | 1.0457 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_107_1_line_7 |  | 5 | 8 | 0.41836 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_107_1_line_8 |  | 5 | 9 | 0.052846 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_107_1_line_9 |  | 6 | 10 | 0.090193 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_107_1_line_10 |  | 7 | 22 | 0.19226 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_107_1_line_11 |  | 7 | 18 | 1.0252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_107_1_line_12 |  | 8 | 12 | 0.067987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_107_1_line_13 |  | 10 | 11 | 1.1627 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
14 | MV_107_1_line_14 |  | 11 | 29 | 0.068387 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
15 | MV_107_1_line_15 |  | 12 | 20 | 0.02339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_107_1_line_16 |  | 13 | 14 | 0.042962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_107_1_line_17 |  | 14 | 42 | 0.32303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_107_1_line_18 |  | 15 | 16 | 0.045793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_107_1_line_19 |  | 16 | 17 | 0.87678 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_107_1_line_20 |  | 17 | 18 | 0.38575 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_107_1_line_21 |  | 17 | 19 | 0.048036 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_107_1_line_22 |  | 18 | 68 | 0.15274 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_107_1_line_23 |  | 21 | 22 | 3.0479 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_107_1_line_24 |  | 23 | 24 | 0.039232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_107_1_line_25 |  | 23 | 25 | 0.19402 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_107_1_line_26 |  | 24 | 30 | 0.87285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_107_1_line_27 |  | 24 | 29 | 0.15228 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
28 | MV_107_1_line_28 |  | 25 | 26 | 0.033662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_107_1_line_29 |  | 26 | 43 | 0.2891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_107_1_line_30 |  | 27 | 28 | 0.020366 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_107_1_line_31 |  | 28 | 51 | 0.27304 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_107_1_line_32 |  | 28 | 45 | 0.26589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_107_1_line_33 |  | 30 | 49 | 0.00684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_107_1_line_34 |  | 31 | 32 | 0.18978 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_107_1_line_35 |  | 31 | 33 | 0.2996 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_107_1_line_36 |  | 32 | 49 | 0.01298 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_107_1_line_37 |  | 32 | 48 | 0.33845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_107_1_line_38 |  | 33 | 39 | 0.058099 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_107_1_line_39 |  | 34 | 35 | 0.078037 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_107_1_line_40 |  | 35 | 36 | 0.10965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_107_1_line_41 |  | 36 | 37 | 0.2096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_107_1_line_42 |  | 36 | 38 | 0.004801 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_107_1_line_43 |  | 37 | 63 | 0.092179 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_107_1_line_44 |  | 39 | 59 | 0.28975 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_107_1_line_45 |  | 40 | 41 | 0.055768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_107_1_line_46 |  | 41 | 42 | 0.40894 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_107_1_line_47 |  | 41 | 43 | 0.37685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_107_1_line_48 |  | 42 | 44 | 0.057077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_107_1_line_49 |  | 42 | 45 | 0.21333 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_107_1_line_50 |  | 43 | 46 | 0.039489 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_107_1_line_51 |  | 45 | 50 | 0.044006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_107_1_line_52 |  | 47 | 48 | 0.001025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_107_1_line_53 |  | 51 | 52 | 0.052959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_107_1_line_54 |  | 53 | 54 | 0.028693 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_107_1_line_55 |  | 53 | 55 | 0.037932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_107_1_line_56 |  | 54 | 56 | 0.19445 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_107_1_line_57 |  | 55 | 57 | 0.20867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_107_1_line_58 |  | 56 | 58 | 0.25737 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_107_1_line_59 |  | 56 | 59 | 0.004733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_107_1_line_60 |  | 57 | 60 | 0.093278 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_107_1_line_61 |  | 57 | 61 | 0.22047 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_107_1_line_62 |  | 58 | 62 | 0.093732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_107_1_line_63 |  | 58 | 63 | 0.061342 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_107_1_line_64 |  | 61 | 67 | 0.06823 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_107_1_line_65 |  | 62 | 64 | 0.089423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_107_1_line_66 |  | 65 | 66 | 0.08311 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_107_1_line_67 |  | 66 | 67 | 0.21024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_107_1_line_68 |  | 68 | 69 | 0.068371 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_107_1_trafo_19 | 25 MVA 110/20 kV | 70 | 10 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2629422.9147 | 1181806.4903
1 | 2629397.7672 | 1181757.0413
2 | 2619471.4968 | 1177662.7161
3 | 2618040.8401 | 1177961.4205
4 | 2618156.7204 | 1178080.2855
5 | 2618923.9405 | 1177696.1083
6 | 2617709.6698 | 1177386.5649
7 | 2618125.8724 | 1179125.5508
8 | 2619321.2697 | 1177629.9928
9 | 2618963.5518 | 1177662.249
10 | 2617623.3133 | 1177412.5914
11 | 2616718.5059 | 1176682.3708
12 | 2619387.9475 | 1177640.1382
13 | 2616016.1389 | 1177661.7171
14 | 2616049.8982 | 1177635.6492
15 | 2616668.7482 | 1178657.7409
16 | 2616713.7057 | 1178665.9271
17 | 2617184.2244 | 1179127.8001
18 | 2617532.4988 | 1179185.6345
19 | 2617138.3103 | 1179141.9209
20 | 2619409.1173 | 1177649.9747
21 | 2621132.3636 | 1180284.0158
22 | 2618317.8128 | 1179114.4598
23 | 2616541.2117 | 1176648.3638
24 | 2616579.2505 | 1176641.954
25 | 2616441.5809 | 1176814.8536
26 | 2616411.2659 | 1176800.2079
27 | 2615703.3957 | 1177157.5137
28 | 2615712.2888 | 1177175.8351
29 | 2616668.0494 | 1176724.2523
30 | 2616845.4392 | 1176166.0946
31 | 2616944.3526 | 1175993.4508
32 | 2616860.892 | 1176163.8923
33 | 2617165.2626 | 1175791.0734
34 | 2617351.7025 | 1176141.4087
35 | 2617399.9845 | 1176080.428
36 | 2617482.8894 | 1176148.9921
37 | 2617518.3228 | 1175949.4489
38 | 2617486.5187 | 1176152.0486
39 | 2617223.3614 | 1175790.9837
40 | 2616313.0438 | 1177261.1985
41 | 2616261.2887 | 1177240.7369
42 | 2616013.319 | 1177432.07
43 | 2616319.495 | 1176967.5216
44 | 2616050.7849 | 1177389.1368
45 | 2615810.8909 | 1177364.7563
46 | 2616293.7487 | 1176995.8552
47 | 2616910.4255 | 1176357.4188
48 | 2616911.2907 | 1176356.8654
49 | 2616848.5288 | 1176159.989
50 | 2615780.6051 | 1177333.4995
51 | 2615831.5472 | 1177073.7287
52 | 2615873.6551 | 1177041.4675
53 | 2617603.5365 | 1175599.986
54 | 2617624.7907 | 1175619.3247
55 | 2617625.3893 | 1175568.9452
56 | 2617513.6421 | 1175748.266
57 | 2617691.9213 | 1175524.6956
58 | 2617653.2526 | 1175886.2552
59 | 2617509.5752 | 1175745.8307
60 | 2617774.3539 | 1175568.3495
61 | 2617851.1219 | 1175372.1767
62 | 2617737.6792 | 1175845.6716
63 | 2617603.3895 | 1175921.983
64 | 2617782.3662 | 1175893.7057
65 | 2618157.6945 | 1175400.2967
66 | 2618079.3363 | 1175427.9972
67 | 2617893.9006 | 1175425.3308
68 | 2617638.56 | 1179295.5453
69 | 2617691.88 | 1179259.4389
70 | 2617623.3133 | 1177412.5914

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99468 | -0.03618 | 0.069966 | 0.033886
1 | 0.99469 | -0.036226 | 0 | 0
2 | 0.99607 | -0.019972 | 0.28666 | 0.13883
3 | 0.99716 | -0.027411 | 0.091264 | 0.044201
4 | 0.99719 | -0.027225 | 0 | 0
5 | 0.99639 | -0.022256 | 0 | 0
6 | 0.99969 | -0.0028987 | 0.22323 | 0.10811
7 | 0.99543 | -0.04409 | 0 | 0
8 | 0.99616 | -0.020604 | 0 | 0
9 | 0.99638 | -0.022142 | 0.18245 | 0.088364
10 | 1 | 0 | -7.6831 | -3.5011
11 | 0.99207 | -0.20282 | 0.22195 | 0.10749
12 | 0.99612 | -0.02031 | 0.09351 | 0.045289
13 | 0.98815 | -0.19565 | 0.22321 | 0.10811
14 | 0.98816 | -0.19576 | 0 | 0
15 | 0.9941 | -0.035511 | 0.10731 | 0.051973
16 | 0.9941 | -0.035569 | 0 | 0
17 | 0.99422 | -0.036062 | 0 | 0
18 | 0.99447 | -0.037785 | 0 | 0
19 | 0.99418 | -0.036298 | 0.40242 | 0.1949
20 | 0.99611 | -0.020234 | 0 | 0
21 | 0.99494 | -0.047753 | 0.075183 | 0.036413
22 | 0.99538 | -0.044486 | 0.067518 | 0.0327
23 | 0.99129 | -0.20956 | 0.12218 | 0.059176
24 | 0.9914 | -0.21046 | 0 | 0
25 | 0.99052 | -0.21537 | 0.22823 | 0.11053
26 | 0.99044 | -0.21474 | 0 | 0
27 | 0.98767 | -0.19739 | 0.22729 | 0.11008
28 | 0.98767 | -0.19733 | 0 | 0
29 | 0.99186 | -0.20519 | 0 | 0
30 | 0.98763 | -0.17775 | 0 | 0
31 | 0.98658 | -0.18386 | 0.34805 | 0.16857
32 | 0.98755 | -0.17705 | 0 | 0
33 | 0.98525 | -0.19332 | 0 | 0
34 | 0.98338 | -0.20085 | 0.16496 | 0.079892
35 | 0.9834 | -0.201 | 0 | 0
36 | 0.98342 | -0.2012 | 0 | 0
37 | 0.9835 | -0.20184 | 0 | 0
38 | 0.98342 | -0.20119 | 0.11969 | 0.057967
39 | 0.985 | -0.19516 | 0.1853 | 0.089745
40 | 0.98897 | -0.20254 | 0.24235 | 0.11737
41 | 0.98898 | -0.2027 | 0 | 0
42 | 0.98826 | -0.19655 | 0 | 0
43 | 0.98977 | -0.20922 | 0 | 0
44 | 0.98824 | -0.19636 | 0.27322 | 0.13233
45 | 0.98789 | -0.19918 | 0 | 0
46 | 0.98976 | -0.20913 | 0.19384 | 0.093882
47 | 0.9874 | -0.17574 | 0.33521 | 0.16235
48 | 0.9874 | -0.17575 | 0 | 0
49 | 0.9876 | -0.17748 | 0.40852 | 0.19786
50 | 0.98787 | -0.19904 | 0.26578 | 0.12872
51 | 0.98753 | -0.19608 | 0 | 0
52 | 0.98751 | -0.19582 | 0.39756 | 0.19255
53 | 0.98347 | -0.20053 | 0.37324 | 0.18077
54 | 0.98352 | -0.20092 | 0 | 0
55 | 0.98343 | -0.20018 | 0 | 0
56 | 0.98381 | -0.20356 | 0 | 0
57 | 0.98322 | -0.19823 | 0 | 0
58 | 0.98358 | -0.2017 | 0 | 0
59 | 0.98382 | -0.20366 | 0.22747 | 0.11017
60 | 0.98316 | -0.19858 | 0.29503 | 0.14289
61 | 0.983 | -0.19972 | 0.27314 | 0.13229
62 | 0.98356 | -0.20145 | 0 | 0
63 | 0.98353 | -0.20211 | 0.16304 | 0.078963
64 | 0.98353 | -0.20119 | 0.23599 | 0.1143
65 | 0.98287 | -0.19962 | 0.22917 | 0.11099
66 | 0.98291 | -0.19938 | 0 | 0
67 | 0.98297 | -0.19994 | 0 | 0
68 | 0.9944 | -0.038252 | 0 | 0
69 | 0.99438 | -0.038059 | 0.2379 | 0.11522
70 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.069966 | -0.033886 | 0.069966 | 0.032536 | 3.8552e-07 | -0.0013502 | 0.0022561 | 0.0022393 | 0.0022561 | 0.99468 | -0.03618 | 0.99469 | -0.036226 | 1.0255
1 | -0.069966 | -0.032536 | 0.070056 | 0.019892 | 8.9934e-05 | -0.012644 | 0.0022393 | 0.0021106 | 0.0022393 | 0.99469 | -0.036226 | 0.99607 | -0.019972 | 1.0664
2 | -0.35671 | -0.15873 | 0.35672 | 0.15687 | 1.3359e-05 | -0.0018512 | 0.011315 | 0.011293 | 0.011315 | 0.99607 | -0.019972 | 0.99611 | -0.020234 | 5.1433
3 | -0.091264 | -0.044201 | 0.091266 | 0.044006 | 2.5468e-06 | -0.00019546 | 0.0029356 | 0.0029332 | 0.0029356 | 0.99716 | -0.027411 | 0.99719 | -0.027225 | 1.3979
4 | 0.63335 | 0.25374 | -0.63282 | -0.27724 | 0.00052601 | -0.023492 | 0.019752 | 0.020016 | 0.020016 | 0.99719 | -0.027225 | 0.99639 | -0.022256 | 9.0983
5 | -1.6174 | -0.66816 | 1.6212 | 0.66954 | 0.0037729 | 0.0013811 | 0.05066 | 0.050649 | 0.05066 | 0.99719 | -0.027225 | 0.99969 | -0.0028987 | 24.1237
6 | 0.89278 | 0.37041 | -0.89132 | -0.37073 | 0.0014595 | -0.00032503 | 0.027981 | 0.027995 | 0.027995 | 0.99719 | -0.027225 | 0.99543 | -0.04409 | 13.3309
7 | 0.45037 | 0.19012 | -0.45026 | -0.2 | 0.00011293 | -0.009881 | 0.014163 | 0.014277 | 0.014277 | 0.99639 | -0.022256 | 0.99616 | -0.020604 | 6.4897
8 | 0.18245 | 0.087112 | -0.18245 | -0.088364 | 2.4271e-06 | -0.0012519 | 0.0058576 | 0.0058733 | 0.0058733 | 0.99639 | -0.022256 | 0.99638 | -0.022142 | 2.6697
9 | -1.8444 | -0.77765 | 1.8449 | 0.77788 | 0.00053686 | 0.00022863 | 0.0578 | 0.057799 | 0.0578 | 0.99969 | -0.0028987 | 1 | 0 | 27.5239
10 | 0.14274 | 0.065306 | -0.14273 | -0.065529 | 7.1025e-06 | -0.00022297 | 0.0045521 | 0.0045548 | 0.0045548 | 0.99543 | -0.04409 | 0.99538 | -0.044486 | 2.169
11 | 0.74858 | 0.30543 | -0.74782 | -0.32943 | 0.00076105 | -0.024005 | 0.023446 | 0.023721 | 0.023721 | 0.99543 | -0.04409 | 0.99447 | -0.037785 | 10.7821
12 | 0.45026 | 0.2 | -0.45024 | -0.20161 | 1.8526e-05 | -0.0016052 | 0.014277 | 0.014296 | 0.014296 | 0.99616 | -0.020604 | 0.99612 | -0.02031 | 6.4983
13 | 5.8242 | 2.7127 | -5.7875 | -2.6722 | 0.036721 | 0.040552 | 0.18547 | 0.18549 | 0.18549 | 1 | 0 | 0.99207 | -0.20282 | 52.9972
14 | 5.5655 | 2.5647 | -5.5645 | -2.5662 | 0.0010504 | -0.0015452 | 0.17832 | 0.17834 | 0.17834 | 0.99207 | -0.20282 | 0.99186 | -0.20519 | 49.2662
15 | 0.35673 | 0.15632 | -0.35672 | -0.15687 | 3.9804e-06 | -0.00055296 | 0.011287 | 0.011293 | 0.011293 | 0.99612 | -0.02031 | 0.99611 | -0.020234 | 5.1334
16 | -0.22321 | -0.10811 | 0.22321 | 0.10711 | 3.0055e-06 | -0.0010007 | 0.0072454 | 0.0072326 | 0.0072454 | 0.98815 | -0.19565 | 0.98816 | -0.19576 | 3.2933
17 | -0.22321 | -0.10711 | 0.22324 | 0.09958 | 2.2267e-05 | -0.0075252 | 0.0072326 | 0.0071402 | 0.0072326 | 0.98816 | -0.19576 | 0.98826 | -0.19655 | 3.2876
18 | -0.10731 | -0.051973 | 0.10731 | 0.050893 | 7.3002e-07 | -0.0010803 | 0.0034624 | 0.0034489 | 0.0034624 | 0.9941 | -0.035511 | 0.9941 | -0.035569 | 1.5738
19 | -0.10731 | -0.050893 | 0.10732 | 0.030206 | 1.2989e-05 | -0.020687 | 0.0034489 | 0.0032373 | 0.0034489 | 0.9941 | -0.035569 | 0.99422 | -0.036062 | 1.5677
20 | -0.50976 | -0.22506 | 0.50989 | 0.21599 | 0.00013393 | -0.0090666 | 0.016179 | 0.016074 | 0.016179 | 0.99422 | -0.036062 | 0.99447 | -0.037785 | 7.3543
21 | 0.40244 | 0.19485 | -0.40242 | -0.1949 | 1.4426e-05 | -4.7647e-05 | 0.012982 | 0.012983 | 0.012983 | 0.99422 | -0.036062 | 0.99418 | -0.036298 | 6.1825
22 | 0.23792 | 0.11344 | -0.23791 | -0.11361 | 1.5936e-05 | -0.00017034 | 0.0076513 | 0.0076535 | 0.0076535 | 0.99447 | -0.037785 | 0.9944 | -0.038252 | 3.6445
23 | -0.075183 | -0.036413 | 0.075215 | 0.032829 | 3.1317e-05 | -0.0035838 | 0.0024238 | 0.0023801 | 0.0024238 | 0.99494 | -0.047753 | 0.99538 | -0.044486 | 1.1542
24 | -2.1797 | -1.0018 | 2.1799 | 1.001 | 0.00025556 | -0.00084476 | 0.069859 | 0.069847 | 0.069859 | 0.99129 | -0.20956 | 0.9914 | -0.21046 | 31.7539
25 | 2.0575 | 0.94265 | -2.056 | -0.94194 | 0.0015016 | 0.00071313 | 0.065906 | 0.065909 | 0.065909 | 0.99129 | -0.20956 | 0.99052 | -0.21537 | 31.3851
26 | 3.3822 | 1.5687 | -3.3684 | -1.585 | 0.013764 | -0.016323 | 0.10856 | 0.10881 | 0.10881 | 0.9914 | -0.21046 | 0.98763 | -0.17775 | 49.4597
27 | -5.5621 | -2.5697 | 5.5645 | 2.5662 | 0.0023402 | -0.0034364 | 0.17841 | 0.17834 | 0.17841 | 0.9914 | -0.21046 | 0.99186 | -0.20519 | 49.2835
28 | 1.8278 | 0.83141 | -1.8276 | -0.83215 | 0.00015392 | -0.00074283 | 0.05852 | 0.05853 | 0.05853 | 0.99052 | -0.21537 | 0.99044 | -0.21474 | 26.6044
29 | 1.8276 | 0.83215 | -1.8263 | -0.83852 | 0.001324 | -0.0063739 | 0.05853 | 0.058612 | 0.058612 | 0.99044 | -0.21474 | 0.98977 | -0.20922 | 26.6417
30 | -0.22729 | -0.11008 | 0.22729 | 0.11006 | 1.9769e-06 | -2.2479e-05 | 0.0073814 | 0.0073811 | 0.0073814 | 0.98767 | -0.19739 | 0.98767 | -0.19733 | 3.5149
31 | 0.39763 | 0.18498 | -0.39757 | -0.19132 | 6.0256e-05 | -0.0063406 | 0.012818 | 0.012897 | 0.012897 | 0.98767 | -0.19733 | 0.98753 | -0.19608 | 5.8624
32 | -0.62492 | -0.29503 | 0.62507 | 0.28888 | 0.00014426 | -0.0061514 | 0.020198 | 0.020122 | 0.020198 | 0.98767 | -0.19733 | 0.98789 | -0.19918 | 9.1811
33 | 3.3684 | 1.585 | -3.3683 | -1.5851 | 0.00010812 | -0.00012722 | 0.10881 | 0.10881 | 0.10881 | 0.98763 | -0.17775 | 0.9876 | -0.17748 | 49.4606
34 | -2.6219 | -1.2318 | 2.6244 | 1.2331 | 0.0024293 | 0.0013009 | 0.084763 | 0.08476 | 0.084763 | 0.98658 | -0.18386 | 0.98755 | -0.17705 | 40.3632
35 | 2.2739 | 1.0632 | -2.271 | -1.0618 | 0.0028798 | 0.0014561 | 0.073448 | 0.073452 | 0.073452 | 0.98658 | -0.18386 | 0.98525 | -0.19332 | 34.9774
36 | -2.9596 | -1.3875 | 2.9598 | 1.3873 | 0.0001582 | -0.00025533 | 0.09555 | 0.095546 | 0.09555 | 0.98755 | -0.17705 | 0.9876 | -0.17748 | 43.4318
37 | 0.33526 | 0.15446 | -0.33521 | -0.16233 | 5.3084e-05 | -0.0078641 | 0.01079 | 0.010889 | 0.010889 | 0.98755 | -0.17705 | 0.9874 | -0.17575 | 4.9494
38 | 2.271 | 1.0618 | -2.2704 | -1.0615 | 0.0005585 | 0.00028251 | 0.073452 | 0.073453 | 0.073453 | 0.98525 | -0.19332 | 0.985 | -0.19516 | 34.9778
39 | -0.16496 | -0.079892 | 0.16496 | 0.078091 | 3.003e-06 | -0.0018009 | 0.0053804 | 0.0053575 | 0.0053804 | 0.98338 | -0.20085 | 0.9834 | -0.201 | 2.4456
40 | -0.16496 | -0.078091 | 0.16496 | 0.07556 | 4.177e-06 | -0.0025307 | 0.0053575 | 0.0053262 | 0.0053575 | 0.9834 | -0.201 | 0.98342 | -0.2012 | 2.4352
41 | -0.28465 | -0.13342 | 0.28467 | 0.12858 | 2.3674e-05 | -0.0048332 | 0.0092279 | 0.0091686 | 0.0092279 | 0.98342 | -0.2012 | 0.9835 | -0.20184 | 4.1945
42 | 0.11969 | 0.057856 | -0.11969 | -0.057967 | 9.7652e-08 | -0.00011083 | 0.0039023 | 0.0039037 | 0.0039037 | 0.98342 | -0.2012 | 0.98342 | -0.20119 | 1.7744
43 | -0.28467 | -0.12858 | 0.28468 | 0.12646 | 1.0316e-05 | -0.0021258 | 0.0091686 | 0.009143 | 0.0091686 | 0.9835 | -0.20184 | 0.98353 | -0.20211 | 4.1675
44 | 2.0851 | 0.97173 | -2.0828 | -0.97059 | 0.0023467 | 0.0011347 | 0.06742 | 0.067424 | 0.067424 | 0.985 | -0.19516 | 0.98382 | -0.20366 | 32.1067
45 | -0.24235 | -0.11737 | 0.24235 | 0.11607 | 4.5899e-06 | -0.001301 | 0.0078601 | 0.0078436 | 0.0078601 | 0.98897 | -0.20254 | 0.98898 | -0.2027 | 3.5728
46 | 1.3887 | 0.63789 | -1.3876 | -0.64711 | 0.0010892 | -0.0092199 | 0.044607 | 0.044724 | 0.044724 | 0.98898 | -0.2027 | 0.98826 | -0.19655 | 20.3292
47 | -1.6311 | -0.75396 | 1.6325 | 0.74556 | 0.0013812 | -0.0083979 | 0.05245 | 0.052343 | 0.05245 | 0.98898 | -0.2027 | 0.98977 | -0.20922 | 23.8408
48 | 0.27323 | 0.131 | -0.27322 | -0.13233 | 5.9807e-06 | -0.0013292 | 0.008851 | 0.0088679 | 0.0088679 | 0.98826 | -0.19655 | 0.98824 | -0.19636 | 4.0309
49 | 0.89116 | 0.41653 | -0.89085 | -0.41658 | 0.00031386 | -5.2041e-05 | 0.028734 | 0.028738 | 0.028738 | 0.98826 | -0.19655 | 0.98789 | -0.19918 | 13.6845
50 | 0.19385 | 0.092959 | -0.19384 | -0.093882 | 2.0765e-06 | -0.00092302 | 0.0062702 | 0.0062819 | 0.0062819 | 0.98977 | -0.20922 | 0.98976 | -0.20913 | 2.8554
51 | 0.26578 | 0.1277 | -0.26578 | -0.12872 | 4.3683e-06 | -0.0010241 | 0.0086165 | 0.0086295 | 0.0086295 | 0.98789 | -0.19918 | 0.98787 | -0.19904 | 3.9225
52 | -0.33521 | -0.16235 | 0.33521 | 0.16233 | 1.6228e-07 | -2.3812e-05 | 0.010889 | 0.010889 | 0.010889 | 0.9874 | -0.17574 | 0.9874 | -0.17575 | 4.9496
53 | 0.39757 | 0.19132 | -0.39756 | -0.19255 | 1.1775e-05 | -0.0012296 | 0.012897 | 0.012913 | 0.012913 | 0.98753 | -0.19608 | 0.98751 | -0.19582 | 5.8695
54 | -1.171 | -0.55602 | 1.171 | 0.55537 | 5.5442e-05 | -0.0006462 | 0.038049 | 0.03804 | 0.038049 | 0.98347 | -0.20053 | 0.98352 | -0.20092 | 17.2949
55 | 0.79772 | 0.37525 | -0.79769 | -0.37612 | 3.3922e-05 | -0.00086588 | 0.025877 | 0.025887 | 0.025887 | 0.98347 | -0.20053 | 0.98343 | -0.20018 | 11.767
56 | -1.171 | -0.55537 | 1.1714 | 0.55099 | 0.0003751 | -0.0043811 | 0.03804 | 0.037984 | 0.03804 | 0.98352 | -0.20092 | 0.98381 | -0.20356 | 17.2911
57 | 0.79769 | 0.37612 | -0.7975 | -0.38088 | 0.00018713 | -0.004762 | 0.025887 | 0.025948 | 0.025948 | 0.98343 | -0.20018 | 0.98322 | -0.19823 | 11.7946
58 | 0.68392 | 0.30954 | -0.68375 | -0.31543 | 0.00016726 | -0.0058967 | 0.022028 | 0.0221 | 0.0221 | 0.98381 | -0.20356 | 0.98358 | -0.2017 | 10.0455
59 | -1.8553 | -0.86053 | 1.8553 | 0.86042 | 2.2754e-05 | -0.00010263 | 0.06001 | 0.060009 | 0.06001 | 0.98381 | -0.20356 | 0.98382 | -0.20366 | 27.2774
60 | 0.29505 | 0.14279 | -0.29503 | -0.14289 | 1.5395e-05 | -9.8001e-05 | 0.0096239 | 0.0096252 | 0.0096252 | 0.98322 | -0.19823 | 0.98316 | -0.19858 | 4.5834
61 | 0.50245 | 0.23808 | -0.50235 | -0.23827 | 0.0001047 | -0.0001888 | 0.016324 | 0.016328 | 0.016328 | 0.98322 | -0.19823 | 0.983 | -0.19972 | 7.7751
62 | 0.23601 | 0.11007 | -0.236 | -0.11223 | 7.3353e-06 | -0.0021628 | 0.0076429 | 0.00767 | 0.00767 | 0.98358 | -0.2017 | 0.98356 | -0.20145 | 3.4864
63 | 0.44775 | 0.20536 | -0.44772 | -0.20542 | 2.2845e-05 | -5.6532e-05 | 0.014457 | 0.014458 | 0.014458 | 0.98358 | -0.2017 | 0.98353 | -0.20211 | 6.8849
64 | 0.2292 | 0.10598 | -0.2292 | -0.10606 | 6.6861e-06 | -7.4518e-05 | 0.0074157 | 0.0074167 | 0.0074167 | 0.983 | -0.19972 | 0.98297 | -0.19994 | 3.5318
65 | 0.236 | 0.11223 | -0.23599 | -0.1143 | 7.0469e-06 | -0.0020633 | 0.00767 | 0.0076962 | 0.0076962 | 0.98356 | -0.20145 | 0.98353 | -0.20119 | 3.4983
66 | -0.22917 | -0.11099 | 0.22918 | 0.1109 | 8.2811e-06 | -9.0665e-05 | 0.0074788 | 0.0074776 | 0.0074788 | 0.98287 | -0.19962 | 0.98291 | -0.19938 | 3.5614
67 | -0.22918 | -0.1109 | 0.2292 | 0.10606 | 1.5565e-05 | -0.0048452 | 0.0074776 | 0.0074167 | 0.0074776 | 0.98291 | -0.19938 | 0.98297 | -0.19994 | 3.3989
68 | 0.23791 | 0.11361 | -0.2379 | -0.11522 | 5.3608e-06 | -0.0016126 | 0.0076535 | 0.0076738 | 0.0076738 | 0.9944 | -0.038252 | 0.99438 | -0.038059 | 3.4881

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 7.6831 | 3.5011

## res_load
| p_mw | q_mvar
0 | 0.069966 | 0.033886
1 | 0.28666 | 0.13883
2 | 0.091264 | 0.044201
3 | 0.22323 | 0.10811
4 | 0.18245 | 0.088364
5 | 0.22195 | 0.10749
6 | 0.09351 | 0.045289
7 | 0.22321 | 0.10811
8 | 0.10731 | 0.051973
9 | 0.40242 | 0.1949
10 | 0.075183 | 0.036413
11 | 0.067518 | 0.0327
12 | 0.12218 | 0.059176
13 | 0.22823 | 0.11053
14 | 0.22729 | 0.11008
15 | 0.34805 | 0.16857
16 | 0.16496 | 0.079892
17 | 0.11969 | 0.057967
18 | 0.1853 | 0.089745
19 | 0.24235 | 0.11737
20 | 0.27322 | 0.13233
21 | 0.19384 | 0.093882
22 | 0.33521 | 0.16235
23 | 0.40852 | 0.19786
24 | 0.26578 | 0.12872
25 | 0.39756 | 0.19255
26 | 0.37324 | 0.18077
27 | 0.22747 | 0.11017
28 | 0.29503 | 0.14289
29 | 0.27314 | 0.13229
30 | 0.16304 | 0.078963
31 | 0.23599 | 0.1143
32 | 0.22917 | 0.11099
33 | 0.2379 | 0.11522

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1