## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_10_1_node_53 | 20 | n |  | TRUE
1 | bus_MV_10_1_node_54 | 20 | n |  | TRUE
2 | bus_MV_10_1_node_77 | 20 | n |  | TRUE
3 | bus_MV_10_1_node_78 | 20 | n |  | TRUE
4 | bus_MV_10_1_node_117 | 20 | n |  | TRUE
5 | bus_MV_10_1_node_110 | 20 | n |  | TRUE
6 | bus_MV_10_1_node_123 | 20 | n |  | TRUE
7 | bus_MV_10_1_node_124 | 20 | n |  | TRUE
8 | bus_MV_10_1_node_264 | 20 | n |  | TRUE
9 | bus_MV_10_1_node_109 | 20 | n |  | TRUE
10 | bus_MV_10_1_node_55 | 20 | n |  | TRUE
11 | bus_MV_10_1_node_57 | 20 | n |  | TRUE
12 | bus_MV_10_1_node_272 | 20 | n |  | TRUE
13 | bus_MV_10_1_node_60 | 20 | n |  | TRUE
14 | bus_MV_10_1_node_271 | 20 | n |  | TRUE
15 | bus_MV_10_1_node_89 | 20 | n |  | TRUE
16 | bus_MV_10_1_node_90 | 20 | n |  | TRUE
17 | bus_MV_10_1_node_234 | 20 | n |  | TRUE
18 | bus_MV_10_1_node_58 | 20 | n |  | TRUE
19 | bus_MV_10_1_node_59 | 20 | n |  | TRUE
20 | bus_MV_10_1_node_274 | 20 | n |  | TRUE
21 | bus_MV_10_1_node_62 | 20 | n |  | TRUE
22 | bus_MV_10_1_node_248 | 20 | n |  | TRUE
23 | bus_MV_10_1_node_273 | 20 | n |  | TRUE
24 | bus_MV_10_1_node_235 | 20 | n |  | TRUE
25 | bus_MV_10_1_node_249 | 20 | n |  | TRUE
26 | bus_MV_10_1_node_70 | 20 | n |  | TRUE
27 | bus_MV_10_1_node_61 | 20 | n |  | TRUE
28 | bus_MV_10_1_node_233 | 20 | n |  | TRUE
29 | bus_MV_10_1_node_247 | 20 | n |  | TRUE
30 | bus_MV_10_1_node_236 | 20 | n |  | TRUE
31 | bus_MV_10_1_node_270 | 20 | n |  | TRUE
32 | bus_MV_10_1_node_65 | 20 | n |  | TRUE
33 | bus_MV_10_1_node_66 | 20 | n |  | TRUE
34 | bus_MV_10_1_node_67 | 20 | n |  | TRUE
35 | bus_MV_10_1_node_71 | 20 | n |  | TRUE
36 | bus_MV_10_1_node_68 | 20 | n |  | TRUE
37 | bus_MV_10_1_node_69 | 20 | n |  | TRUE
38 | bus_MV_10_1_node_73 | 20 | n |  | TRUE
39 | bus_MV_10_1_node_74 | 20 | n |  | TRUE
40 | bus_MV_10_1_node_75 | 20 | n |  | TRUE
41 | bus_MV_10_1_node_121 | 20 | n |  | TRUE
42 | bus_MV_10_1_node_122 | 20 | n |  | TRUE
43 | bus_MV_10_1_node_276 | 20 | n |  | TRUE
44 | bus_MV_10_1_node_79 | 20 | n |  | TRUE
45 | bus_MV_10_1_node_81 | 20 | n |  | TRUE
46 | bus_MV_10_1_node_80 | 20 | n |  | TRUE
47 | bus_MV_10_1_node_83 | 20 | n |  | TRUE
48 | bus_MV_10_1_node_82 | 20 | n |  | TRUE
49 | bus_MV_10_1_node_102 | 20 | n |  | TRUE
50 | bus_MV_10_1_node_84 | 20 | n |  | TRUE
51 | bus_MV_10_1_node_101 | 20 | n |  | TRUE
52 | bus_MV_10_1_node_188 | 20 | n |  | TRUE
53 | bus_MV_10_1_node_239 | 20 | n |  | TRUE
54 | bus_MV_10_1_node_189 | 20 | n |  | TRUE
55 | bus_MV_10_1_node_105 | 20 | n |  | TRUE
56 | bus_MV_10_1_node_85 | 20 | n |  | TRUE
57 | bus_MV_10_1_node_86 | 20 | n |  | TRUE
58 | bus_MV_10_1_node_237 | 20 | n |  | TRUE
59 | bus_MV_10_1_node_238 | 20 | n |  | TRUE
60 | bus_MV_10_1_node_87 | 20 | n |  | TRUE
61 | bus_MV_10_1_node_88 | 20 | n |  | TRUE
62 | bus_MV_10_1_node_257 | 20 | n |  | TRUE
63 | bus_MV_10_1_node_91 | 20 | n |  | TRUE
64 | bus_MV_10_1_node_256 | 20 | n |  | TRUE
65 | bus_MV_10_1_node_92 | 20 | n |  | TRUE
66 | bus_MV_10_1_node_111 | 20 | n |  | TRUE
67 | bus_MV_10_1_node_96 | 20 | n |  | TRUE
68 | bus_MV_10_1_node_95 | 20 | n |  | TRUE
69 | bus_MV_10_1_node_106 | 20 | n |  | TRUE
70 | bus_MV_10_1_node_254 | 20 | n |  | TRUE
71 | bus_MV_10_1_node_255 | 20 | n |  | TRUE
72 | bus_MV_10_1_node_97 | 20 | n |  | TRUE
73 | bus_MV_10_1_node_113 | 20 | n |  | TRUE
74 | bus_MV_10_1_node_250 | 20 | n |  | TRUE
75 | bus_MV_10_1_node_99 | 20 | n |  | TRUE
76 | bus_MV_10_1_node_112 | 20 | n |  | TRUE
77 | bus_MV_10_1_node_94 | 20 | n |  | TRUE
78 | bus_MV_10_1_node_98 | 20 | n |  | TRUE
79 | bus_MV_10_1_node_100 | 20 | n |  | TRUE
80 | bus_MV_10_1_node_116 | 20 | n |  | TRUE
81 | bus_MV_10_1_node_262 | 20 | n |  | TRUE
82 | bus_MV_10_1_node_252 | 20 | n |  | TRUE
83 | bus_MV_10_1_node_93 | 20 | n |  | TRUE
84 | bus_MV_10_1_node_104 | 20 | n |  | TRUE
85 | bus_MV_10_1_node_114 | 20 | n |  | TRUE
86 | bus_MV_10_1_node_253 | 20 | n |  | TRUE
87 | bus_MV_10_1_node_183 | 20 | n |  | TRUE
88 | bus_MV_10_1_node_184 | 20 | n |  | TRUE
89 | bus_MV_10_1_node_185 | 20 | n |  | TRUE
90 | bus_MV_10_1_node_187 | 20 | n |  | TRUE
91 | bus_MV_10_1_node_191 | 20 | n |  | TRUE
92 | bus_MV_10_1_node_190 | 20 | n |  | TRUE
93 | bus_MV_10_1_node_108 | 20 | n |  | TRUE
94 | bus_MV_10_1_node_277 | 20 | n |  | TRUE
95 | bus_MV_10_1_node_240 | 20 | n |  | TRUE
96 | bus_MV_10_1_node_241 | 20 | n |  | TRUE
97 | bus_MV_10_1_node_115 | 20 | n |  | TRUE
98 | bus_MV_10_1_node_120 | 20 | n |  | TRUE
99 | bus_MV_10_1_node_118 | 20 | n |  | TRUE
100 | bus_MV_10_1_node_119 | 20 | n |  | TRUE
101 | bus_MV_10_1_node_168 | 20 | n |  | TRUE
102 | bus_MV_10_1_node_263 | 20 | n |  | TRUE
103 | bus_MV_10_1_node_166 | 20 | n |  | TRUE
104 | bus_MV_10_1_node_169 | 20 | n |  | TRUE
105 | bus_MV_10_1_node_170 | 20 | n |  | TRUE
106 | bus_MV_10_1_node_171 | 20 | n |  | TRUE
107 | bus_MV_10_1_node_281 | 20 | n |  | TRUE
108 | bus_MV_10_1_node_177 | 20 | n |  | TRUE
109 | bus_MV_10_1_node_279 | 20 | n |  | TRUE
110 | bus_MV_10_1_node_149 | 20 | n |  | TRUE
111 | bus_MV_10_1_node_125 | 20 | n |  | TRUE
112 | bus_MV_10_1_node_126 | 20 | n |  | TRUE
113 | bus_MV_10_1_node_192 | 20 | n |  | TRUE
114 | bus_MV_10_1_node_127 | 20 | n |  | TRUE
115 | bus_MV_10_1_node_268 | 20 | n |  | TRUE
116 | bus_MV_10_1_node_135 | 20 | n |  | TRUE
117 | bus_MV_10_1_node_186 | 20 | n |  | TRUE
118 | bus_MV_10_1_node_243 | 20 | n |  | TRUE
119 | bus_MV_10_1_node_251 | 20 | n |  | TRUE
120 | bus_MV_10_1_node_182 | 20 | n |  | TRUE
121 | bus_MV_10_1_node_181 | 20 | n |  | TRUE
122 | bus_MV_10_1_node_128 | 20 | n |  | TRUE
123 | bus_MV_10_1_node_129 | 20 | n |  | TRUE
124 | bus_MV_10_1_node_130 | 20 | n |  | TRUE
125 | bus_MV_10_1_node_131 | 20 | n |  | TRUE
126 | bus_MV_10_1_node_136 | 20 | n |  | TRUE
127 | bus_MV_10_1_node_269 | 20 | n |  | TRUE
128 | bus_MV_10_1_node_292 | 20 | n |  | TRUE
129 | bus_MV_10_1_node_133 | 20 | n |  | TRUE
130 | bus_MV_10_1_node_291 | 20 | n |  | TRUE
131 | bus_MV_10_1_node_212 | 20 | n |  | TRUE
132 | bus_MV_10_1_node_132 | 20 | n |  | TRUE
133 | bus_MV_10_1_node_134 | 20 | n |  | TRUE
134 | bus_MV_10_1_node_137 | 20 | n |  | TRUE
135 | bus_MV_10_1_node_139 | 20 | n |  | TRUE
136 | bus_MV_10_1_node_144 | 20 | n |  | TRUE
137 | bus_MV_10_1_node_141 | 20 | n |  | TRUE
138 | bus_MV_10_1_node_138 | 20 | n |  | TRUE
139 | bus_MV_10_1_node_140 | 20 | n |  | TRUE
140 | bus_MV_10_1_node_142 | 20 | n |  | TRUE
141 | bus_MV_10_1_node_180 | 20 | n |  | TRUE
142 | bus_MV_10_1_node_245 | 20 | n |  | TRUE
143 | bus_MV_10_1_node_143 | 20 | n |  | TRUE
144 | bus_MV_10_1_node_154 | 20 | n |  | TRUE
145 | bus_MV_10_1_node_246 | 20 | n |  | TRUE
146 | bus_MV_10_1_node_155 | 20 | n |  | TRUE
147 | bus_MV_10_1_node_145 | 20 | n |  | TRUE
148 | bus_MV_10_1_node_146 | 20 | n |  | TRUE
149 | bus_MV_10_1_node_147 | 20 | n |  | TRUE
150 | bus_MV_10_1_node_151 | 20 | n |  | TRUE
151 | bus_MV_10_1_node_152 | 20 | n |  | TRUE
152 | bus_MV_10_1_node_148 | 20 | n |  | TRUE
153 | bus_MV_10_1_node_172 | 20 | n |  | TRUE
154 | bus_MV_10_1_node_283 | 20 | n |  | TRUE
155 | bus_MV_10_1_node_159 | 20 | n |  | TRUE
156 | bus_MV_10_1_node_174 | 20 | n |  | TRUE
157 | bus_MV_10_1_node_176 | 20 | n |  | TRUE
158 | bus_MV_10_1_node_175 | 20 | n |  | TRUE
159 | bus_MV_10_1_node_178 | 20 | n |  | TRUE
160 | bus_MV_10_1_node_153 | 20 | n |  | TRUE
161 | bus_MV_10_1_node_282 | 20 | n |  | TRUE
162 | bus_MV_10_1_node_160 | 20 | n |  | TRUE
163 | bus_MV_10_1_node_157 | 20 | n |  | TRUE
164 | bus_MV_10_1_node_156 | 20 | n |  | TRUE
165 | bus_MV_10_1_node_158 | 20 | n |  | TRUE
166 | bus_MV_10_1_node_164 | 20 | n |  | TRUE
167 | bus_MV_10_1_node_162 | 20 | n |  | TRUE
168 | bus_MV_10_1_node_161 | 20 | n |  | TRUE
169 | bus_MV_10_1_node_163 | 20 | n |  | TRUE
170 | bus_MV_10_1_node_165 | 20 | n |  | TRUE
171 | bus_MV_10_1_node_179 | 20 | n |  | TRUE
172 | bus_MV_10_1_node_242 | 20 | n |  | TRUE
173 | bus_HV_10_1_node_252 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_10_1_load_53 | 0 | 0.13407 | 0.064931 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_10_1_load_54 | 1 | 0.2117 | 0.10253 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_10_1_load_117 | 4 | 0.12186 | 0.059017 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_10_1_load_124 | 7 | 0.13056 | 0.063232 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_10_1_load_264 | 8 | 0.076616 | 0.037107 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_10_1_load_55 | 10 | 0.12392 | 0.060017 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_10_1_load_272 | 12 | 0.11507 | 0.055733 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_10_1_load_89 | 15 | 0.1055 | 0.051094 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_10_1_load_90 | 16 | 0.082535 | 0.039974 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_10_1_load_274 | 20 | 0.10284 | 0.049806 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_10_1_load_62 | 21 | 0.11921 | 0.057736 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_10_1_load_248 | 22 | 0.14611 | 0.070763 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_10_1_load_249 | 25 | 0.11443 | 0.055419 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_10_1_load_61 | 27 | 0.14546 | 0.07045 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_10_1_load_233 | 28 | 0.083128 | 0.040261 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_10_1_load_247 | 29 | 0.14302 | 0.06927 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_10_1_load_270 | 31 | 0.11976 | 0.058003 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_10_1_load_65 | 32 | 0.12046 | 0.058341 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_10_1_load_71 | 35 | 0.062441 | 0.030241 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_10_1_load_68 | 36 | 0.13168 | 0.063776 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_10_1_load_73 | 38 | 0.10579 | 0.051236 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_10_1_load_121 | 41 | 0.14683 | 0.071111 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_10_1_load_276 | 43 | 0.11648 | 0.056415 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_10_1_load_79 | 44 | 0.058142 | 0.02816 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_10_1_load_102 | 49 | 0.094888 | 0.045956 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_10_1_load_84 | 50 | 0.12784 | 0.061918 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_10_1_load_188 | 52 | 0.19068 | 0.092352 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_10_1_load_239 | 53 | 0.13491 | 0.065339 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_10_1_load_86 | 57 | 0.14434 | 0.069905 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_10_1_load_237 | 58 | 0.13275 | 0.064293 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_10_1_load_87 | 60 | 0.11218 | 0.05433 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_10_1_load_257 | 62 | 0.14002 | 0.067813 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_10_1_load_256 | 64 | 0.09686 | 0.046912 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_10_1_load_111 | 66 | 0.13477 | 0.065274 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_10_1_load_106 | 69 | 0.12088 | 0.058544 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_10_1_load_113 | 73 | 0.083914 | 0.040641 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_10_1_load_250 | 74 | 0.086727 | 0.042004 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_10_1_load_112 | 76 | 0.11768 | 0.056997 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_10_1_load_116 | 80 | 0.14329 | 0.069399 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_10_1_load_262 | 81 | 0.1503 | 0.072793 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_10_1_load_252 | 82 | 0.080407 | 0.038943 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_10_1_load_93 | 83 | 0.1278 | 0.061898 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_10_1_load_253 | 86 | 0.1534 | 0.074293 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_10_1_load_183 | 87 | 0.10151 | 0.049163 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_10_1_load_191 | 91 | 0.24356 | 0.11796 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_10_1_load_277 | 94 | 0.083608 | 0.040493 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_10_1_load_240 | 95 | 0.082755 | 0.04008 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_10_1_load_120 | 98 | 0.1113 | 0.053907 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_10_1_load_118 | 99 | 0.058934 | 0.028543 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_10_1_load_263 | 102 | 0.10155 | 0.049181 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_10_1_load_166 | 103 | 0.12877 | 0.062367 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_10_1_load_281 | 107 | 0.1059 | 0.051291 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_10_1_load_177 | 108 | 0.10524 | 0.050971 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_10_1_load_279 | 109 | 0.1102 | 0.05337 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_10_1_load_125 | 111 | 0.10366 | 0.050206 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_10_1_load_192 | 113 | 0.34425 | 0.16673 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_10_1_load_268 | 115 | 0.13594 | 0.065838 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_10_1_load_243 | 118 | 0.082201 | 0.039812 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_10_1_load_251 | 119 | 0.4094 | 0.19828 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_10_1_load_181 | 121 | 0.072257 | 0.034996 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_10_1_load_128 | 122 | 0.10674 | 0.051696 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_10_1_load_269 | 127 | 0.12576 | 0.060909 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_10_1_load_292 | 128 | 0.067615 | 0.032747 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_10_1_load_291 | 130 | 0.076135 | 0.036874 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_10_1_load_212 | 131 | 0.084848 | 0.041094 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_10_1_load_132 | 132 | 0.12596 | 0.061007 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_10_1_load_144 | 136 | 0.13337 | 0.064596 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_10_1_load_138 | 138 | 0.14757 | 0.071469 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_10_1_load_180 | 141 | 0.13944 | 0.067534 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_10_1_load_245 | 142 | 0.14121 | 0.068394 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_10_1_load_246 | 145 | 0.15856 | 0.076792 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_10_1_load_145 | 147 | 0.15267 | 0.073943 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_10_1_load_151 | 150 | 0.091313 | 0.044225 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_10_1_load_172 | 153 | 0.10481 | 0.050762 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_10_1_load_283 | 154 | 0.12754 | 0.061771 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_10_1_load_159 | 155 | 0.095439 | 0.046223 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_10_1_load_178 | 159 | 0.074527 | 0.036095 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_10_1_load_282 | 161 | 0.070836 | 0.034307 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_10_1_load_160 | 162 | 0.11719 | 0.056757 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_10_1_load_156 | 164 | 0.052266 | 0.025314 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_10_1_load_164 | 166 | 0.14585 | 0.07064 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_10_1_load_161 | 168 | 0.11985 | 0.058044 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_10_1_load_165 | 170 | 0.087956 | 0.042599 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_10_1_load_179 | 171 | 0.14766 | 0.071515 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_10_1_load_242 | 172 | 0.079322 | 0.038417 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 82 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_10_1_line_0 |  | 0 | 1 | 1.039 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_10_1_line_1 |  | 1 | 2 | 1.6733 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_10_1_line_2 |  | 2 | 3 | 0.35103 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_10_1_line_3 |  | 2 | 4 | 0.064081 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_10_1_line_4 |  | 3 | 41 | 0.05888 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_10_1_line_5 |  | 5 | 6 | 0.59321 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_10_1_line_6 |  | 5 | 7 | 0.087412 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_10_1_line_7 |  | 5 | 8 | 0.2939 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_10_1_line_8 |  | 5 | 9 | 0.41207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_10_1_line_9 |  | 6 | 43 | 0.097723 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_10_1_line_10 |  | 6 | 42 | 0.19142 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_10_1_line_11 |  | 8 | 40 | 0.013073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_10_1_line_12 |  | 9 | 95 | 0.037553 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_10_1_line_13 |  | 9 | 93 | 0.32873 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_10_1_line_14 |  | 10 | 11 | 0.034815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_10_1_line_15 |  | 10 | 12 | 0.13502 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_10_1_line_16 |  | 11 | 13 | 0.088175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_10_1_line_17 |  | 12 | 14 | 0.035508 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_10_1_line_18 |  | 13 | 22 | 0.015012 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_10_1_line_19 |  | 14 | 23 | 0.057697 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_10_1_line_20 |  | 15 | 16 | 0.064806 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_10_1_line_21 |  | 15 | 17 | 0.98628 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_10_1_line_22 |  | 16 | 60 | 0.15013 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_10_1_line_23 |  | 17 | 24 | 0.51535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_10_1_line_24 |  | 17 | 28 | 0.10382 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_10_1_line_25 |  | 18 | 19 | 0.22574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_10_1_line_26 |  | 18 | 20 | 0.05603 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_10_1_line_27 |  | 19 | 21 | 0.042967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_10_1_line_28 |  | 20 | 23 | 0.080746 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_10_1_line_29 |  | 21 | 24 | 0.33613 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_10_1_line_30 |  | 22 | 25 | 0.065121 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_10_1_line_31 |  | 22 | 26 | 0.062355 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_10_1_line_32 |  | 23 | 34 | 0.078033 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_10_1_line_33 |  | 24 | 29 | 0.033085 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_10_1_line_34 |  | 24 | 30 | 0.30421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_10_1_line_35 |  | 25 | 27 | 0.23186 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_10_1_line_36 |  | 26 | 37 | 0.27878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_10_1_line_37 |  | 30 | 31 | 0.021969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_10_1_line_38 |  | 32 | 33 | 0.10127 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_10_1_line_39 |  | 33 | 34 | 0.25367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_10_1_line_40 |  | 34 | 35 | 0.09572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_10_1_line_41 |  | 36 | 37 | 0.031994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_10_1_line_42 |  | 38 | 39 | 0.003305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_10_1_line_43 |  | 39 | 40 | 0.20008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_10_1_line_44 |  | 41 | 42 | 0.014848 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_10_1_line_45 |  | 44 | 45 | 0.057044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_10_1_line_46 |  | 44 | 46 | 0.061844 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_10_1_line_47 |  | 45 | 47 | 0.26424 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_10_1_line_48 |  | 46 | 48 | 0.25716 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_10_1_line_49 |  | 47 | 53 | 0.16791 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_10_1_line_50 |  | 48 | 52 | 0.03104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_10_1_line_51 |  | 49 | 50 | 0.16608 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_10_1_line_52 |  | 49 | 51 | 0.13606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_10_1_line_53 |  | 50 | 56 | 0.028531 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_10_1_line_54 |  | 51 | 84 | 0.1736 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_10_1_line_55 |  | 51 | 79 | 0.30821 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_10_1_line_56 |  | 52 | 54 | 0.008843 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_10_1_line_57 |  | 53 | 55 | 0.017546 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_10_1_line_58 |  | 54 | 92 | 0.65873 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_10_1_line_59 |  | 55 | 59 | 0.11083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_10_1_line_60 |  | 56 | 57 | 0.024526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_10_1_line_61 |  | 57 | 58 | 0.037033 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_10_1_line_62 |  | 58 | 59 | 0.083284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_10_1_line_63 |  | 60 | 61 | 0.24415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_10_1_line_64 |  | 60 | 62 | 0.14964 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_10_1_line_65 |  | 61 | 63 | 0.25284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_10_1_line_66 |  | 61 | 64 | 0.087228 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_10_1_line_67 |  | 63 | 65 | 0.056273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_10_1_line_68 |  | 63 | 66 | 0.019951 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_10_1_line_69 |  | 64 | 70 | 0.031344 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_10_1_line_70 |  | 65 | 67 | 0.38537 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
71 | MV_10_1_line_71 |  | 65 | 68 | 0.3844 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
72 | MV_10_1_line_72 |  | 65 | 69 | 0.010645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_10_1_line_73 |  | 67 | 72 | 0.12194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_10_1_line_74 |  | 67 | 73 | 0.010509 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
75 | MV_10_1_line_75 |  | 68 | 75 | 0.27355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_10_1_line_76 |  | 68 | 76 | 0.062932 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_10_1_line_77 |  | 68 | 77 | 0.36393 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
78 | MV_10_1_line_78 |  | 70 | 71 | 0.14102 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_10_1_line_79 |  | 71 | 94 | 0.003606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_10_1_line_80 |  | 72 | 74 | 0.0592 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_10_1_line_81 |  | 73 | 85 | 0.053081 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
82 | MV_10_1_line_82 |  | 75 | 81 | 0.006608 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_10_1_line_83 |  | 77 | 83 | 0.045799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_10_1_line_84 |  | 77 | 78 | 0.57809 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
85 | MV_10_1_line_85 |  | 78 | 79 | 0.50505 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
86 | MV_10_1_line_86 |  | 78 | 80 | 0.045819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_10_1_line_87 |  | 79 | 82 | 0.052225 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_10_1_line_88 |  | 84 | 86 | 0.059724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_10_1_line_89 |  | 85 | 97 | 0.41172 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
90 | MV_10_1_line_90 |  | 87 | 88 | 0.061349 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_10_1_line_91 |  | 88 | 89 | 0.33479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_10_1_line_92 |  | 89 | 90 | 0.25711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_10_1_line_93 |  | 89 | 91 | 0.032529 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_10_1_line_94 |  | 90 | 119 | 0.12566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_10_1_line_95 |  | 90 | 117 | 0.48598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_10_1_line_96 |  | 91 | 92 | 0.001913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_10_1_line_97 |  | 93 | 94 | 0.022687 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_10_1_line_98 |  | 95 | 96 | 0.034329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_10_1_line_99 |  | 96 | 172 | 0.005401 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_10_1_line_100 |  | 97 | 98 | 0.1078 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
101 | MV_10_1_line_101 |  | 98 | 102 | 0.018707 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_10_1_line_102 |  | 98 | 100 | 0.089358 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
103 | MV_10_1_line_103 |  | 99 | 100 | 0.24403 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
104 | MV_10_1_line_104 |  | 99 | 101 | 1.3021 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
105 | MV_10_1_line_105 |  | 101 | 106 | 0.31039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_10_1_line_106 |  | 101 | 103 | 0.02579 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
107 | MV_10_1_line_107 |  | 103 | 104 | 0.20625 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
108 | MV_10_1_line_108 |  | 103 | 105 | 0.30913 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_10_1_line_109 |  | 104 | 107 | 0.22531 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
110 | MV_10_1_line_110 |  | 105 | 108 | 0.035606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_10_1_line_111 |  | 106 | 109 | 0.011135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_10_1_line_112 |  | 107 | 110 | 0.88224 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
113 | MV_10_1_line_113 |  | 110 | 155 | 0.038149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_10_1_line_114 |  | 110 | 152 | 0.70042 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
115 | MV_10_1_line_115 |  | 111 | 112 | 0.18855 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
116 | MV_10_1_line_116 |  | 111 | 113 | 1.245 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
117 | MV_10_1_line_117 |  | 112 | 114 | 0.10949 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
118 | MV_10_1_line_118 |  | 114 | 120 | 0.016 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
119 | MV_10_1_line_119 |  | 114 | 115 | 0.016536 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
120 | MV_10_1_line_120 |  | 115 | 116 | 0.011862 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
121 | MV_10_1_line_121 |  | 116 | 126 | 0.57437 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
122 | MV_10_1_line_122 |  | 117 | 118 | 0.0089908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_10_1_line_123 |  | 120 | 121 | 0.061899 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
124 | MV_10_1_line_124 |  | 122 | 123 | 0.01928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_10_1_line_125 |  | 123 | 124 | 0.56357 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
126 | MV_10_1_line_126 |  | 123 | 125 | 0.32291 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
127 | MV_10_1_line_127 |  | 124 | 130 | 0.039042 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
128 | MV_10_1_line_128 |  | 125 | 128 | 0.054245 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
129 | MV_10_1_line_129 |  | 126 | 127 | 0.039725 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_10_1_line_130 |  | 126 | 128 | 1.5294 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
131 | MV_10_1_line_131 |  | 126 | 129 | 0.92872 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
132 | MV_10_1_line_132 |  | 129 | 132 | 0.023629 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
133 | MV_10_1_line_133 |  | 130 | 131 | 1.8164 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
134 | MV_10_1_line_134 |  | 132 | 133 | 0.030115 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
135 | MV_10_1_line_135 |  | 133 | 134 | 0.16574 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
136 | MV_10_1_line_136 |  | 134 | 135 | 0.32029 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
137 | MV_10_1_line_137 |  | 134 | 136 | 0.050487 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
138 | MV_10_1_line_138 |  | 135 | 137 | 0.41281 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
139 | MV_10_1_line_139 |  | 135 | 138 | 0.031252 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
140 | MV_10_1_line_140 |  | 137 | 141 | 0.13636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_10_1_line_141 |  | 138 | 139 | 0.04951 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
142 | MV_10_1_line_142 |  | 139 | 140 | 0.11345 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
143 | MV_10_1_line_143 |  | 140 | 142 | 0.019279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_10_1_line_144 |  | 140 | 143 | 0.47215 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
145 | MV_10_1_line_145 |  | 143 | 144 | 0.073465 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
146 | MV_10_1_line_146 |  | 143 | 145 | 0.021631 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
147 | MV_10_1_line_147 |  | 144 | 146 | 0.097353 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
148 | MV_10_1_line_148 |  | 146 | 162 | 0.019257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_10_1_line_149 |  | 146 | 151 | 0.49543 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
150 | MV_10_1_line_150 |  | 146 | 160 | 0.13591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_10_1_line_151 |  | 147 | 148 | 0.041902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_10_1_line_152 |  | 148 | 149 | 0.1852 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
153 | MV_10_1_line_153 |  | 148 | 150 | 0.32995 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
154 | MV_10_1_line_154 |  | 149 | 152 | 0.45686 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
155 | MV_10_1_line_155 |  | 149 | 153 | 0.064424 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
156 | MV_10_1_line_156 |  | 150 | 151 | 0.009418 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
157 | MV_10_1_line_157 |  | 152 | 154 | 0.060269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_10_1_line_158 |  | 153 | 156 | 0.052075 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
159 | MV_10_1_line_159 |  | 156 | 157 | 0.34301 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
160 | MV_10_1_line_160 |  | 156 | 158 | 0.2907 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
161 | MV_10_1_line_161 |  | 157 | 171 | 0.030429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_10_1_line_162 |  | 158 | 159 | 0.008378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_10_1_line_163 |  | 160 | 161 | 0.006509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_10_1_line_164 |  | 161 | 163 | 0.18937 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
165 | MV_10_1_line_165 |  | 163 | 165 | 0.15302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_10_1_line_166 |  | 163 | 164 | 0.031197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_10_1_line_167 |  | 165 | 166 | 0.095534 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
168 | MV_10_1_line_168 |  | 166 | 167 | 0.027758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_10_1_line_169 |  | 167 | 168 | 0.012711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_10_1_line_170 |  | 168 | 169 | 0.01656 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_10_1_line_171 |  | 169 | 170 | 0.015946 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_10_1_trafo_252 | 25 MVA 110/20 kV | 173 | 82 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2723089.0994 | 1228073.7175
1 | 2722050.712 | 1228110.308
2 | 2721183.2258 | 1229541.1593
3 | 2721127.7793 | 1229794.9772
4 | 2721220.6231 | 1229593.1963
5 | 2720527.8284 | 1230190.1927
6 | 2721102.4072 | 1230042.703
7 | 2720464.8157 | 1230250.7754
8 | 2720573.2503 | 1229899.826
9 | 2720393.2439 | 1230382.698
10 | 2718701.56 | 1228632.5727
11 | 2718667.6888 | 1228630.6843
12 | 2718830.7284 | 1228593.2651
13 | 2718611.9287 | 1228637.9335
14 | 2718836.9645 | 1228628.2172
15 | 2719803.2187 | 1229820.3294
16 | 2719852.8938 | 1229861.9486
17 | 2718916.9488 | 1229387.5714
18 | 2718870.5863 | 1228790.7507
19 | 2718697.1371 | 1228819.1316
20 | 2718879.7029 | 1228735.467
21 | 2718704.1726 | 1228861.5166
22 | 2718596.8787 | 1228638.2114
23 | 2718868.5621 | 1228656.2485
24 | 2718753.1489 | 1229194.0568
25 | 2718554.7861 | 1228687.9004
26 | 2718539.5229 | 1228613.7489
27 | 2718399.2126 | 1228859.815
28 | 2718848.6542 | 1229465.7659
29 | 2718724.2462 | 1229210.3038
30 | 2718920.001 | 1229299.7963
31 | 2718911.8611 | 1229279.3841
32 | 2718849.1147 | 1228348.8062
33 | 2718876.5278 | 1228446.2975
34 | 2718943.9088 | 1228676.5484
35 | 2718981.3847 | 1228764.5118
36 | 2718377.9945 | 1228379.8147
37 | 2718408.659 | 1228370.3953
38 | 2720732.4102 | 1229897.5754
39 | 2720734.4037 | 1229894.936
40 | 2720585.1813 | 1229894.408
41 | 2721113.0231 | 1229851.9778
42 | 2721113.8882 | 1229866.785
43 | 2721170.1453 | 1230113.1392
44 | 2718485.4493 | 1230961.1834
45 | 2718541.688 | 1230950.8739
46 | 2718424.2866 | 1230970.3389
47 | 2718793.1022 | 1230869.7935
48 | 2718208.6135 | 1230975.4959
49 | 2719204.5721 | 1230728.0375
50 | 2719070.8438 | 1230629.5577
51 | 2719336.8747 | 1230758.849
52 | 2718180.1422 | 1230962.9423
53 | 2718949.8987 | 1230809.7136
54 | 2718173.5087 | 1230957.0725
55 | 2718965.9673 | 1230802.5627
56 | 2719047.4714 | 1230638.1855
57 | 2719026.9602 | 1230651.6324
58 | 2718993.4039 | 1230667.0086
59 | 2718918.1616 | 1230702.5715
60 | 2719911.2858 | 1230000.2555
61 | 2720080.7897 | 1230173.6471
62 | 2720054.3117 | 1229956.2727
63 | 2720149.9841 | 1230378.2857
64 | 2720167.3908 | 1230184.0825
65 | 2720185.4496 | 1230394.1261
66 | 2720131.9723 | 1230386.9732
67 | 2720256.8274 | 1230512.6526
68 | 2719984.0359 | 1230426.5848
69 | 2720190.0592 | 1230403.7269
70 | 2720165.8257 | 1230215.387
71 | 2720275.9251 | 1230206.9949
72 | 2720268.5134 | 1230622.5767
73 | 2720263.8564 | 1230520.4644
74 | 2720297.2723 | 1230674.322
75 | 2719855.7035 | 1230465.0386
76 | 2720031.98 | 1230385.8198
77 | 2720084.2791 | 1230677.3416
78 | 2719878.3598 | 1230815.3302
79 | 2719596.1804 | 1230761.3718
80 | 2719838.6566 | 1230838.3927
81 | 2719860.723 | 1230460.7252
82 | 2719632.6097 | 1230798.5342
83 | 2720043.3006 | 1230697.7943
84 | 2719270.4074 | 1230919.2209
85 | 2720302.5023 | 1230556.7116
86 | 2719237.5093 | 1230966.521
87 | 2718124.0642 | 1231189.2741
88 | 2718077.142 | 1231228.7956
89 | 2717842.6506 | 1231258.5338
90 | 2717949.1331 | 1231449.7968
91 | 2717815.2432 | 1231240.8878
92 | 2717813.7208 | 1231239.7234
93 | 2720293.6951 | 1230226.3809
94 | 2720278.3641 | 1230209.6575
95 | 2720401.7154 | 1230419.1982
96 | 2720408.8638 | 1230451.6804
97 | 2720436.5954 | 1230834.0588
98 | 2720456.2307 | 1230728.0606
99 | 2720745.3612 | 1230708.9203
100 | 2720504.372 | 1230670.5233
101 | 2721885.8332 | 1231337.2046
102 | 2720439.489 | 1230719.7148
103 | 2721909.3477 | 1231347.9509
104 | 2721895.7387 | 1231553.7489
105 | 2722194.6838 | 1231466.8931
106 | 2722031.665 | 1231126.7373
107 | 2721759.3821 | 1231732.8549
108 | 2722211.8076 | 1231498.0591
109 | 2722040.6508 | 1231133.3493
110 | 2721227.0998 | 1232436.4334
111 | 2718028.468 | 1232831.1247
112 | 2718187.4012 | 1232933.1972
113 | 2717891.1144 | 1231593.7426
114 | 2718260.3052 | 1233004.682
115 | 2718276.8333 | 1233004.166
116 | 2718288.1169 | 1233000.4098
117 | 2717697.0222 | 1231508.6474
118 | 2717702.8792 | 1231515.4688
119 | 2717895.2648 | 1231514.6465
120 | 2718252.0028 | 1233014.2801
121 | 2718196.6384 | 1233041.4117
122 | 2718638.9039 | 1234816.1667
123 | 2718637.4482 | 1234796.9444
124 | 2718706.7902 | 1235003.4842
125 | 2718435.1986 | 1234759.3243
126 | 2718649.5243 | 1233197.6037
127 | 2718683.7117 | 1233177.8148
128 | 2718417.7225 | 1234709.2914
129 | 2719373.7654 | 1232980.2415
130 | 2718672.6087 | 1235022.3499
131 | 2718992.813 | 1236810.2637
132 | 2719397.4339 | 1232979.0604
133 | 2719427.5996 | 1232977.554
134 | 2719578.7923 | 1232915.4439
135 | 2719823.8917 | 1232720.6232
136 | 2719554.6155 | 1232871.122
137 | 2720117.8813 | 1232873.8574
138 | 2719806.6726 | 1232694.5107
139 | 2719789.2938 | 1232648.1455
140 | 2719801.9633 | 1232540.837
141 | 2720059.5233 | 1232994.2307
142 | 2719788.2247 | 1232527.2715
143 | 2719978.8735 | 1232341.3449
144 | 2720003.9339 | 1232395.1272
145 | 2719971.7876 | 1232320.9077
146 | 2720041.0377 | 1232475.4852
147 | 2720640.8348 | 1232919.0287
148 | 2720658.1342 | 1232881.3272
149 | 2720773.158 | 1232965.0973
150 | 2720432.2063 | 1232640.8633
151 | 2720425.0057 | 1232634.768
152 | 2720958.7126 | 1232825.6801
153 | 2720740.2146 | 1233020.5061
154 | 2720915.5178 | 1232867.7685
155 | 2721212.1542 | 1232468.7881
156 | 2720713.5394 | 1233065.267
157 | 2720499.3898 | 1233315.3567
158 | 2720901.5457 | 1233286.9892
159 | 2720909.7401 | 1233288.8463
160 | 2720135.0428 | 1232390.4382
161 | 2720130.579 | 1232385.6886
162 | 2720047.8693 | 1232493.4932
163 | 2720258.7946 | 1232246.3246
164 | 2720289.9418 | 1232249.2905
165 | 2720112.3991 | 1232269.2612
166 | 2720031.8952 | 1232320.6987
167 | 2720046.0613 | 1232344.5928
168 | 2720052.5512 | 1232355.5326
169 | 2720061.349 | 1232369.5771
170 | 2720068.2872 | 1232383.8175
171 | 2720526.5243 | 1233320.6
172 | 2720414.2665 | 1230451.2895
173 | 2719632.6097 | 1230798.5342

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9894 | -0.031794 | 0.13407 | 0.064931
1 | 0.98967 | -0.03002 | 0.2117 | 0.10253
2 | 0.9908 | -0.022572 | 0 | 0
3 | 0.99101 | -0.024407 | 0 | 0
4 | 0.99079 | -0.022668 | 0.12186 | 0.059017
5 | 0.99206 | -0.019172 | 0 | 0
6 | 0.99123 | -0.025368 | 0 | 0
7 | 0.99204 | -0.019312 | 0.13056 | 0.063232
8 | 0.99196 | -0.019964 | 0.076616 | 0.037107
9 | 0.99261 | -0.023672 | 0 | 0
10 | 0.987 | -0.043325 | 0.12392 | 0.060017
11 | 0.98698 | -0.043119 | 0 | 0
12 | 0.98717 | -0.042088 | 0.11507 | 0.055733
13 | 0.98692 | -0.042588 | 0 | 0
14 | 0.98721 | -0.0424 | 0 | 0
15 | 0.99247 | -0.024572 | 0.1055 | 0.051094
16 | 0.99261 | -0.025634 | 0.082535 | 0.039974
17 | 0.98957 | -0.047743 | 0 | 0
18 | 0.98748 | -0.042883 | 0 | 0
19 | 0.98779 | -0.045441 | 0 | 0
20 | 0.98737 | -0.043736 | 0.10284 | 0.049806
21 | 0.98785 | -0.045919 | 0.11921 | 0.057736
22 | 0.98691 | -0.042497 | 0.14611 | 0.070763
23 | 0.98727 | -0.042903 | 0 | 0
24 | 0.98862 | -0.040122 | 0 | 0
25 | 0.98687 | -0.042709 | 0.11443 | 0.055419
26 | 0.98689 | -0.042638 | 0 | 0
27 | 0.98681 | -0.04313 | 0.14546 | 0.07045
28 | 0.98956 | -0.047646 | 0.083128 | 0.040261
29 | 0.98861 | -0.040065 | 0.14302 | 0.06927
30 | 0.98857 | -0.039757 | 0 | 0
31 | 0.98857 | -0.039725 | 0.11976 | 0.058003
32 | 0.98718 | -0.042964 | 0.12046 | 0.058341
33 | 0.9872 | -0.042812 | 0 | 0
34 | 0.98724 | -0.043137 | 0 | 0
35 | 0.98723 | -0.04307 | 0.062441 | 0.030241
36 | 0.98684 | -0.042209 | 0.13168 | 0.063776
37 | 0.98684 | -0.04226 | 0 | 0
38 | 0.99193 | -0.019721 | 0.10579 | 0.051236
39 | 0.99193 | -0.019725 | 0 | 0
40 | 0.99196 | -0.019951 | 0 | 0
41 | 0.99106 | -0.024009 | 0.14683 | 0.071111
42 | 0.99108 | -0.024109 | 0 | 0
43 | 0.9912 | -0.025509 | 0.11648 | 0.056415
44 | 0.99702 | 0.0055336 | 0.058142 | 0.02816
45 | 0.9971 | 0.004982 | 0 | 0
46 | 0.9969 | 0.0044823 | 0 | 0
47 | 0.99746 | 0.0024931 | 0 | 0
48 | 0.99656 | 0.0068523 | 0 | 0
49 | 0.9988 | 0.0063823 | 0.094888 | 0.045956
50 | 0.99829 | 0.0021448 | 0.12784 | 0.061918
51 | 0.9991 | 0.0041735 | 0 | 0
52 | 0.99652 | 0.0071453 | 0.19068 | 0.092352
53 | 0.9978 | 0.0055757 | 0.13491 | 0.065339
54 | 0.99651 | 0.0072087 | 0 | 0
55 | 0.99783 | 0.0053861 | 0 | 0
56 | 0.99824 | 0.0025358 | 0 | 0
57 | 0.99819 | 0.0028729 | 0.14434 | 0.069905
58 | 0.99813 | 0.0033195 | 0.13275 | 0.064293
59 | 0.998 | 0.004199 | 0 | 0
60 | 0.9931 | -0.021745 | 0.11218 | 0.05433
61 | 0.99372 | -0.026673 | 0 | 0
62 | 0.99306 | -0.022003 | 0.14002 | 0.067813
63 | 0.9948 | -0.03518 | 0 | 0
64 | 0.99348 | -0.028499 | 0.09686 | 0.046912
65 | 0.99505 | -0.037147 | 0 | 0
66 | 0.99479 | -0.035147 | 0.13477 | 0.065274
67 | 0.99453 | -0.04185 | 0 | 0
68 | 0.99601 | -0.030026 | 0 | 0
69 | 0.99505 | -0.037132 | 0.12088 | 0.058544
70 | 0.99341 | -0.029119 | 0 | 0
71 | 0.99318 | -0.027309 | 0 | 0
72 | 0.99452 | -0.041734 | 0 | 0
73 | 0.99452 | -0.041974 | 0.083914 | 0.040641
74 | 0.99451 | -0.041796 | 0.086727 | 0.042004
75 | 0.99596 | -0.02959 | 0 | 0
76 | 0.996 | -0.030117 | 0.11768 | 0.056997
77 | 0.99696 | -0.023021 | 0 | 0
78 | 0.99848 | -0.011573 | 0 | 0
79 | 0.99983 | -0.0012549 | 0 | 0
80 | 0.99847 | -0.011496 | 0.14329 | 0.069399
81 | 0.99596 | -0.029578 | 0.1503 | 0.072793
82 | 1 | 0 | -10.3691 | -4.2115
83 | 0.99695 | -0.022952 | 0.1278 | 0.061898
84 | 0.99905 | 0.0038285 | 0 | 0
85 | 0.99445 | -0.042598 | 0 | 0
86 | 0.99904 | 0.0039356 | 0.1534 | 0.074293
87 | 0.99574 | 0.012706 | 0.10151 | 0.049163
88 | 0.99575 | 0.012782 | 0 | 0
89 | 0.99579 | 0.012459 | 0 | 0
90 | 0.99563 | 0.013691 | 0 | 0
91 | 0.99582 | 0.012287 | 0.24356 | 0.11796
92 | 0.99582 | 0.012271 | 0 | 0
93 | 0.99312 | -0.02768 | 0 | 0
94 | 0.99317 | -0.027262 | 0.083608 | 0.040493
95 | 0.9926 | -0.023601 | 0.082755 | 0.04008
96 | 0.9926 | -0.023569 | 0 | 0
97 | 0.99392 | -0.047351 | 0 | 0
98 | 0.99366 | -0.064963 | 0.1113 | 0.053907
99 | 0.99298 | -0.10386 | 0.058934 | 0.028543
100 | 0.99355 | -0.065954 | 0 | 0
101 | 0.99001 | -0.30387 | 0 | 0
102 | 0.99365 | -0.064986 | 0.10155 | 0.049181
103 | 0.98998 | -0.30415 | 0.12877 | 0.062367
104 | 0.98956 | -0.33318 | 0 | 0
105 | 0.98992 | -0.30458 | 0 | 0
106 | 0.98997 | -0.30353 | 0 | 0
107 | 0.98931 | -0.33558 | 0.1059 | 0.051291
108 | 0.98991 | -0.30454 | 0.10524 | 0.050971
109 | 0.98997 | -0.30351 | 0.1102 | 0.05337
110 | 0.98757 | -0.45623 | 0 | 0
111 | 0.98411 | -0.52064 | 0.10366 | 0.050206
112 | 0.98414 | -0.52052 | 0 | 0
113 | 0.98382 | -0.5373 | 0.34425 | 0.16673
114 | 0.98416 | -0.52043 | 0 | 0
115 | 0.98416 | -0.52009 | 0.13594 | 0.065838
116 | 0.98417 | -0.52008 | 0 | 0
117 | 0.99558 | 0.013987 | 0 | 0
118 | 0.99558 | 0.013996 | 0.082201 | 0.039812
119 | 0.99557 | 0.0143 | 0.4094 | 0.19828
120 | 0.98416 | -0.52044 | 0 | 0
121 | 0.98416 | -0.52044 | 0.072257 | 0.034996
122 | 0.98395 | -0.54073 | 0.10674 | 0.051696
123 | 0.98396 | -0.54076 | 0 | 0
124 | 0.98392 | -0.5416 | 0 | 0
125 | 0.98398 | -0.54049 | 0 | 0
126 | 0.98429 | -0.51925 | 0 | 0
127 | 0.98428 | -0.51919 | 0.12576 | 0.060909
128 | 0.98399 | -0.54043 | 0.067615 | 0.032747
129 | 0.98461 | -0.51606 | 0 | 0
130 | 0.98391 | -0.54181 | 0.076135 | 0.036874
131 | 0.98376 | -0.54711 | 0.084848 | 0.041094
132 | 0.98462 | -0.51597 | 0.12596 | 0.061007
133 | 0.98463 | -0.51585 | 0 | 0
134 | 0.9847 | -0.51516 | 0 | 0
135 | 0.98484 | -0.51371 | 0 | 0
136 | 0.98468 | -0.51524 | 0.13337 | 0.064596
137 | 0.98482 | -0.51388 | 0 | 0
138 | 0.98485 | -0.51354 | 0.14757 | 0.071469
139 | 0.98488 | -0.51327 | 0 | 0
140 | 0.98494 | -0.51264 | 0 | 0
141 | 0.98479 | -0.51366 | 0.13944 | 0.067534
142 | 0.98493 | -0.51261 | 0.14121 | 0.068394
143 | 0.9852 | -0.50979 | 0 | 0
144 | 0.98525 | -0.50932 | 0 | 0
145 | 0.98519 | -0.50984 | 0.15856 | 0.076792
146 | 0.98531 | -0.50868 | 0 | 0
147 | 0.98623 | -0.46906 | 0.15267 | 0.073943
148 | 0.98624 | -0.46914 | 0 | 0
149 | 0.9864 | -0.4676 | 0 | 0
150 | 0.98571 | -0.5048 | 0.091313 | 0.044225
151 | 0.98571 | -0.50488 | 0 | 0
152 | 0.98685 | -0.46331 | 0 | 0
153 | 0.98639 | -0.46765 | 0.10481 | 0.050762
154 | 0.98684 | -0.46321 | 0.12754 | 0.061771
155 | 0.98756 | -0.45619 | 0.095439 | 0.046223
156 | 0.98639 | -0.46769 | 0 | 0
157 | 0.98637 | -0.46781 | 0 | 0
158 | 0.98635 | -0.46797 | 0 | 0
159 | 0.98635 | -0.46796 | 0.074527 | 0.036095
160 | 0.98522 | -0.50796 | 0 | 0
161 | 0.98522 | -0.50792 | 0.070836 | 0.034307
162 | 0.9853 | -0.50865 | 0.11719 | 0.056757
163 | 0.98507 | -0.50898 | 0 | 0
164 | 0.98507 | -0.50896 | 0.052266 | 0.025314
165 | 0.985 | -0.50835 | 0 | 0
166 | 0.98493 | -0.50878 | 0.14585 | 0.07064
167 | 0.98493 | -0.50871 | 0 | 0
168 | 0.98492 | -0.50868 | 0.11985 | 0.058044
169 | 0.98492 | -0.50867 | 0 | 0
170 | 0.98492 | -0.50865 | 0.087956 | 0.042599
171 | 0.98637 | -0.46775 | 0.14766 | 0.071515
172 | 0.9926 | -0.023564 | 0.079322 | 0.038417
173 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13407 | -0.064931 | 0.1341 | 0.063739 | 3.4846e-05 | -0.0011928 | 0.0043462 | 0.0043309 | 0.0043462 | 0.9894 | -0.031794 | 0.98967 | -0.03002 | 2.0696
1 | -0.3458 | -0.16627 | 0.34617 | 0.16454 | 0.00037261 | -0.0017254 | 0.011192 | 0.011167 | 0.011192 | 0.98967 | -0.03002 | 0.9908 | -0.022572 | 5.3295
2 | -0.46803 | -0.22349 | 0.46814 | 0.21529 | 0.00010628 | -0.0081979 | 0.015111 | 0.015009 | 0.015111 | 0.9908 | -0.022572 | 0.99101 | -0.024407 | 6.8687
3 | 0.12186 | 0.058943 | -0.12186 | -0.059017 | 1.7763e-06 | -7.3986e-05 | 0.0039439 | 0.0039449 | 0.0039449 | 0.9908 | -0.022572 | 0.99079 | -0.022668 | 1.8785
4 | -0.46814 | -0.21529 | 0.46816 | 0.21524 | 2.3632e-05 | -5.4234e-05 | 0.015009 | 0.015009 | 0.015009 | 0.99101 | -0.024407 | 0.99106 | -0.024009 | 7.1474
5 | 0.73216 | 0.33751 | -0.73158 | -0.33784 | 0.00058188 | -0.00033192 | 0.023459 | 0.023468 | 0.023468 | 0.99206 | -0.019172 | 0.99123 | -0.025368 | 11.1752
6 | 0.13056 | 0.063131 | -0.13056 | -0.063232 | 2.7743e-06 | -0.00010096 | 0.0042199 | 0.0042212 | 0.0042212 | 0.99206 | -0.019172 | 0.99204 | -0.019312 | 2.0101
7 | 0.18243 | 0.082924 | -0.18241 | -0.083258 | 1.7817e-05 | -0.00033411 | 0.005831 | 0.0058352 | 0.0058352 | 0.99206 | -0.019172 | 0.99196 | -0.019964 | 2.7787
8 | -1.0451 | -0.48356 | 1.0458 | 0.47406 | 0.00061555 | -0.0095059 | 0.03351 | 0.033392 | 0.03351 | 0.99206 | -0.019172 | 0.99261 | -0.023672 | 15.2316
9 | 0.11649 | 0.056302 | -0.11648 | -0.056415 | 2.4728e-06 | -0.00011307 | 0.0037679 | 0.0037693 | 0.0037693 | 0.99123 | -0.025368 | 0.9912 | -0.025509 | 1.7949
10 | 0.61509 | 0.28154 | -0.61499 | -0.286 | 9.9457e-05 | -0.0044603 | 0.019701 | 0.019755 | 0.019755 | 0.99123 | -0.025368 | 0.99108 | -0.024109 | 8.9798
11 | 0.10579 | 0.046151 | -0.10579 | -0.046458 | 1.9712e-07 | -0.00030707 | 0.0033589 | 0.0033625 | 0.0033625 | 0.99196 | -0.019964 | 0.99196 | -0.019951 | 1.5284
12 | 0.16208 | 0.07668 | -0.16208 | -0.077563 | 1.3661e-06 | -0.000883 | 0.0052145 | 0.0052256 | 0.0052256 | 0.99261 | -0.023672 | 0.9926 | -0.023601 | 2.3753
13 | -1.2078 | -0.55074 | 1.2085 | 0.5432 | 0.0006525 | -0.0075436 | 0.038606 | 0.038513 | 0.038606 | 0.99261 | -0.023672 | 0.99312 | -0.02768 | 17.5482
14 | 0.53776 | 0.24958 | -0.53774 | -0.25039 | 1.3982e-05 | -0.00080561 | 0.01734 | 0.01735 | 0.01735 | 0.987 | -0.043325 | 0.98698 | -0.043119 | 7.8862
15 | -0.66168 | -0.3096 | 0.66179 | 0.30951 | 0.00010981 | -8.8267e-05 | 0.021366 | 0.021364 | 0.021366 | 0.987 | -0.043325 | 0.98717 | -0.042088 | 10.1744
16 | 0.53774 | 0.25039 | -0.53771 | -0.25243 | 3.5484e-05 | -0.0020401 | 0.01735 | 0.017375 | 0.017375 | 0.98698 | -0.043119 | 0.98692 | -0.042588 | 7.8977
17 | -0.77686 | -0.36525 | 0.77689 | 0.36443 | 2.9859e-05 | -0.00081736 | 0.025103 | 0.025093 | 0.025103 | 0.98717 | -0.042088 | 0.98721 | -0.0424 | 11.4104
18 | 0.53771 | 0.25243 | -0.5377 | -0.25278 | 6.0517e-06 | -0.00034731 | 0.017375 | 0.017379 | 0.017379 | 0.98692 | -0.042588 | 0.98691 | -0.042497 | 7.8997
19 | -0.77689 | -0.36443 | 0.77694 | 0.3631 | 4.8467e-05 | -0.0013283 | 0.025093 | 0.025076 | 0.025093 | 0.98721 | -0.0424 | 0.98727 | -0.042903 | 11.4058
20 | -1.6405 | -0.74077 | 1.6407 | 0.73932 | 0.00023707 | -0.001454 | 0.052356 | 0.052338 | 0.052356 | 0.99247 | -0.024572 | 0.99261 | -0.025634 | 23.7981
21 | 1.535 | 0.68968 | -1.5308 | -0.68819 | 0.0042114 | 0.0014815 | 0.048948 | 0.048961 | 0.048961 | 0.99247 | -0.024572 | 0.98957 | -0.047743 | 23.315
22 | -1.7233 | -0.77929 | 1.7241 | 0.77962 | 0.00080921 | 0.00033019 | 0.055004 | 0.055002 | 0.055004 | 0.99261 | -0.025634 | 0.9931 | -0.021745 | 26.1922
23 | 1.4477 | 0.65036 | -1.4462 | -0.66196 | 0.0014793 | -0.011599 | 0.046297 | 0.046442 | 0.046442 | 0.98957 | -0.047743 | 0.98862 | -0.040122 | 21.1101
24 | 0.083129 | 0.037834 | -0.083128 | -0.040261 | 9.949e-07 | -0.002427 | 0.0026644 | 0.0026945 | 0.0026945 | 0.98957 | -0.047743 | 0.98956 | -0.047646 | 1.2248
25 | -1.0629 | -0.49132 | 1.0633 | 0.48616 | 0.00035247 | -0.0051527 | 0.034231 | 0.034167 | 0.034231 | 0.98748 | -0.042883 | 0.98779 | -0.045441 | 15.5597
26 | 1.0629 | 0.49132 | -1.0628 | -0.49131 | 0.00011698 | 8.056e-06 | 0.034231 | 0.034232 | 0.034232 | 0.98748 | -0.042883 | 0.98737 | -0.043736 | 16.3011
27 | -1.0633 | -0.48616 | 1.0633 | 0.48518 | 6.6939e-05 | -0.00098119 | 0.034167 | 0.034155 | 0.034167 | 0.98779 | -0.045441 | 0.98785 | -0.045919 | 15.5306
28 | 0.95996 | 0.4415 | -0.95985 | -0.44335 | 0.00010295 | -0.0018488 | 0.030892 | 0.030915 | 0.030915 | 0.98737 | -0.043736 | 0.98727 | -0.042903 | 14.0523
29 | -1.1825 | -0.54292 | 1.1834 | 0.54307 | 0.0008658 | 0.00015043 | 0.038025 | 0.03802 | 0.038025 | 0.98785 | -0.045919 | 0.98862 | -0.040122 | 18.1071
30 | 0.2599 | 0.12553 | -0.2599 | -0.1256 | 8.2711e-06 | -7.0536e-05 | 0.0084426 | 0.0084436 | 0.0084436 | 0.98691 | -0.042497 | 0.98687 | -0.042709 | 4.0208
31 | 0.13169 | 0.05648 | -0.13169 | -0.056552 | 1.9521e-06 | -7.1279e-05 | 0.0041913 | 0.0041922 | 0.0041922 | 0.98691 | -0.042497 | 0.98689 | -0.042638 | 1.9963
32 | 0.18291 | 0.08025 | -0.18291 | -0.080338 | 4.7434e-06 | -8.7826e-05 | 0.0058405 | 0.0058415 | 0.0058415 | 0.98727 | -0.042903 | 0.98724 | -0.043137 | 2.7817
33 | 0.14303 | 0.068498 | -0.14302 | -0.06927 | 9.4907e-07 | -0.00077177 | 0.0046306 | 0.0046404 | 0.0046404 | 0.98862 | -0.040122 | 0.98861 | -0.040065 | 2.1093
34 | 0.11977 | 0.050393 | -0.11976 | -0.05749 | 5.9745e-06 | -0.0070967 | 0.0037941 | 0.0038792 | 0.0038792 | 0.98862 | -0.040122 | 0.98857 | -0.039757 | 1.7633
35 | 0.14547 | 0.070186 | -0.14546 | -0.07045 | 9.2279e-06 | -0.00026377 | 0.0047246 | 0.004728 | 0.004728 | 0.98687 | -0.042709 | 0.98681 | -0.04313 | 2.2514
36 | 0.13169 | 0.056552 | -0.13168 | -0.063032 | 6.6607e-06 | -0.0064805 | 0.0041922 | 0.0042706 | 0.0042706 | 0.98689 | -0.042638 | 0.98684 | -0.04226 | 1.9412
37 | 0.11976 | 0.05749 | -0.11976 | -0.058003 | 4.4209e-07 | -0.00051248 | 0.0038792 | 0.0038857 | 0.0038857 | 0.98857 | -0.039757 | 0.98857 | -0.039725 | 1.7662
38 | -0.12046 | -0.058341 | 0.12046 | 0.058225 | 2.763e-06 | -0.00011609 | 0.0039139 | 0.0039124 | 0.0039139 | 0.98718 | -0.042964 | 0.9872 | -0.042812 | 1.8638
39 | -0.12046 | -0.058225 | 0.12047 | 0.052324 | 5.0869e-06 | -0.0059014 | 0.0039124 | 0.0038405 | 0.0039124 | 0.9872 | -0.042812 | 0.98724 | -0.043137 | 1.7784
40 | 0.062441 | 0.028014 | -0.062441 | -0.030241 | 5.1869e-07 | -0.0022273 | 0.0020012 | 0.0020287 | 0.0020287 | 0.98724 | -0.043137 | 0.98723 | -0.04307 | 0.92213
41 | -0.13168 | -0.063776 | 0.13168 | 0.063032 | 7.8069e-07 | -0.00074369 | 0.00428 | 0.0042706 | 0.00428 | 0.98684 | -0.042209 | 0.98684 | -0.04226 | 1.9455
42 | -0.10579 | -0.051236 | 0.10579 | 0.051158 | 5.1621e-08 | -7.7627e-05 | 0.0034208 | 0.0034198 | 0.0034208 | 0.99193 | -0.019721 | 0.99193 | -0.019725 | 1.5549
43 | -0.10579 | -0.051158 | 0.10579 | 0.046458 | 3.0706e-06 | -0.0046995 | 0.0034198 | 0.0033625 | 0.0034198 | 0.99193 | -0.019725 | 0.99196 | -0.019951 | 1.5544
44 | -0.61499 | -0.28635 | 0.61499 | 0.286 | 7.7378e-06 | -0.00034591 | 0.01976 | 0.019755 | 0.01976 | 0.99106 | -0.024009 | 0.99108 | -0.024109 | 8.9817
45 | -1.0868 | -0.47383 | 1.0869 | 0.47251 | 8.9696e-05 | -0.0013274 | 0.034327 | 0.034312 | 0.034327 | 0.99702 | 0.0055336 | 0.9971 | 0.004982 | 15.6033
46 | 1.0286 | 0.44567 | -1.0285 | -0.44568 | 0.00011609 | -6.6551e-07 | 0.032458 | 0.032459 | 0.032459 | 0.99702 | 0.0055336 | 0.9969 | 0.0044823 | 15.4568
47 | -1.0869 | -0.47251 | 1.0873 | 0.46636 | 0.00041442 | -0.0061517 | 0.034312 | 0.03424 | 0.034312 | 0.9971 | 0.004982 | 0.99746 | 0.0024931 | 15.5962
48 | 1.0285 | 0.44568 | -1.0282 | -0.45167 | 0.0003625 | -0.0059925 | 0.032459 | 0.03253 | 0.03253 | 0.9969 | 0.0044823 | 0.99656 | 0.0068523 | 14.7863
49 | -1.0873 | -0.46636 | 1.0876 | 0.46638 | 0.00035071 | 2.0168e-05 | 0.03424 | 0.034237 | 0.03424 | 0.99746 | 0.0024931 | 0.9978 | 0.0055757 | 16.3046
50 | 1.0282 | 0.45167 | -1.0281 | -0.45239 | 4.3861e-05 | -0.00072299 | 0.03253 | 0.032538 | 0.032538 | 0.99656 | 0.0068523 | 0.99652 | 0.0071453 | 14.7902
51 | 1.6289 | 0.72115 | -1.6281 | -0.72085 | 0.00078443 | 0.00029365 | 0.051487 | 0.051489 | 0.051489 | 0.9988 | 0.0063823 | 0.99829 | 0.0021448 | 24.5186
52 | -1.7238 | -0.7671 | 1.7244 | 0.76402 | 0.00053979 | -0.0030818 | 0.054532 | 0.054494 | 0.054532 | 0.9988 | 0.0063823 | 0.9991 | 0.0041735 | 24.7874
53 | 1.5003 | 0.65894 | -1.5002 | -0.65959 | 8.5533e-05 | -0.00065347 | 0.047384 | 0.047392 | 0.047392 | 0.99829 | 0.0021448 | 0.99824 | 0.0025358 | 21.5418
54 | 0.15341 | 0.072668 | -0.1534 | -0.072871 | 7.4442e-06 | -0.0002022 | 0.0049046 | 0.0049072 | 0.0049072 | 0.9991 | 0.0041735 | 0.99905 | 0.0038285 | 2.3367
55 | -1.8778 | -0.83669 | 1.8792 | 0.82977 | 0.0014495 | -0.0069209 | 0.059397 | 0.059311 | 0.059397 | 0.9991 | 0.0041735 | 0.99983 | -0.0012549 | 26.9988
56 | 0.83743 | 0.36004 | -0.83743 | -0.36025 | 8.2324e-06 | -0.00020723 | 0.026406 | 0.026408 | 0.026408 | 0.99652 | 0.0071453 | 0.99651 | 0.0072087 | 12.0038
57 | -1.2225 | -0.53171 | 1.2226 | 0.53131 | 3.4842e-05 | -0.00040677 | 0.03857 | 0.038565 | 0.03857 | 0.9978 | 0.0055757 | 0.99783 | 0.0053861 | 17.5318
58 | 0.83743 | 0.36025 | -0.83681 | -0.37567 | 0.00061749 | -0.015424 | 0.026408 | 0.02659 | 0.02659 | 0.99651 | 0.0072087 | 0.99582 | 0.012271 | 12.0865
59 | -1.2226 | -0.53131 | 1.2228 | 0.52874 | 0.00021987 | -0.0025698 | 0.038565 | 0.038535 | 0.038565 | 0.99783 | 0.0053861 | 0.998 | 0.004199 | 17.5296
60 | 1.5002 | 0.65959 | -1.5001 | -0.66015 | 7.355e-05 | -0.00056168 | 0.047392 | 0.047399 | 0.047399 | 0.99824 | 0.0025358 | 0.99819 | 0.0028729 | 21.5449
61 | 1.3558 | 0.59025 | -1.3557 | -0.5911 | 9.0434e-05 | -0.00085412 | 0.042764 | 0.042774 | 0.042774 | 0.99819 | 0.0028729 | 0.99813 | 0.0033195 | 19.4429
62 | 1.223 | 0.52681 | -1.2228 | -0.52874 | 0.00016501 | -0.0019319 | 0.038512 | 0.038535 | 0.038535 | 0.99813 | 0.0033195 | 0.998 | 0.004199 | 17.5159
63 | -1.9763 | -0.90159 | 1.9776 | 0.89622 | 0.0012981 | -0.0053678 | 0.063142 | 0.063073 | 0.063142 | 0.9931 | -0.021745 | 0.99372 | -0.026673 | 28.7011
64 | 0.14002 | 0.067641 | -0.14002 | -0.067813 | 5.45e-06 | -0.00017276 | 0.0045202 | 0.0045224 | 0.0045224 | 0.9931 | -0.021745 | 0.99306 | -0.022003 | 2.1535
65 | -3.3673 | -1.5236 | 3.3712 | 1.5188 | 0.0038887 | -0.0048143 | 0.10737 | 0.1073 | 0.10737 | 0.99372 | -0.026673 | 0.9948 | -0.03518 | 48.8041
66 | 1.3897 | 0.62741 | -1.3894 | -0.62732 | 0.00030495 | 8.8205e-05 | 0.044296 | 0.044297 | 0.044297 | 0.99372 | -0.026673 | 0.99348 | -0.028499 | 21.0938
67 | -3.506 | -1.5836 | 3.5069 | 1.5826 | 0.00093612 | -0.0010523 | 0.11164 | 0.11162 | 0.11164 | 0.9948 | -0.03518 | 0.99505 | -0.037147 | 50.7436
68 | 0.13477 | 0.064802 | -0.13477 | -0.065274 | 5.0227e-07 | -0.00047126 | 0.0043395 | 0.0043455 | 0.0043455 | 0.9948 | -0.03518 | 0.99479 | -0.035147 | 1.9752
69 | 1.2926 | 0.58041 | -1.2925 | -0.58039 | 9.4661e-05 | 2.2364e-05 | 0.041171 | 0.041172 | 0.041172 | 0.99348 | -0.028499 | 0.99341 | -0.029119 | 19.6055
70 | 4.2699 | 1.5739 | -4.2678 | -1.5967 | 0.0020793 | -0.022791 | 0.13202 | 0.13226 | 0.13226 | 0.99505 | -0.037147 | 0.99453 | -0.04185 | 20.731
71 | -7.8977 | -3.2148 | 7.9049 | 3.195 | 0.007261 | -0.019848 | 0.24738 | 0.24712 | 0.24738 | 0.99505 | -0.037147 | 0.99601 | -0.030026 | 38.7737
72 | 0.12088 | 0.058292 | -0.12088 | -0.058544 | 2.1558e-07 | -0.00025159 | 0.0038933 | 0.0038965 | 0.0038965 | 0.99505 | -0.037147 | 0.99505 | -0.037132 | 1.7711
73 | 0.086729 | 0.039055 | -0.086728 | -0.041934 | 1.2565e-06 | -0.0028792 | 0.0027609 | 0.0027962 | 0.0027962 | 0.99453 | -0.04185 | 0.99452 | -0.041734 | 1.271
74 | 4.1811 | 1.5577 | -4.181 | -1.5583 | 5.4466e-05 | -0.00062239 | 0.12951 | 0.12952 | 0.12952 | 0.99453 | -0.04185 | 0.99452 | -0.041974 | 20.3003
75 | 0.15031 | 0.06616 | -0.1503 | -0.072636 | 8.4079e-06 | -0.0064764 | 0.0047597 | 0.0048384 | 0.0048384 | 0.99601 | -0.030026 | 0.99596 | -0.02959 | 2.1993
76 | 0.11769 | 0.056923 | -0.11768 | -0.056997 | 1.6101e-06 | -7.3521e-05 | 0.0037889 | 0.0037899 | 0.0037899 | 0.99601 | -0.030026 | 0.996 | -0.030117 | 1.8047
77 | -8.1729 | -3.318 | 8.1803 | 3.2995 | 0.0073428 | -0.018571 | 0.25565 | 0.25541 | 0.25565 | 0.99601 | -0.030026 | 0.99696 | -0.023021 | 40.0711
78 | 1.2925 | 0.58039 | -1.2922 | -0.58362 | 0.00031942 | -0.0032272 | 0.041172 | 0.041211 | 0.041211 | 0.99341 | -0.029119 | 0.99318 | -0.027309 | 18.7323
79 | 1.2922 | 0.58362 | -1.2922 | -0.5837 | 8.1761e-06 | -8.25e-05 | 0.041211 | 0.041212 | 0.041212 | 0.99318 | -0.027309 | 0.99317 | -0.027262 | 18.7328
80 | 0.086728 | 0.041934 | -0.086727 | -0.042004 | 8.2498e-07 | -6.9383e-05 | 0.0027962 | 0.0027971 | 0.0027971 | 0.99452 | -0.041734 | 0.99451 | -0.041796 | 1.332
81 | 4.0971 | 1.5177 | -4.0968 | -1.5208 | 0.00026387 | -0.0031499 | 0.12682 | 0.12685 | 0.12685 | 0.99452 | -0.041974 | 0.99445 | -0.042598 | 19.8832
82 | 0.1503 | 0.072636 | -0.1503 | -0.072793 | 2.0661e-07 | -0.00015644 | 0.0048384 | 0.0048404 | 0.0048404 | 0.99596 | -0.02959 | 0.99596 | -0.029578 | 2.2002
83 | 0.1278 | 0.060811 | -0.1278 | -0.061898 | 1.0303e-06 | -0.0010865 | 0.0040982 | 0.0041118 | 0.0041118 | 0.99696 | -0.023021 | 0.99695 | -0.022952 | 1.869
84 | -8.3081 | -3.3603 | 8.3201 | 3.3309 | 0.012011 | -0.029393 | 0.2595 | 0.25911 | 0.2595 | 0.99696 | -0.023021 | 0.99848 | -0.011573 | 40.6736
85 | -8.4634 | -3.3992 | 8.4742 | 3.3736 | 0.010837 | -0.025577 | 0.26369 | 0.26335 | 0.26369 | 0.99848 | -0.011573 | 0.99983 | -0.0012549 | 41.3303
86 | 0.14329 | 0.068308 | -0.14329 | -0.069399 | 1.2922e-06 | -0.0010903 | 0.0045894 | 0.0046031 | 0.0046031 | 0.99848 | -0.011573 | 0.99847 | -0.011496 | 2.0923
87 | -10.3534 | -4.2034 | 10.3551 | 4.201 | 0.0016795 | -0.0023351 | 0.32263 | 0.32259 | 0.32263 | 0.99983 | -0.0012549 | 1 | 0 | 50.5683
88 | 0.1534 | 0.072871 | -0.1534 | -0.074293 | 1.9269e-06 | -0.0014227 | 0.0049072 | 0.0049249 | 0.0049249 | 0.99905 | 0.0038285 | 0.99904 | 0.0039356 | 2.2386
89 | 4.0968 | 1.5208 | -4.0948 | -1.5452 | 0.0020515 | -0.024414 | 0.12685 | 0.12712 | 0.12712 | 0.99445 | -0.042598 | 0.99392 | -0.047351 | 19.924
90 | -0.10151 | -0.049163 | 0.10151 | 0.049092 | 1.1684e-06 | -7.1884e-05 | 0.0032699 | 0.003269 | 0.0032699 | 0.99574 | 0.012706 | 0.99575 | 0.012782 | 1.5571
91 | -0.10151 | -0.049092 | 0.10152 | 0.041167 | 4.6359e-06 | -0.0079247 | 0.003269 | 0.0031757 | 0.003269 | 0.99575 | 0.012782 | 0.99579 | 0.012459 | 1.4859
92 | 0.49172 | 0.21735 | -0.49163 | -0.22341 | 8.3756e-05 | -0.0060614 | 0.015585 | 0.015657 | 0.015657 | 0.99579 | 0.012459 | 0.99563 | 0.013691 | 7.117
93 | -0.59323 | -0.25852 | 0.59325 | 0.25775 | 1.5275e-05 | -0.00076563 | 0.01876 | 0.018751 | 0.01876 | 0.99579 | 0.012459 | 0.99582 | 0.012287 | 8.5271
94 | 0.40943 | 0.19532 | -0.4094 | -0.19828 | 2.9102e-05 | -0.0029653 | 0.013153 | 0.01319 | 0.01319 | 0.99563 | 0.013691 | 0.99557 | 0.0143 | 5.9954
95 | 0.082206 | 0.028099 | -0.082201 | -0.039599 | 4.3106e-06 | -0.0115 | 0.0025189 | 0.0026456 | 0.0026456 | 0.99563 | 0.013691 | 0.99558 | 0.013987 | 1.2026
96 | -0.83681 | -0.37572 | 0.83681 | 0.37567 | 1.8057e-06 | -4.4758e-05 | 0.026591 | 0.02659 | 0.026591 | 0.99582 | 0.012287 | 0.99582 | 0.012271 | 12.0868
97 | -1.2085 | -0.5432 | 1.2086 | 0.54321 | 5.9957e-05 | 1.0841e-05 | 0.038513 | 0.038513 | 0.038513 | 0.99312 | -0.02768 | 0.99317 | -0.027262 | 18.3397
98 | 0.079322 | 0.037483 | -0.079322 | -0.03829 | 2.9952e-07 | -0.00080746 | 0.0025515 | 0.0025616 | 0.0025616 | 0.9926 | -0.023601 | 0.9926 | -0.023569 | 1.1644
99 | 0.079322 | 0.03829 | -0.079322 | -0.038417 | 4.7343e-08 | -0.00012704 | 0.0025616 | 0.0025632 | 0.0025632 | 0.9926 | -0.023569 | 0.9926 | -0.023564 | 1.1651
100 | 4.0948 | 1.5452 | -4.0942 | -1.5437 | 0.00062186 | 0.0015251 | 0.12712 | 0.12712 | 0.12712 | 0.99392 | -0.047351 | 0.99366 | -0.064963 | 19.708
101 | 0.10155 | 0.049159 | -0.10155 | -0.049181 | 3.5809e-07 | -2.1825e-05 | 0.0032776 | 0.0032779 | 0.0032779 | 0.99366 | -0.064963 | 0.99365 | -0.064986 | 1.5609
102 | 3.8813 | 1.4406 | -3.8809 | -1.4459 | 0.00039962 | -0.0053179 | 0.12028 | 0.12033 | 0.12033 | 0.99366 | -0.064963 | 0.99355 | -0.065954 | 18.8608
103 | -3.8796 | -1.4429 | 3.8809 | 1.4459 | 0.0012615 | 0.0030594 | 0.12034 | 0.12033 | 0.12034 | 0.99298 | -0.10386 | 0.99355 | -0.065954 | 18.6566
104 | 3.8207 | 1.4143 | -3.8142 | -1.3986 | 0.0065219 | 0.015768 | 0.11844 | 0.11846 | 0.11846 | 0.99298 | -0.10386 | 0.99001 | -0.30387 | 18.3656
105 | 0.1102 | 0.045848 | -0.1102 | -0.05311 | 5.1412e-06 | -0.0072618 | 0.0034803 | 0.0035671 | 0.0035671 | 0.99001 | -0.30387 | 0.98997 | -0.30353 | 1.6214
106 | 3.704 | 1.3527 | -3.7039 | -1.3543 | 0.00010537 | -0.0015288 | 0.11498 | 0.115 | 0.115 | 0.99001 | -0.30387 | 0.98998 | -0.30415 | 18.0246
107 | 3.4699 | 1.2421 | -3.469 | -1.2401 | 0.0008504 | 0.0020075 | 0.10747 | 0.10747 | 0.10747 | 0.98998 | -0.30415 | 0.98956 | -0.33318 | 16.662
108 | 0.10525 | 0.049781 | -0.10524 | -0.050138 | 6.3569e-06 | -0.00035768 | 0.003395 | 0.0033995 | 0.0033995 | 0.98998 | -0.30415 | 0.98992 | -0.30458 | 1.6188
109 | 3.469 | 1.2401 | -3.4682 | -1.2535 | 0.00080515 | -0.013406 | 0.10747 | 0.10761 | 0.10761 | 0.98956 | -0.33318 | 0.98931 | -0.33558 | 16.8663
110 | 0.10524 | 0.050138 | -0.10524 | -0.050971 | 5.5104e-07 | -0.00083291 | 0.0033995 | 0.0034101 | 0.0034101 | 0.98992 | -0.30458 | 0.98991 | -0.30454 | 1.55
111 | 0.1102 | 0.05311 | -0.1102 | -0.05337 | 1.8933e-07 | -0.0002605 | 0.0035671 | 0.0035704 | 0.0035704 | 0.98997 | -0.30353 | 0.98997 | -0.30351 | 1.6229
112 | 3.3623 | 1.2022 | -3.3589 | -1.1942 | 0.0034196 | 0.0080041 | 0.10419 | 0.1042 | 0.1042 | 0.98931 | -0.33558 | 0.98757 | -0.45623 | 16.1557
113 | 0.095439 | 0.045335 | -0.095439 | -0.046223 | 4.8757e-07 | -0.00088819 | 0.0030885 | 0.0030998 | 0.0030998 | 0.98757 | -0.45623 | 0.98756 | -0.45619 | 1.409
114 | 3.2634 | 1.1489 | -3.2612 | -1.1905 | 0.0022228 | -0.041638 | 0.10113 | 0.10156 | 0.10156 | 0.98757 | -0.45623 | 0.98685 | -0.46331 | 15.9178
115 | -0.44796 | -0.21542 | 0.44798 | 0.20395 | 1.2264e-05 | -0.011467 | 0.014581 | 0.014438 | 0.014581 | 0.98411 | -0.52064 | 0.98414 | -0.52052 | 2.2854
116 | 0.3443 | 0.16521 | -0.34425 | -0.16673 | 5.588e-05 | -0.0015159 | 0.011202 | 0.011223 | 0.011223 | 0.98411 | -0.52064 | 0.98382 | -0.5373 | 1.7401
117 | -0.44798 | -0.20395 | 0.44798 | 0.19729 | 7.0132e-06 | -0.0066589 | 0.014438 | 0.014358 | 0.014438 | 0.98414 | -0.52052 | 0.98416 | -0.52043 | 2.263
118 | 0.072257 | 0.030255 | -0.072257 | -0.031229 | 2.6227e-08 | -0.00097367 | 0.0022977 | 0.0023089 | 0.0023089 | 0.98416 | -0.52043 | 0.98416 | -0.52044 | 0.3619
119 | -0.52024 | -0.22755 | 0.52024 | 0.22753 | 1.6376e-06 | -1.7736e-05 | 0.016656 | 0.016655 | 0.016656 | 0.98416 | -0.52043 | 0.98416 | -0.52009 | 2.5823
120 | -0.65618 | -0.29337 | 0.65618 | 0.29264 | 1.6286e-06 | -0.00072098 | 0.021083 | 0.021075 | 0.021083 | 0.98416 | -0.52009 | 0.98417 | -0.52008 | 3.3046
121 | -0.65618 | -0.29264 | 0.65626 | 0.25773 | 7.7309e-05 | -0.034915 | 0.021075 | 0.020678 | 0.021075 | 0.98417 | -0.52008 | 0.98429 | -0.51925 | 3.3032
122 | 0.082201 | 0.039599 | -0.082201 | -0.039812 | 8.4102e-08 | -0.00021275 | 0.0026456 | 0.0026483 | 0.0026483 | 0.99558 | 0.013987 | 0.99558 | 0.013996 | 1.2038
123 | 0.072257 | 0.031229 | -0.072257 | -0.034996 | 1.0396e-07 | -0.0037669 | 0.0023089 | 0.0023549 | 0.0023549 | 0.98416 | -0.52044 | 0.98416 | -0.52044 | 0.36911
124 | -0.10674 | -0.051696 | 0.10674 | 0.051251 | 3.1112e-07 | -0.00044559 | 0.0034795 | 0.0034738 | 0.0034795 | 0.98395 | -0.54073 | 0.98396 | -0.54076 | 1.5816
125 | 0.161 | 0.05482 | -0.16099 | -0.075659 | 5.3576e-06 | -0.020838 | 0.0049897 | 0.005219 | 0.005219 | 0.98396 | -0.54076 | 0.98392 | -0.5416 | 1.2397
126 | -0.26774 | -0.10607 | 0.26775 | 0.086431 | 6.9521e-06 | -0.01964 | 0.008449 | 0.0082541 | 0.008449 | 0.98396 | -0.54076 | 0.98398 | -0.54049 | 1.3243
127 | 0.16099 | 0.075659 | -0.16099 | -0.075707 | 7.5811e-07 | -4.7824e-05 | 0.005219 | 0.0052197 | 0.0052197 | 0.98392 | -0.5416 | 0.98391 | -0.54181 | 1.2731
128 | -0.26775 | -0.086431 | 0.26775 | 0.083132 | 1.1379e-06 | -0.0032994 | 0.0082541 | 0.0082249 | 0.0082541 | 0.98398 | -0.54049 | 0.98399 | -0.54043 | 1.2937
129 | 0.12576 | 0.05999 | -0.12576 | -0.060909 | 8.8816e-07 | -0.00091864 | 0.0040865 | 0.0040982 | 0.0040982 | 0.98429 | -0.51925 | 0.98428 | -0.51919 | 1.8628
130 | 0.33542 | 0.11399 | -0.33536 | -0.11588 | 5.9049e-05 | -0.0018887 | 0.01039 | 0.010409 | 0.010409 | 0.98429 | -0.51925 | 0.98399 | -0.54043 | 1.6139
131 | -1.1174 | -0.43171 | 1.1178 | 0.37535 | 0.0003484 | -0.056357 | 0.035134 | 0.03457 | 0.035134 | 0.98429 | -0.51925 | 0.98461 | -0.51606 | 5.5068
132 | -1.1178 | -0.37535 | 1.1178 | 0.37392 | 8.7226e-06 | -0.0014344 | 0.03457 | 0.034557 | 0.03457 | 0.98461 | -0.51606 | 0.98462 | -0.51597 | 5.4186
133 | 0.084858 | 0.038832 | -0.084848 | -0.041094 | 9.8058e-06 | -0.0022614 | 0.002738 | 0.0027664 | 0.0027664 | 0.98391 | -0.54181 | 0.98376 | -0.54711 | 0.67474
134 | -1.2438 | -0.43493 | 1.2438 | 0.4331 | 1.388e-05 | -0.0018266 | 0.03863 | 0.038613 | 0.03863 | 0.98462 | -0.51597 | 0.98463 | -0.51585 | 6.0549
135 | -1.2438 | -0.4331 | 1.2439 | 0.42305 | 7.6163e-05 | -0.010054 | 0.038613 | 0.038516 | 0.038613 | 0.98463 | -0.51585 | 0.9847 | -0.51516 | 6.0521
136 | -1.3772 | -0.48758 | 1.3774 | 0.46817 | 0.00018076 | -0.019414 | 0.042831 | 0.042643 | 0.042831 | 0.9847 | -0.51516 | 0.98484 | -0.51371 | 6.7133
137 | 0.13338 | 0.064538 | -0.13337 | -0.064596 | 1.6975e-06 | -5.7377e-05 | 0.0043438 | 0.0043445 | 0.0043445 | 0.9847 | -0.51516 | 0.98468 | -0.51524 | 2.0688
138 | 0.13945 | 0.039222 | -0.13944 | -0.064377 | 2.4252e-06 | -0.025155 | 0.004246 | 0.004502 | 0.004502 | 0.98484 | -0.51371 | 0.98482 | -0.51388 | 0.70564
139 | -1.5169 | -0.50739 | 1.5169 | 0.5055 | 2.1219e-05 | -0.0018926 | 0.046884 | 0.046866 | 0.046884 | 0.98484 | -0.51371 | 0.98485 | -0.51354 | 7.3485
140 | 0.13944 | 0.064377 | -0.13944 | -0.067534 | 3.7217e-06 | -0.0031564 | 0.004502 | 0.0045416 | 0.0045416 | 0.98482 | -0.51388 | 0.98479 | -0.51366 | 2.0644
141 | -1.6644 | -0.57697 | 1.6645 | 0.57397 | 4.0767e-05 | -0.0029944 | 0.051635 | 0.051607 | 0.051635 | 0.98485 | -0.51354 | 0.98488 | -0.51327 | 8.0933
142 | -1.6645 | -0.57397 | 1.6646 | 0.56711 | 9.3241e-05 | -0.006862 | 0.051607 | 0.051541 | 0.051607 | 0.98488 | -0.51327 | 0.98494 | -0.51264 | 8.0888
143 | 0.14122 | 0.067947 | -0.14121 | -0.068394 | 5.4364e-07 | -0.00044638 | 0.0045931 | 0.0045988 | 0.0045988 | 0.98494 | -0.51264 | 0.98493 | -0.51261 | 2.0903
144 | -1.8058 | -0.63506 | 1.8062 | 0.60653 | 0.00045695 | -0.028529 | 0.056104 | 0.055829 | 0.056104 | 0.98494 | -0.51264 | 0.9852 | -0.50979 | 8.7937
145 | -1.9648 | -0.6833 | 1.9649 | 0.67886 | 8.428e-05 | -0.0044331 | 0.060953 | 0.06091 | 0.060953 | 0.9852 | -0.50979 | 0.98525 | -0.50932 | 9.5538
146 | 0.15856 | 0.076767 | -0.15856 | -0.076792 | 1.0269e-06 | -2.4421e-05 | 0.0051618 | 0.0051621 | 0.0051621 | 0.9852 | -0.50979 | 0.98519 | -0.50984 | 2.4581
147 | -1.9649 | -0.67886 | 1.965 | 0.67299 | 0.0001115 | -0.0058753 | 0.06091 | 0.060854 | 0.06091 | 0.98525 | -0.50932 | 0.98531 | -0.50868 | 9.547
148 | 0.11719 | 0.056311 | -0.11719 | -0.056757 | 3.7359e-07 | -0.00044626 | 0.0038092 | 0.0038149 | 0.0038149 | 0.98531 | -0.50868 | 0.9853 | -0.50865 | 1.734
149 | -2.5591 | -0.95069 | 2.5601 | 0.921 | 0.0009756 | -0.029683 | 0.079983 | 0.079679 | 0.079983 | 0.98531 | -0.50868 | 0.98571 | -0.50488 | 12.5365
150 | 0.47691 | 0.22139 | -0.47687 | -0.22453 | 4.3164e-05 | -0.0031372 | 0.015405 | 0.015444 | 0.015444 | 0.98531 | -0.50868 | 0.98522 | -0.50796 | 7.0199
151 | -0.15267 | -0.073943 | 0.15268 | 0.072971 | 1.3758e-06 | -0.00097269 | 0.0049654 | 0.0049531 | 0.0049654 | 0.98623 | -0.46906 | 0.98624 | -0.46914 | 2.257
152 | -2.8049 | -1.0394 | 2.8053 | 1.0283 | 0.00043813 | -0.011074 | 0.087556 | 0.087441 | 0.087556 | 0.98624 | -0.46914 | 0.9864 | -0.4676 | 13.7234
153 | 2.6522 | 0.96638 | -2.6514 | -0.96467 | 0.00080418 | 0.0017191 | 0.082624 | 0.082629 | 0.082629 | 0.98624 | -0.46914 | 0.98571 | -0.5048 | 12.8106
154 | -3.1323 | -1.1573 | 3.1337 | 1.1301 | 0.0013444 | -0.027186 | 0.097726 | 0.097446 | 0.097726 | 0.9864 | -0.4676 | 0.98685 | -0.46331 | 15.3176
155 | 0.32701 | 0.12905 | -0.327 | -0.13298 | 2.1159e-06 | -0.0039373 | 0.010288 | 0.010331 | 0.010331 | 0.9864 | -0.4676 | 0.98639 | -0.46765 | 1.6193
156 | 2.5601 | 0.92044 | -2.5601 | -0.921 | 1.8475e-05 | -0.00056456 | 0.079673 | 0.079679 | 0.079679 | 0.98571 | -0.5048 | 0.98571 | -0.50488 | 12.4889
157 | 0.12754 | 0.06037 | -0.12754 | -0.061771 | 1.3767e-06 | -0.001401 | 0.0041277 | 0.0041454 | 0.0041454 | 0.98685 | -0.46331 | 0.98684 | -0.46321 | 1.8843
158 | 0.22219 | 0.082222 | -0.22219 | -0.085405 | 7.7722e-07 | -0.0031831 | 0.0069336 | 0.0069665 | 0.0069665 | 0.98639 | -0.46765 | 0.98639 | -0.46769 | 1.0919
159 | 0.14766 | 0.04984 | -0.14766 | -0.070808 | 2.3098e-06 | -0.020968 | 0.004561 | 0.0047926 | 0.0047926 | 0.98639 | -0.46769 | 0.98637 | -0.46781 | 0.7512
160 | 0.07453 | 0.035565 | -0.074527 | -0.035901 | 3.0306e-06 | -0.00033574 | 0.0024168 | 0.0024211 | 0.0024211 | 0.98639 | -0.46769 | 0.98635 | -0.46797 | 1.1529
161 | 0.14766 | 0.070808 | -0.14766 | -0.071515 | 9.3483e-07 | -0.00070658 | 0.0047926 | 0.0048016 | 0.0048016 | 0.98637 | -0.46781 | 0.98637 | -0.46775 | 2.1826
162 | 0.074527 | 0.035901 | -0.074527 | -0.036095 | 6.5631e-08 | -0.00019459 | 0.0024211 | 0.0024236 | 0.0024236 | 0.98635 | -0.46797 | 0.98635 | -0.46796 | 1.1016
163 | 0.47687 | 0.22453 | -0.47687 | -0.22468 | 2.0728e-06 | -0.00015024 | 0.015444 | 0.015446 | 0.015446 | 0.98522 | -0.50796 | 0.98522 | -0.50792 | 7.0208
164 | 0.40603 | 0.19037 | -0.40597 | -0.19055 | 5.8265e-05 | -0.00018291 | 0.01314 | 0.013142 | 0.013142 | 0.98522 | -0.50792 | 0.98507 | -0.50898 | 6.2583
165 | 0.35371 | 0.16596 | -0.35368 | -0.1695 | 2.6883e-05 | -0.0035369 | 0.01145 | 0.011494 | 0.011494 | 0.98507 | -0.50898 | 0.985 | -0.50835 | 5.2246
166 | 0.052266 | 0.024591 | -0.052266 | -0.025314 | 1.1997e-07 | -0.00072275 | 0.0016927 | 0.0017019 | 0.0017019 | 0.98507 | -0.50898 | 0.98507 | -0.50896 | 0.77357
167 | 0.35368 | 0.1695 | -0.35366 | -0.16959 | 2.2491e-05 | -9.6558e-05 | 0.011494 | 0.011496 | 0.011496 | 0.985 | -0.50835 | 0.98493 | -0.50878 | 5.4741
168 | 0.2078 | 0.098954 | -0.2078 | -0.099596 | 1.6884e-06 | -0.00064243 | 0.0067459 | 0.006754 | 0.006754 | 0.98493 | -0.50878 | 0.98493 | -0.50871 | 3.07
169 | 0.2078 | 0.099596 | -0.2078 | -0.09989 | 7.745e-07 | -0.00029418 | 0.006754 | 0.0067577 | 0.0067577 | 0.98493 | -0.50871 | 0.98492 | -0.50868 | 3.0717
170 | 0.087956 | 0.041846 | -0.087956 | -0.04223 | 1.8048e-07 | -0.0003835 | 0.0028548 | 0.0028597 | 0.0028597 | 0.98492 | -0.50868 | 0.98492 | -0.50867 | 1.2999
171 | 0.087956 | 0.04223 | -0.087956 | -0.042599 | 1.7437e-07 | -0.00036928 | 0.0028597 | 0.0028644 | 0.0028644 | 0.98492 | -0.50867 | 0.98492 | -0.50865 | 1.302

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 10.4495 | 4.2505

## res_load
| p_mw | q_mvar
0 | 0.13407 | 0.064931
1 | 0.2117 | 0.10253
2 | 0.12186 | 0.059017
3 | 0.13056 | 0.063232
4 | 0.076616 | 0.037107
5 | 0.12392 | 0.060017
6 | 0.11507 | 0.055733
7 | 0.1055 | 0.051094
8 | 0.082535 | 0.039974
9 | 0.10284 | 0.049806
10 | 0.11921 | 0.057736
11 | 0.14611 | 0.070763
12 | 0.11443 | 0.055419
13 | 0.14546 | 0.07045
14 | 0.083128 | 0.040261
15 | 0.14302 | 0.06927
16 | 0.11976 | 0.058003
17 | 0.12046 | 0.058341
18 | 0.062441 | 0.030241
19 | 0.13168 | 0.063776
20 | 0.10579 | 0.051236
21 | 0.14683 | 0.071111
22 | 0.11648 | 0.056415
23 | 0.058142 | 0.02816
24 | 0.094888 | 0.045956
25 | 0.12784 | 0.061918
26 | 0.19068 | 0.092352
27 | 0.13491 | 0.065339
28 | 0.14434 | 0.069905
29 | 0.13275 | 0.064293
30 | 0.11218 | 0.05433
31 | 0.14002 | 0.067813
32 | 0.09686 | 0.046912
33 | 0.13477 | 0.065274
34 | 0.12088 | 0.058544
35 | 0.083914 | 0.040641
36 | 0.086727 | 0.042004
37 | 0.11768 | 0.056997
38 | 0.14329 | 0.069399
39 | 0.1503 | 0.072793
40 | 0.080407 | 0.038943
41 | 0.1278 | 0.061898
42 | 0.1534 | 0.074293
43 | 0.10151 | 0.049163
44 | 0.24356 | 0.11796
45 | 0.083608 | 0.040493
46 | 0.082755 | 0.04008
47 | 0.1113 | 0.053907
48 | 0.058934 | 0.028543
49 | 0.10155 | 0.049181
50 | 0.12877 | 0.062367
51 | 0.1059 | 0.051291
52 | 0.10524 | 0.050971
53 | 0.1102 | 0.05337
54 | 0.10366 | 0.050206
55 | 0.34425 | 0.16673
56 | 0.13594 | 0.065838
57 | 0.082201 | 0.039812
58 | 0.4094 | 0.19828
59 | 0.072257 | 0.034996
60 | 0.10674 | 0.051696
61 | 0.12576 | 0.060909
62 | 0.067615 | 0.032747
63 | 0.076135 | 0.036874
64 | 0.084848 | 0.041094
65 | 0.12596 | 0.061007
66 | 0.13337 | 0.064596
67 | 0.14757 | 0.071469
68 | 0.13944 | 0.067534
69 | 0.14121 | 0.068394
70 | 0.15856 | 0.076792
71 | 0.15267 | 0.073943
72 | 0.091313 | 0.044225
73 | 0.10481 | 0.050762
74 | 0.12754 | 0.061771
75 | 0.095439 | 0.046223
76 | 0.074527 | 0.036095
77 | 0.070836 | 0.034307
78 | 0.11719 | 0.056757
79 | 0.052266 | 0.025314
80 | 0.14585 | 0.07064
81 | 0.11985 | 0.058044
82 | 0.087956 | 0.042599
83 | 0.14766 | 0.071515
84 | 0.079322 | 0.038417

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1