## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_114_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_114_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_114_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_114_0_node_5 | 20 | n |  | TRUE
4 | bus_MV_114_0_node_7 | 20 | n |  | TRUE
5 | bus_MV_114_0_node_6 | 20 | n |  | TRUE
6 | bus_MV_114_0_node_39 | 20 | n |  | TRUE
7 | bus_MV_114_0_node_4 | 20 | n |  | TRUE
8 | bus_MV_114_0_node_25 | 20 | n |  | TRUE
9 | bus_MV_114_0_node_37 | 20 | n |  | TRUE
10 | bus_MV_114_0_node_16 | 20 | n |  | TRUE
11 | bus_MV_114_0_node_3 | 20 | n |  | TRUE
12 | bus_MV_114_0_node_11 | 20 | n |  | TRUE
13 | bus_MV_114_0_node_9 | 20 | n |  | TRUE
14 | bus_MV_114_0_node_10 | 20 | n |  | TRUE
15 | bus_MV_114_0_node_12 | 20 | n |  | TRUE
16 | bus_MV_114_0_node_8 | 20 | n |  | TRUE
17 | bus_MV_114_0_node_17 | 20 | n |  | TRUE
18 | bus_MV_114_0_node_76 | 20 | n |  | TRUE
19 | bus_MV_114_0_node_13 | 20 | n |  | TRUE
20 | bus_MV_114_0_node_14 | 20 | n |  | TRUE
21 | bus_MV_114_0_node_15 | 20 | n |  | TRUE
22 | bus_MV_114_0_node_19 | 20 | n |  | TRUE
23 | bus_MV_114_0_node_18 | 20 | n |  | TRUE
24 | bus_MV_114_0_node_72 | 20 | n |  | TRUE
25 | bus_MV_114_0_node_73 | 20 | n |  | TRUE
26 | bus_MV_114_0_node_74 | 20 | n |  | TRUE
27 | bus_MV_114_0_node_56 | 20 | n |  | TRUE
28 | bus_MV_114_0_node_57 | 20 | n |  | TRUE
29 | bus_MV_114_0_node_20 | 20 | n |  | TRUE
30 | bus_MV_114_0_node_22 | 20 | n |  | TRUE
31 | bus_MV_114_0_node_23 | 20 | n |  | TRUE
32 | bus_MV_114_0_node_21 | 20 | n |  | TRUE
33 | bus_MV_114_0_node_32 | 20 | n |  | TRUE
34 | bus_MV_114_0_node_33 | 20 | n |  | TRUE
35 | bus_MV_114_0_node_27 | 20 | n |  | TRUE
36 | bus_MV_114_0_node_35 | 20 | n |  | TRUE
37 | bus_MV_114_0_node_24 | 20 | n |  | TRUE
38 | bus_MV_114_0_node_28 | 20 | n |  | TRUE
39 | bus_MV_114_0_node_29 | 20 | n |  | TRUE
40 | bus_MV_114_0_node_34 | 20 | n |  | TRUE
41 | bus_MV_114_0_node_30 | 20 | n |  | TRUE
42 | bus_MV_114_0_node_31 | 20 | n |  | TRUE
43 | bus_MV_114_0_node_36 | 20 | n |  | TRUE
44 | bus_MV_114_0_node_38 | 20 | n |  | TRUE
45 | bus_MV_114_0_node_55 | 20 | n |  | TRUE
46 | bus_MV_114_0_node_77 | 20 | n |  | TRUE
47 | bus_MV_114_0_node_54 | 20 | n |  | TRUE
48 | bus_MV_114_0_node_40 | 20 | n |  | TRUE
49 | bus_MV_114_0_node_41 | 20 | n |  | TRUE
50 | bus_MV_114_0_node_42 | 20 | n |  | TRUE
51 | bus_MV_114_0_node_43 | 20 | n |  | TRUE
52 | bus_MV_114_0_node_46 | 20 | n |  | TRUE
53 | bus_MV_114_0_node_66 | 20 | n |  | TRUE
54 | bus_MV_114_0_node_63 | 20 | n |  | TRUE
55 | bus_MV_114_0_node_44 | 20 | n |  | TRUE
56 | bus_MV_114_0_node_68 | 20 | n |  | TRUE
57 | bus_MV_114_0_node_70 | 20 | n |  | TRUE
58 | bus_MV_114_0_node_45 | 20 | n |  | TRUE
59 | bus_MV_114_0_node_47 | 20 | n |  | TRUE
60 | bus_MV_114_0_node_48 | 20 | n |  | TRUE
61 | bus_MV_114_0_node_50 | 20 | n |  | TRUE
62 | bus_MV_114_0_node_60 | 20 | n |  | TRUE
63 | bus_MV_114_0_node_67 | 20 | n |  | TRUE
64 | bus_MV_114_0_node_64 | 20 | n |  | TRUE
65 | bus_MV_114_0_node_62 | 20 | n |  | TRUE
66 | bus_MV_114_0_node_69 | 20 | n |  | TRUE
67 | bus_MV_114_0_node_71 | 20 | n |  | TRUE
68 | bus_MV_114_0_node_49 | 20 | n |  | TRUE
69 | bus_MV_114_0_node_51 | 20 | n |  | TRUE
70 | bus_MV_114_0_node_59 | 20 | n |  | TRUE
71 | bus_MV_114_0_node_61 | 20 | n |  | TRUE
72 | bus_MV_114_0_node_58 | 20 | n |  | TRUE
73 | bus_MV_114_0_node_52 | 20 | n |  | TRUE
74 | bus_MV_114_0_node_65 | 20 | n |  | TRUE
75 | bus_HV_114_0_node_38 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_114_0_load_0 | 0 | 0.28312 | 0.13712 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_114_0_load_5 | 3 | 0.30638 | 0.14839 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_114_0_load_4 | 7 | 0.12739 | 0.061698 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_114_0_load_37 | 9 | 0.14878 | 0.072059 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_114_0_load_16 | 10 | 0.22749 | 0.11018 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_114_0_load_11 | 12 | 0.37642 | 0.18231 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_114_0_load_12 | 15 | 0.39186 | 0.18979 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_114_0_load_17 | 17 | 0.40048 | 0.19396 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_114_0_load_76 | 18 | 0.11771 | 0.05701 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_114_0_load_13 | 19 | 0.33521 | 0.16235 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_114_0_load_18 | 23 | 0.39123 | 0.18948 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_114_0_load_72 | 24 | 0.32237 | 0.15613 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_114_0_load_74 | 26 | 0.35602 | 0.17243 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_114_0_load_56 | 27 | 0.4095 | 0.19833 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_114_0_load_20 | 29 | 0.1501 | 0.072697 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_114_0_load_21 | 32 | 0.11971 | 0.057977 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_114_0_load_32 | 33 | 0.14922 | 0.07227 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_114_0_load_35 | 36 | 0.16417 | 0.07951 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_114_0_load_24 | 37 | 0.14691 | 0.071149 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_114_0_load_34 | 40 | 0.16185 | 0.078387 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_114_0_load_31 | 42 | 0.14821 | 0.071784 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_114_0_load_36 | 43 | 0.091681 | 0.044403 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_114_0_load_77 | 46 | 0.37382 | 0.18105 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_114_0_load_40 | 48 | 0.28566 | 0.13835 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_114_0_load_66 | 53 | 0.20239 | 0.098022 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_114_0_load_68 | 56 | 0.1265 | 0.061266 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_114_0_load_70 | 57 | 0.28013 | 0.13567 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_114_0_load_48 | 60 | 0.40597 | 0.19662 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_114_0_load_60 | 62 | 0.36281 | 0.17571 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_114_0_load_67 | 63 | 1.0935 | 0.52961 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_114_0_load_62 | 65 | 2.777 | 1.3449 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_114_0_load_69 | 66 | 0.1034 | 0.050079 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_114_0_load_71 | 67 | 0.17981 | 0.087087 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_114_0_load_59 | 70 | 0.26101 | 0.12641 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_114_0_load_61 | 71 | 0.26359 | 0.12766 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_114_0_load_52 | 73 | 0.37455 | 0.1814 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_114_0_load_65 | 74 | 3.0828 | 1.4931 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_114_0_line_0 |  | 0 | 1 | 0.18089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_114_0_line_1 |  | 1 | 2 | 0.12417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_114_0_line_2 |  | 2 | 10 | 0.089224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_114_0_line_3 |  | 2 | 4 | 0.10606 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_114_0_line_4 |  | 3 | 4 | 0.02603 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_114_0_line_5 |  | 3 | 5 | 0.034962 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_114_0_line_6 |  | 4 | 13 | 0.2185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_114_0_line_7 |  | 4 | 14 | 0.068854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_114_0_line_8 |  | 5 | 11 | 0.013486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_114_0_line_9 |  | 6 | 7 | 1.5435 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_114_0_line_10 |  | 6 | 8 | 3.6698 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_114_0_line_11 |  | 6 | 9 | 0.085635 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
12 | MV_114_0_line_12 |  | 7 | 15 | 0.38938 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_114_0_line_13 |  | 8 | 38 | 0.13689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_114_0_line_14 |  | 9 | 44 | 0.011283 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
15 | MV_114_0_line_15 |  | 11 | 12 | 0.045915 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_114_0_line_16 |  | 13 | 17 | 0.10901 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_114_0_line_17 |  | 14 | 19 | 0.030078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_114_0_line_18 |  | 15 | 16 | 0.16726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_114_0_line_19 |  | 16 | 17 | 0.17069 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_114_0_line_20 |  | 17 | 18 | 0.8011 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_114_0_line_21 |  | 19 | 20 | 0.036759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_114_0_line_22 |  | 20 | 21 | 0.16935 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_114_0_line_23 |  | 21 | 22 | 0.35632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_114_0_line_24 |  | 21 | 23 | 0.12447 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_114_0_line_25 |  | 22 | 24 | 0.071196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_114_0_line_26 |  | 22 | 25 | 0.11987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_114_0_line_27 |  | 25 | 26 | 0.065968 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_114_0_line_28 |  | 27 | 28 | 0.003745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_114_0_line_29 |  | 28 | 72 | 0.26966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_114_0_line_30 |  | 29 | 30 | 0.11595 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_114_0_line_31 |  | 30 | 31 | 0.09895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_114_0_line_32 |  | 30 | 32 | 0.1908 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_114_0_line_33 |  | 31 | 36 | 0.060014 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_114_0_line_34 |  | 33 | 34 | 0.23366 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_114_0_line_35 |  | 33 | 35 | 0.14671 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_114_0_line_36 |  | 34 | 36 | 0.010465 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_114_0_line_37 |  | 35 | 41 | 0.4018 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_114_0_line_38 |  | 35 | 37 | 0.15828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_114_0_line_39 |  | 37 | 38 | 0.053723 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_114_0_line_40 |  | 37 | 39 | 0.16913 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_114_0_line_41 |  | 37 | 40 | 0.079434 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_114_0_line_42 |  | 39 | 42 | 0.066331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_114_0_line_43 |  | 41 | 43 | 0.086216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_114_0_line_44 |  | 44 | 45 | 0.88737 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
45 | MV_114_0_line_45 |  | 45 | 46 | 0.021838 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
46 | MV_114_0_line_46 |  | 45 | 47 | 0.017949 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_114_0_line_47 |  | 46 | 52 | 0.003837 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
48 | MV_114_0_line_48 |  | 47 | 73 | 0.032133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_114_0_line_49 |  | 48 | 49 | 0.005573 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_114_0_line_50 |  | 49 | 50 | 0.41162 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
51 | MV_114_0_line_51 |  | 49 | 51 | 0.28829 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_114_0_line_52 |  | 49 | 52 | 0.39449 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
53 | MV_114_0_line_53 |  | 50 | 53 | 0.21932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_114_0_line_54 |  | 50 | 54 | 0.17457 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
55 | MV_114_0_line_55 |  | 51 | 55 | 0.58879 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_114_0_line_56 |  | 51 | 56 | 0.031388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_114_0_line_57 |  | 52 | 59 | 0.24492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_114_0_line_58 |  | 53 | 63 | 0.052338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_114_0_line_59 |  | 54 | 64 | 0.062681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_114_0_line_60 |  | 54 | 65 | 0.039976 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_114_0_line_61 |  | 55 | 57 | 0.080406 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_114_0_line_62 |  | 56 | 66 | 0.025325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_114_0_line_63 |  | 57 | 67 | 0.042837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_114_0_line_64 |  | 58 | 59 | 0.25372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_114_0_line_65 |  | 58 | 60 | 0.065364 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_114_0_line_66 |  | 58 | 61 | 0.16406 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_114_0_line_67 |  | 59 | 62 | 0.03042 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_114_0_line_68 |  | 60 | 68 | 0.003685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_114_0_line_69 |  | 61 | 70 | 0.06288 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_114_0_line_70 |  | 64 | 74 | 0.056094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_114_0_line_71 |  | 68 | 69 | 0.11161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_114_0_line_72 |  | 69 | 71 | 0.030671 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_114_0_line_73 |  | 70 | 72 | 0.039402 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_114_0_trafo_38 | 25 MVA 110/20 kV | 75 | 44 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2607301.8851 | 1122552.9747
1 | 2607204.6579 | 1122698.3748
2 | 2607144.8418 | 1122764.5147
3 | 2607131.8864 | 1122870.7626
4 | 2607106.811 | 1122863.5187
5 | 2607164.7646 | 1122858.873
6 | 2608610.193 | 1124522.932
7 | 2607844.1654 | 1123182.9108
8 | 2611559.4162 | 1122338.98
9 | 2608621.5338 | 1124603.9654
10 | 2607128.9226 | 1122681.6556
11 | 2607173.5903 | 1122848.6561
12 | 2607217.2288 | 1122834.0004
13 | 2607103.1162 | 1123043.5468
14 | 2607055.0267 | 1122841.1477
15 | 2607456.6858 | 1123144.4509
16 | 2607297.6419 | 1123128.6733
17 | 2607128.2452 | 1123149.6168
18 | 2606369.6981 | 1123407.2274
19 | 2607033.2748 | 1122820.3125
20 | 2607008.3063 | 1122793.4929
21 | 2606952.4479 | 1122643.8671
22 | 2606697.1931 | 1122436.3251
23 | 2606830.9113 | 1122670.7432
24 | 2606648.7893 | 1122392.4175
25 | 2606809.6207 | 1122393.873
26 | 2606874.2288 | 1122407.1963
27 | 2607310.1201 | 1125199.4106
28 | 2607313.3475 | 1125201.3265
29 | 2612259.4124 | 1122141.1556
30 | 2612333.3494 | 1122230.4795
31 | 2612263.1089 | 1122296.1031
32 | 2612517.5639 | 1122180.7647
33 | 2611967.274 | 1122349.5402
34 | 2612199.5238 | 1122323.9333
35 | 2611837.9607 | 1122280.2533
36 | 2612209.7771 | 1122321.6972
37 | 2611692.8694 | 1122337.6343
38 | 2611681.5403 | 1122390.1494
39 | 2611763.5815 | 1122491.2681
40 | 2611758.3627 | 1122382.5825
41 | 2611686.7309 | 1122229.2583
42 | 2611821.0187 | 1122458.4633
43 | 2611602.0141 | 1122214.3778
44 | 2608622.6048 | 1124615.1947
45 | 2608077.6771 | 1125315.535
46 | 2608058.0345 | 1125306.1489
47 | 2608090.6407 | 1125327.936
48 | 2607898.3825 | 1125537.1751
49 | 2607903.7139 | 1125538.8495
50 | 2608117.0399 | 1125478.6446
51 | 2607790.9587 | 1125768.85
52 | 2608056.9043 | 1125309.8158
53 | 2608272.4082 | 1125462.9939
54 | 2608245.6131 | 1125597.0082
55 | 2607876.9632 | 1125918.9559
56 | 2607760.6745 | 1125760.5978
57 | 2607923.1955 | 1125880.5509
58 | 2607710.4357 | 1125437.4527
59 | 2607867.3355 | 1125334.6694
60 | 2607672.5854 | 1125490.7421
61 | 2607562.6902 | 1125366.133
62 | 2607897.002 | 1125341.3999
63 | 2608310.7151 | 1125498.6574
64 | 2608202.3129 | 1125642.4387
65 | 2608274.18 | 1125624.9725
66 | 2607736.2405 | 1125753.9398
67 | 2607937.7821 | 1125840.2741
68 | 2607671.6637 | 1125494.3093
69 | 2607616.2877 | 1125559.5051
70 | 2607504.838 | 1125341.8185
71 | 2607586.6946 | 1125551.4437
72 | 2607468.271 | 1125327.1421
73 | 2608115.3097 | 1125348.2453
74 | 2608154.7439 | 1125613.3155
75 | 2608622.6048 | 1124615.1947

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98289 | -0.093727 | 0.28312 | 0.13712
1 | 0.98295 | -0.094336 | 0 | 0
2 | 0.983 | -0.094726 | 0 | 0
3 | 0.98308 | -0.093746 | 0.30638 | 0.14839
4 | 0.9831 | -0.093963 | 0 | 0
5 | 0.98306 | -0.093915 | 0 | 0
6 | 0.99976 | -0.0025234 | 0 | 0
7 | 0.98878 | -0.077016 | 0.12739 | 0.061698
8 | 0.99174 | -0.061755 | 0 | 0
9 | 0.99998 | -7.6756e-05 | 0.14878 | 0.072059
10 | 0.98297 | -0.094481 | 0.22749 | 0.11018
11 | 0.98305 | -0.093853 | 0 | 0
12 | 0.98303 | -0.093641 | 0.37642 | 0.18231
13 | 0.98384 | -0.1005 | 0 | 0
14 | 0.98298 | -0.092852 | 0 | 0
15 | 0.9861 | -0.095415 | 0.39186 | 0.18979
16 | 0.98543 | -0.089412 | 0 | 0
17 | 0.98439 | -0.096612 | 0.40048 | 0.19396
18 | 0.98421 | -0.097821 | 0.11771 | 0.05701
19 | 0.98292 | -0.092364 | 0.33521 | 0.16235
20 | 0.98287 | -0.091919 | 0 | 0
21 | 0.98264 | -0.08984 | 0 | 0
22 | 0.98233 | -0.087046 | 0 | 0
23 | 0.98254 | -0.090451 | 0.39123 | 0.18948
24 | 0.9823 | -0.086765 | 0.32237 | 0.15613
25 | 0.98227 | -0.086529 | 0 | 0
26 | 0.98223 | -0.086823 | 0.35602 | 0.17243
27 | 0.99209 | -0.34905 | 0.4095 | 0.19833
28 | 0.99209 | -0.34907 | 0 | 0
29 | 0.99083 | -0.061924 | 0.1501 | 0.072697
30 | 0.99087 | -0.061709 | 0 | 0
31 | 0.9909 | -0.062024 | 0 | 0
32 | 0.99082 | -0.061992 | 0.11971 | 0.057977
33 | 0.99112 | -0.060923 | 0.14922 | 0.07227
34 | 0.99093 | -0.062261 | 0 | 0
35 | 0.99129 | -0.059811 | 0 | 0
36 | 0.99092 | -0.062208 | 0.16417 | 0.07951
37 | 0.99143 | -0.060926 | 0.14691 | 0.071149
38 | 0.99154 | -0.060077 | 0 | 0
39 | 0.99138 | -0.061258 | 0 | 0
40 | 0.9914 | -0.061084 | 0.16185 | 0.078387
41 | 0.99124 | -0.059538 | 0 | 0
42 | 0.99136 | -0.061142 | 0.14821 | 0.071784
43 | 0.99123 | -0.059447 | 0.091681 | 0.044403
44 | 1 | 0 | -15.6411 | -7.4735
45 | 0.99358 | -0.35778 | 0 | 0
46 | 0.9935 | -0.35808 | 0.37382 | 0.18105
47 | 0.99357 | -0.3577 | 0 | 0
48 | 0.99243 | -0.36236 | 0.28566 | 0.13835
49 | 0.99243 | -0.36238 | 0 | 0
50 | 0.99146 | -0.36604 | 0 | 0
51 | 0.99218 | -0.36036 | 0 | 0
52 | 0.99349 | -0.35813 | 0 | 0
53 | 0.9911 | -0.36263 | 0.20239 | 0.098022
54 | 0.9909 | -0.37189 | 0 | 0
55 | 0.99184 | -0.35745 | 0 | 0
56 | 0.99217 | -0.36028 | 0.1265 | 0.061266
57 | 0.99179 | -0.35701 | 0.28013 | 0.13567
58 | 0.99252 | -0.34954 | 0 | 0
59 | 0.99296 | -0.35341 | 0 | 0
60 | 0.99244 | -0.3501 | 0.40597 | 0.19662
61 | 0.99231 | -0.35102 | 0 | 0
62 | 0.99294 | -0.35355 | 0.36281 | 0.17571
63 | 0.99102 | -0.36194 | 1.0935 | 0.52961
64 | 0.99065 | -0.36954 | 0 | 0
65 | 0.99076 | -0.37054 | 2.777 | 1.3449
66 | 0.99217 | -0.36025 | 0.1034 | 0.050079
67 | 0.99178 | -0.35691 | 0.17981 | 0.087087
68 | 0.99244 | -0.35008 | 0 | 0
69 | 0.9924 | -0.34974 | 0 | 0
70 | 0.99226 | -0.35054 | 0.26101 | 0.12641
71 | 0.99239 | -0.34964 | 0.26359 | 0.12766
72 | 0.99223 | -0.35036 | 0 | 0
73 | 0.99355 | -0.35756 | 0.37455 | 0.1814
74 | 0.99043 | -0.36744 | 3.0828 | 1.4931
75 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.28312 | -0.13712 | 0.28314 | 0.13295 | 2.0496e-05 | -0.0041667 | 0.0092391 | 0.0091863 | 0.0092391 | 0.98289 | -0.093727 | 0.98295 | -0.094336 | 4.1996
1 | -0.28314 | -0.13295 | 0.28315 | 0.13009 | 1.3935e-05 | -0.0028606 | 0.0091863 | 0.0091509 | 0.0091863 | 0.98295 | -0.094336 | 0.983 | -0.094726 | 4.1756
2 | 0.2275 | 0.10812 | -0.22749 | -0.11018 | 6.5405e-06 | -0.0020565 | 0.0073971 | 0.0074232 | 0.0074232 | 0.983 | -0.094726 | 0.98297 | -0.094481 | 3.3742
3 | -0.51065 | -0.23822 | 0.5107 | 0.23813 | 5.1738e-05 | -8.995e-05 | 0.016548 | 0.016546 | 0.016548 | 0.983 | -0.094726 | 0.9831 | -0.093963 | 7.8798
4 | -0.68283 | -0.3293 | 0.68284 | 0.3287 | 1.7214e-05 | -0.00059555 | 0.022261 | 0.022253 | 0.022261 | 0.98308 | -0.093746 | 0.9831 | -0.093963 | 10.1184
5 | 0.37644 | 0.18091 | -0.37643 | -0.18094 | 9.3696e-06 | -3.4468e-05 | 0.012264 | 0.012265 | 0.012265 | 0.98308 | -0.093746 | 0.98306 | -0.093915 | 5.8403
6 | -2.5993 | -1.2276 | 2.6014 | 1.2232 | 0.0020768 | -0.0044299 | 0.084409 | 0.084346 | 0.084409 | 0.9831 | -0.093963 | 0.98384 | -0.1005 | 38.3678
7 | 1.4058 | 0.66081 | -1.4056 | -0.66234 | 0.00019131 | -0.0015319 | 0.045611 | 0.045631 | 0.045631 | 0.9831 | -0.093963 | 0.98298 | -0.092852 | 20.7414
8 | 0.37643 | 0.18094 | -0.37643 | -0.18125 | 2.709e-06 | -0.00031037 | 0.012265 | 0.012269 | 0.012269 | 0.98306 | -0.093915 | 0.98305 | -0.093853 | 5.5766
9 | 3.6929 | 1.7514 | -3.6546 | -1.7292 | 0.03831 | 0.022174 | 0.11802 | 0.11804 | 0.11804 | 0.99976 | -0.0025234 | 0.98878 | -0.077016 | 56.2087
10 | 1.1411 | 0.52447 | -1.1325 | -0.52342 | 0.0086109 | 0.0010497 | 0.036263 | 0.036316 | 0.036316 | 0.99976 | -0.0025234 | 0.99174 | -0.061755 | 17.2934
11 | -4.8341 | -2.2759 | 4.8351 | 2.2736 | 0.00098424 | -0.0022218 | 0.15428 | 0.15424 | 0.15428 | 0.99976 | -0.0025234 | 0.99998 | -7.6756e-05 | 42.6179
12 | 3.5272 | 1.6675 | -3.5182 | -1.6623 | 0.0090017 | 0.0051852 | 0.11391 | 0.11391 | 0.11391 | 0.98878 | -0.077016 | 0.9861 | -0.095415 | 54.2436
13 | 1.1325 | 0.52342 | -1.1323 | -0.52656 | 0.00024128 | -0.0031424 | 0.036316 | 0.036355 | 0.036355 | 0.99174 | -0.061755 | 0.99154 | -0.060077 | 16.5252
14 | -4.9838 | -2.3457 | 4.9839 | 2.345 | 8.815e-05 | -0.00065928 | 0.15901 | 0.159 | 0.15901 | 0.99998 | -7.6756e-05 | 1 | 0 | 24.9236
15 | 0.37643 | 0.18125 | -0.37642 | -0.18231 | 9.2364e-06 | -0.0010567 | 0.012269 | 0.012282 | 0.012282 | 0.98305 | -0.093853 | 0.98303 | -0.093641 | 5.5828
16 | -2.6014 | -1.2232 | 2.6028 | 1.2239 | 0.0013817 | 0.00073941 | 0.084346 | 0.084345 | 0.084346 | 0.98384 | -0.1005 | 0.98439 | -0.096612 | 40.1648
17 | 1.4056 | 0.66234 | -1.4055 | -0.66301 | 8.3625e-05 | -0.00066906 | 0.045631 | 0.04564 | 0.04564 | 0.98298 | -0.092852 | 0.98292 | -0.092364 | 20.7453
18 | 3.1264 | 1.4726 | -3.1241 | -1.4758 | 0.0022864 | -0.0032025 | 0.10117 | 0.10121 | 0.10121 | 0.9861 | -0.095415 | 0.98543 | -0.089412 | 46.0067
19 | 3.1241 | 1.4758 | -3.121 | -1.474 | 0.0031155 | 0.0017538 | 0.10121 | 0.10122 | 0.10122 | 0.98543 | -0.089412 | 0.98439 | -0.096612 | 48.1987
20 | 0.11773 | 0.056097 | -0.11771 | -0.05701 | 2.094e-05 | -0.00091344 | 0.0038244 | 0.0038362 | 0.0038362 | 0.98439 | -0.096612 | 0.98421 | -0.097821 | 1.8267
21 | 1.0703 | 0.50066 | -1.0702 | -0.50149 | 5.9112e-05 | -0.00083037 | 0.034702 | 0.034712 | 0.034712 | 0.98292 | -0.092364 | 0.98287 | -0.091919 | 15.7783
22 | 1.0702 | 0.50149 | -1.0699 | -0.50532 | 0.0002728 | -0.0038243 | 0.034712 | 0.034761 | 0.034761 | 0.98287 | -0.091919 | 0.98264 | -0.08984 | 15.8005
23 | 0.67867 | 0.31596 | -0.67844 | -0.3241 | 0.00023115 | -0.0081437 | 0.021992 | 0.022095 | 0.022095 | 0.98264 | -0.08984 | 0.98233 | -0.087046 | 10.0433
24 | 0.39126 | 0.18936 | -0.39123 | -0.18948 | 3.6169e-05 | -0.00012081 | 0.01277 | 0.012772 | 0.012772 | 0.98264 | -0.08984 | 0.98254 | -0.090451 | 6.0817
25 | 0.32238 | 0.15449 | -0.32237 | -0.15613 | 1.0511e-05 | -0.0016372 | 0.010505 | 0.010526 | 0.010526 | 0.98233 | -0.087046 | 0.9823 | -0.086765 | 4.7847
26 | 0.35606 | 0.16961 | -0.35603 | -0.17236 | 2.156e-05 | -0.0027552 | 0.01159 | 0.011625 | 0.011625 | 0.98233 | -0.087046 | 0.98227 | -0.086529 | 5.2841
27 | 0.35603 | 0.17236 | -0.35602 | -0.17243 | 1.5885e-05 | -6.6032e-05 | 0.011625 | 0.011626 | 0.011626 | 0.98227 | -0.086529 | 0.98223 | -0.086823 | 5.5361
28 | -0.4095 | -0.19833 | 0.4095 | 0.19824 | 8.7624e-07 | -8.7748e-05 | 0.013239 | 0.013238 | 0.013239 | 0.99209 | -0.34905 | 0.99209 | -0.34907 | 6.0179
29 | -0.4095 | -0.19824 | 0.40956 | 0.19192 | 6.2709e-05 | -0.0063193 | 0.013238 | 0.013159 | 0.013238 | 0.99209 | -0.34907 | 0.99223 | -0.35036 | 6.0174
30 | -0.1501 | -0.072697 | 0.15011 | 0.072564 | 4.8761e-06 | -0.00013285 | 0.004859 | 0.0048573 | 0.004859 | 0.99083 | -0.061924 | 0.99087 | -0.061709 | 2.3138
31 | -0.26982 | -0.13032 | 0.26983 | 0.128 | 1.0033e-05 | -0.0023167 | 0.0087296 | 0.0087005 | 0.0087296 | 0.99087 | -0.061709 | 0.9909 | -0.062024 | 3.968
32 | 0.11971 | 0.057756 | -0.11971 | -0.057977 | 5.1013e-06 | -0.00022044 | 0.0038723 | 0.0038752 | 0.0038752 | 0.99087 | -0.061709 | 0.99082 | -0.061992 | 1.8453
33 | -0.26983 | -0.128 | 0.26983 | 0.1266 | 6.0526e-06 | -0.0014052 | 0.0087005 | 0.008683 | 0.0087005 | 0.9909 | -0.062024 | 0.99092 | -0.062208 | 3.9548
34 | 0.43409 | 0.20564 | -0.434 | -0.20586 | 8.1502e-05 | -0.00022291 | 0.01399 | 0.013994 | 0.013994 | 0.99112 | -0.060923 | 0.99093 | -0.062261 | 6.6636
35 | -0.5833 | -0.27791 | 0.5834 | 0.2778 | 9.2561e-05 | -0.00011409 | 0.018819 | 0.018817 | 0.018819 | 0.99112 | -0.060923 | 0.99129 | -0.059811 | 8.9615
36 | 0.434 | 0.20586 | -0.434 | -0.20611 | 2.7364e-06 | -0.00024454 | 0.013994 | 0.013997 | 0.013997 | 0.99093 | -0.062261 | 0.99092 | -0.062208 | 6.3621
37 | 0.091687 | 0.032956 | -0.091682 | -0.042381 | 4.4695e-06 | -0.0094253 | 0.0028373 | 0.0029415 | 0.0029415 | 0.99129 | -0.059811 | 0.99124 | -0.059538 | 1.337
38 | -0.67508 | -0.31075 | 0.67518 | 0.30707 | 9.8763e-05 | -0.0036848 | 0.021642 | 0.021597 | 0.021642 | 0.99129 | -0.059811 | 0.99143 | -0.060926 | 9.8373
39 | -1.1322 | -0.52655 | 1.1323 | 0.52656 | 0.00012652 | 1.6198e-05 | 0.036356 | 0.036355 | 0.036356 | 0.99143 | -0.060926 | 0.99154 | -0.060077 | 17.3125
40 | 0.14822 | 0.070033 | -0.14822 | -0.070228 | 6.8693e-06 | -0.00019414 | 0.0047733 | 0.0047758 | 0.0047758 | 0.99143 | -0.060926 | 0.99138 | -0.061258 | 2.2742
41 | 0.16185 | 0.078297 | -0.16185 | -0.078387 | 3.8797e-06 | -9.0777e-05 | 0.0052352 | 0.0052364 | 0.0052364 | 0.99143 | -0.060926 | 0.9914 | -0.061084 | 2.4935
42 | 0.14822 | 0.070228 | -0.14821 | -0.071784 | 2.028e-06 | -0.0015559 | 0.0047758 | 0.0047954 | 0.0047954 | 0.99138 | -0.061258 | 0.99136 | -0.061142 | 2.1797
43 | 0.091682 | 0.042381 | -0.091681 | -0.044403 | 1.0043e-06 | -0.0020223 | 0.0029415 | 0.0029667 | 0.0029667 | 0.99124 | -0.059538 | 0.99123 | -0.059447 | 1.3485
44 | 10.6432 | 5.1179 | -10.6064 | -5.0201 | 0.036821 | 0.097795 | 0.34092 | 0.34093 | 0.34093 | 1 | 0 | 0.99358 | -0.35778 | 52.858
45 | 10.2318 | 4.8399 | -10.2311 | -4.8408 | 0.00072981 | -0.00094349 | 0.32886 | 0.32887 | 0.32887 | 0.99358 | -0.35778 | 0.9935 | -0.35808 | 51.5477
46 | 0.37456 | 0.18022 | -0.37455 | -0.18065 | 3.4962e-06 | -0.00042201 | 0.012077 | 0.012082 | 0.012082 | 0.99358 | -0.35778 | 0.99357 | -0.3577 | 5.4918
47 | 9.8573 | 4.6598 | -9.8572 | -4.66 | 0.000119 | -0.00017095 | 0.31681 | 0.31681 | 0.31681 | 0.9935 | -0.35808 | 0.99349 | -0.35813 | 49.6566
48 | 0.37455 | 0.18065 | -0.37455 | -0.1814 | 6.267e-06 | -0.0007555 | 0.012082 | 0.012092 | 0.012092 | 0.99357 | -0.3577 | 0.99355 | -0.35756 | 5.4962
49 | -0.28566 | -0.13835 | 0.28566 | 0.13822 | 6.3406e-07 | -0.00013087 | 0.0092324 | 0.0092308 | 0.0092324 | 0.99243 | -0.36236 | 0.99243 | -0.36238 | 4.1966
50 | 7.1681 | 3.431 | -7.1613 | -3.4526 | 0.0068055 | -0.021615 | 0.23116 | 0.23148 | 0.23148 | 0.99243 | -0.36238 | 0.99146 | -0.36604 | 36.2816
51 | 0.69023 | 0.30938 | -0.69004 | -0.3161 | 0.00018699 | -0.0067223 | 0.022002 | 0.022083 | 0.022083 | 0.99243 | -0.36238 | 0.99218 | -0.36036 | 10.0377
52 | -8.144 | -3.8786 | 8.1523 | 3.8589 | 0.0083823 | -0.019719 | 0.26238 | 0.26208 | 0.26238 | 0.99243 | -0.36238 | 0.99349 | -0.35813 | 41.1257
53 | 1.2965 | 0.62143 | -1.296 | -0.62643 | 0.00051386 | -0.0049931 | 0.041861 | 0.041926 | 0.041926 | 0.99146 | -0.36604 | 0.9911 | -0.36263 | 19.0573
54 | 5.8648 | 2.8312 | -5.8617 | -2.8349 | 0.0030328 | -0.0036798 | 0.18962 | 0.18969 | 0.18969 | 0.99146 | -0.36604 | 0.9909 | -0.37189 | 52.4006
55 | 0.46014 | 0.20609 | -0.45997 | -0.21987 | 0.00017107 | -0.013783 | 0.014669 | 0.014838 | 0.014838 | 0.99218 | -0.36036 | 0.99184 | -0.35745 | 6.7447
56 | 0.2299 | 0.11001 | -0.2299 | -0.11075 | 2.3071e-06 | -0.00073707 | 0.0074154 | 0.0074247 | 0.0074247 | 0.99218 | -0.36036 | 0.99217 | -0.36028 | 3.3748
57 | 1.7048 | 0.80107 | -1.7038 | -0.80655 | 0.00098076 | -0.0054779 | 0.054732 | 0.054804 | 0.054804 | 0.99349 | -0.35813 | 0.99296 | -0.35341 | 24.9108
58 | 1.0936 | 0.5284 | -1.0935 | -0.52961 | 8.7481e-05 | -0.0012014 | 0.035376 | 0.035392 | 0.035392 | 0.9911 | -0.36263 | 0.99102 | -0.36194 | 16.0871
59 | 3.0844 | 1.4907 | -3.0835 | -1.492 | 0.00083361 | -0.0012218 | 0.0998 | 0.099819 | 0.099819 | 0.9909 | -0.37189 | 0.99065 | -0.36954 | 45.3723
60 | 2.7774 | 1.3441 | -2.777 | -1.3449 | 0.00043128 | -0.00080911 | 0.08989 | 0.089902 | 0.089902 | 0.9909 | -0.37189 | 0.99076 | -0.37054 | 40.8644
61 | 0.45997 | 0.21987 | -0.45994 | -0.22175 | 2.3672e-05 | -0.0018814 | 0.014838 | 0.014862 | 0.014862 | 0.99184 | -0.35745 | 0.99179 | -0.35701 | 6.7555
62 | 0.1034 | 0.049484 | -0.1034 | -0.050079 | 3.7692e-07 | -0.00059512 | 0.0033352 | 0.0033427 | 0.0033427 | 0.99217 | -0.36028 | 0.99217 | -0.36025 | 1.5194
63 | 0.17981 | 0.086081 | -0.17981 | -0.087087 | 1.9297e-06 | -0.0010055 | 0.0058026 | 0.0058153 | 0.0058153 | 0.99179 | -0.35701 | 0.99178 | -0.35691 | 2.6433
64 | -1.3404 | -0.63665 | 1.341 | 0.63087 | 0.00062984 | -0.0057833 | 0.043159 | 0.043085 | 0.043159 | 0.99252 | -0.34954 | 0.99296 | -0.35341 | 19.6178
65 | 0.66963 | 0.32081 | -0.66957 | -0.32085 | 5.4317e-05 | -4.284e-05 | 0.021596 | 0.021597 | 0.021597 | 0.99252 | -0.34954 | 0.99244 | -0.3501 | 10.2842
66 | 0.67076 | 0.31584 | -0.67062 | -0.31595 | 0.00013593 | -0.00010775 | 0.021564 | 0.021566 | 0.021566 | 0.99252 | -0.34954 | 0.99231 | -0.35102 | 10.2695
67 | 0.36281 | 0.17568 | -0.36281 | -0.17571 | 7.4443e-06 | -3.1143e-05 | 0.011719 | 0.01172 | 0.01172 | 0.99296 | -0.35341 | 0.99294 | -0.35355 | 5.5808
68 | 0.26361 | 0.12424 | -0.26361 | -0.12432 | 3.5349e-07 | -8.6553e-05 | 0.0084765 | 0.0084776 | 0.0084776 | 0.99244 | -0.3501 | 0.99244 | -0.35008 | 3.8534
69 | 0.67062 | 0.31595 | -0.67058 | -0.31741 | 3.9075e-05 | -0.0014667 | 0.021566 | 0.021584 | 0.021584 | 0.99231 | -0.35102 | 0.99226 | -0.35054 | 9.811
70 | 3.0835 | 1.492 | -3.0828 | -1.4931 | 0.00074627 | -0.0010927 | 0.099819 | 0.099836 | 0.099836 | 0.99065 | -0.36954 | 0.99043 | -0.36744 | 45.3799
71 | 0.26361 | 0.12432 | -0.26359 | -0.12694 | 1.075e-05 | -0.0026213 | 0.0084776 | 0.0085104 | 0.0085104 | 0.99244 | -0.35008 | 0.9924 | -0.34974 | 3.8684
72 | 0.26359 | 0.12694 | -0.26359 | -0.12766 | 2.9688e-06 | -0.00072034 | 0.0085104 | 0.0085196 | 0.0085196 | 0.9924 | -0.34974 | 0.99239 | -0.34964 | 3.8725
73 | 0.40957 | 0.191 | -0.40956 | -0.19192 | 9.1005e-06 | -0.00092354 | 0.013147 | 0.013159 | 0.013159 | 0.99226 | -0.35054 | 0.99223 | -0.35036 | 5.9813

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 15.6411 | 7.4735

## res_load
| p_mw | q_mvar
0 | 0.28312 | 0.13712
1 | 0.30638 | 0.14839
2 | 0.12739 | 0.061698
3 | 0.14878 | 0.072059
4 | 0.22749 | 0.11018
5 | 0.37642 | 0.18231
6 | 0.39186 | 0.18979
7 | 0.40048 | 0.19396
8 | 0.11771 | 0.05701
9 | 0.33521 | 0.16235
10 | 0.39123 | 0.18948
11 | 0.32237 | 0.15613
12 | 0.35602 | 0.17243
13 | 0.4095 | 0.19833
14 | 0.1501 | 0.072697
15 | 0.11971 | 0.057977
16 | 0.14922 | 0.07227
17 | 0.16417 | 0.07951
18 | 0.14691 | 0.071149
19 | 0.16185 | 0.078387
20 | 0.14821 | 0.071784
21 | 0.091681 | 0.044403
22 | 0.37382 | 0.18105
23 | 0.28566 | 0.13835
24 | 0.20239 | 0.098022
25 | 0.1265 | 0.061266
26 | 0.28013 | 0.13567
27 | 0.40597 | 0.19662
28 | 0.36281 | 0.17571
29 | 1.0935 | 0.52961
30 | 2.777 | 1.3449
31 | 0.1034 | 0.050079
32 | 0.17981 | 0.087087
33 | 0.26101 | 0.12641
34 | 0.26359 | 0.12766
35 | 0.37455 | 0.1814
36 | 3.0828 | 1.4931

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1