## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_117_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_117_0_node_56 | 20 | n |  | TRUE
2 | bus_MV_117_0_node_37 | 20 | n |  | TRUE
3 | bus_MV_117_0_node_39 | 20 | n |  | TRUE
4 | bus_MV_117_0_node_40 | 20 | n |  | TRUE
5 | bus_MV_117_0_node_1 | 20 | n |  | TRUE
6 | bus_MV_117_0_node_2 | 20 | n |  | TRUE
7 | bus_MV_117_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_117_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_117_0_node_4 | 20 | n |  | TRUE
10 | bus_MV_117_0_node_70 | 20 | n |  | TRUE
11 | bus_MV_117_0_node_32 | 20 | n |  | TRUE
12 | bus_MV_117_0_node_38 | 20 | n |  | TRUE
13 | bus_MV_117_0_node_52 | 20 | n |  | TRUE
14 | bus_MV_117_0_node_169 | 20 | n |  | TRUE
15 | bus_MV_117_0_node_50 | 20 | n |  | TRUE
16 | bus_MV_117_0_node_43 | 20 | n |  | TRUE
17 | bus_MV_117_0_node_28 | 20 | n |  | TRUE
18 | bus_MV_117_0_node_6 | 20 | n |  | TRUE
19 | bus_MV_117_0_node_48 | 20 | n |  | TRUE
20 | bus_MV_117_0_node_7 | 20 | n |  | TRUE
21 | bus_MV_117_0_node_8 | 20 | n |  | TRUE
22 | bus_MV_117_0_node_9 | 20 | n |  | TRUE
23 | bus_MV_117_0_node_10 | 20 | n |  | TRUE
24 | bus_MV_117_0_node_11 | 20 | n |  | TRUE
25 | bus_MV_117_0_node_12 | 20 | n |  | TRUE
26 | bus_MV_117_0_node_13 | 20 | n |  | TRUE
27 | bus_MV_117_0_node_14 | 20 | n |  | TRUE
28 | bus_MV_117_0_node_46 | 20 | n |  | TRUE
29 | bus_MV_117_0_node_22 | 20 | n |  | TRUE
30 | bus_MV_117_0_node_53 | 20 | n |  | TRUE
31 | bus_MV_117_0_node_30 | 20 | n |  | TRUE
32 | bus_MV_117_0_node_15 | 20 | n |  | TRUE
33 | bus_MV_117_0_node_17 | 20 | n |  | TRUE
34 | bus_MV_117_0_node_59 | 20 | n |  | TRUE
35 | bus_MV_117_0_node_45 | 20 | n |  | TRUE
36 | bus_MV_117_0_node_165 | 20 | n |  | TRUE
37 | bus_MV_117_0_node_19 | 20 | n |  | TRUE
38 | bus_MV_117_0_node_58 | 20 | n |  | TRUE
39 | bus_MV_117_0_node_35 | 20 | n |  | TRUE
40 | bus_MV_117_0_node_42 | 20 | n |  | TRUE
41 | bus_MV_117_0_node_57 | 20 | n |  | TRUE
42 | bus_MV_117_0_node_167 | 20 | n |  | TRUE
43 | bus_MV_117_0_node_36 | 20 | n |  | TRUE
44 | bus_MV_117_0_node_34 | 20 | n |  | TRUE
45 | bus_MV_117_0_node_18 | 20 | n |  | TRUE
46 | bus_MV_117_0_node_20 | 20 | n |  | TRUE
47 | bus_MV_117_0_node_21 | 20 | n |  | TRUE
48 | bus_MV_117_0_node_23 | 20 | n |  | TRUE
49 | bus_MV_117_0_node_25 | 20 | n |  | TRUE
50 | bus_MV_117_0_node_29 | 20 | n |  | TRUE
51 | bus_MV_117_0_node_27 | 20 | n |  | TRUE
52 | bus_MV_117_0_node_24 | 20 | n |  | TRUE
53 | bus_MV_117_0_node_26 | 20 | n |  | TRUE
54 | bus_MV_117_0_node_153 | 20 | n |  | TRUE
55 | bus_MV_117_0_node_31 | 20 | n |  | TRUE
56 | bus_MV_117_0_node_73 | 20 | n |  | TRUE
57 | bus_MV_117_0_node_55 | 20 | n |  | TRUE
58 | bus_MV_117_0_node_71 | 20 | n |  | TRUE
59 | bus_MV_117_0_node_72 | 20 | n |  | TRUE
60 | bus_MV_117_0_node_33 | 20 | n |  | TRUE
61 | bus_MV_117_0_node_54 | 20 | n |  | TRUE
62 | bus_MV_117_0_node_41 | 20 | n |  | TRUE
63 | bus_MV_117_0_node_166 | 20 | n |  | TRUE
64 | bus_MV_117_0_node_44 | 20 | n |  | TRUE
65 | bus_MV_117_0_node_47 | 20 | n |  | TRUE
66 | bus_MV_117_0_node_49 | 20 | n |  | TRUE
67 | bus_MV_117_0_node_51 | 20 | n |  | TRUE
68 | bus_MV_117_0_node_164 | 20 | n |  | TRUE
69 | bus_MV_117_0_node_64 | 20 | n |  | TRUE
70 | bus_MV_117_0_node_60 | 20 | n |  | TRUE
71 | bus_MV_117_0_node_62 | 20 | n |  | TRUE
72 | bus_MV_117_0_node_61 | 20 | n |  | TRUE
73 | bus_MV_117_0_node_65 | 20 | n |  | TRUE
74 | bus_MV_117_0_node_66 | 20 | n |  | TRUE
75 | bus_MV_117_0_node_67 | 20 | n |  | TRUE
76 | bus_MV_117_0_node_149 | 20 | n |  | TRUE
77 | bus_MV_117_0_node_68 | 20 | n |  | TRUE
78 | bus_MV_117_0_node_69 | 20 | n |  | TRUE
79 | bus_MV_117_0_node_170 | 20 | n |  | TRUE
80 | bus_MV_117_0_node_148 | 20 | n |  | TRUE
81 | bus_MV_117_0_node_74 | 20 | n |  | TRUE
82 | bus_MV_117_0_node_75 | 20 | n |  | TRUE
83 | bus_MV_117_0_node_76 | 20 | n |  | TRUE
84 | bus_MV_117_0_node_77 | 20 | n |  | TRUE
85 | bus_MV_117_0_node_133 | 20 | n |  | TRUE
86 | bus_MV_117_0_node_134 | 20 | n |  | TRUE
87 | bus_MV_117_0_node_132 | 20 | n |  | TRUE
88 | bus_MV_117_0_node_79 | 20 | n |  | TRUE
89 | bus_MV_117_0_node_146 | 20 | n |  | TRUE
90 | bus_MV_117_0_node_80 | 20 | n |  | TRUE
91 | bus_MV_117_0_node_82 | 20 | n |  | TRUE
92 | bus_MV_117_0_node_81 | 20 | n |  | TRUE
93 | bus_MV_117_0_node_86 | 20 | n |  | TRUE
94 | bus_MV_117_0_node_84 | 20 | n |  | TRUE
95 | bus_MV_117_0_node_83 | 20 | n |  | TRUE
96 | bus_MV_117_0_node_115 | 20 | n |  | TRUE
97 | bus_MV_117_0_node_126 | 20 | n |  | TRUE
98 | bus_MV_117_0_node_85 | 20 | n |  | TRUE
99 | bus_MV_117_0_node_136 | 20 | n |  | TRUE
100 | bus_MV_117_0_node_168 | 20 | n |  | TRUE
101 | bus_MV_117_0_node_116 | 20 | n |  | TRUE
102 | bus_MV_117_0_node_128 | 20 | n |  | TRUE
103 | bus_MV_117_0_node_125 | 20 | n |  | TRUE
104 | bus_MV_117_0_node_87 | 20 | n |  | TRUE
105 | bus_MV_117_0_node_88 | 20 | n |  | TRUE
106 | bus_MV_117_0_node_141 | 20 | n |  | TRUE
107 | bus_MV_117_0_node_93 | 20 | n |  | TRUE
108 | bus_MV_117_0_node_103 | 20 | n |  | TRUE
109 | bus_MV_117_0_node_92 | 20 | n |  | TRUE
110 | bus_MV_117_0_node_137 | 20 | n |  | TRUE
111 | bus_MV_117_0_node_138 | 20 | n |  | TRUE
112 | bus_MV_117_0_node_139 | 20 | n |  | TRUE
113 | bus_MV_117_0_node_140 | 20 | n |  | TRUE
114 | bus_MV_117_0_node_161 | 20 | n |  | TRUE
115 | bus_MV_117_0_node_142 | 20 | n |  | TRUE
116 | bus_MV_117_0_node_143 | 20 | n |  | TRUE
117 | bus_MV_117_0_node_117 | 20 | n |  | TRUE
118 | bus_MV_117_0_node_145 | 20 | n |  | TRUE
119 | bus_MV_117_0_node_95 | 20 | n |  | TRUE
120 | bus_MV_117_0_node_96 | 20 | n |  | TRUE
121 | bus_MV_117_0_node_89 | 20 | n |  | TRUE
122 | bus_MV_117_0_node_90 | 20 | n |  | TRUE
123 | bus_MV_117_0_node_94 | 20 | n |  | TRUE
124 | bus_MV_117_0_node_127 | 20 | n |  | TRUE
125 | bus_MV_117_0_node_102 | 20 | n |  | TRUE
126 | bus_MV_117_0_node_109 | 20 | n |  | TRUE
127 | bus_MV_117_0_node_104 | 20 | n |  | TRUE
128 | bus_MV_117_0_node_101 | 20 | n |  | TRUE
129 | bus_MV_117_0_node_106 | 20 | n |  | TRUE
130 | bus_MV_117_0_node_105 | 20 | n |  | TRUE
131 | bus_MV_117_0_node_171 | 20 | n |  | TRUE
132 | bus_MV_117_0_node_100 | 20 | n |  | TRUE
133 | bus_MV_117_0_node_98 | 20 | n |  | TRUE
134 | bus_MV_117_0_node_107 | 20 | n |  | TRUE
135 | bus_MV_117_0_node_158 | 20 | n |  | TRUE
136 | bus_MV_117_0_node_159 | 20 | n |  | TRUE
137 | bus_MV_117_0_node_157 | 20 | n |  | TRUE
138 | bus_MV_117_0_node_99 | 20 | n |  | TRUE
139 | bus_MV_117_0_node_108 | 20 | n |  | TRUE
140 | bus_MV_117_0_node_110 | 20 | n |  | TRUE
141 | bus_MV_117_0_node_162 | 20 | n |  | TRUE
142 | bus_MV_117_0_node_135 | 20 | n |  | TRUE
143 | bus_MV_117_0_node_111 | 20 | n |  | TRUE
144 | bus_MV_117_0_node_112 | 20 | n |  | TRUE
145 | bus_MV_117_0_node_122 | 20 | n |  | TRUE
146 | bus_MV_117_0_node_113 | 20 | n |  | TRUE
147 | bus_MV_117_0_node_114 | 20 | n |  | TRUE
148 | bus_MV_117_0_node_119 | 20 | n |  | TRUE
149 | bus_MV_117_0_node_163 | 20 | n |  | TRUE
150 | bus_MV_117_0_node_123 | 20 | n |  | TRUE
151 | bus_MV_117_0_node_131 | 20 | n |  | TRUE
152 | bus_MV_117_0_node_130 | 20 | n |  | TRUE
153 | bus_MV_117_0_node_129 | 20 | n |  | TRUE
154 | bus_MV_117_0_node_144 | 20 | n |  | TRUE
155 | bus_MV_117_0_node_118 | 20 | n |  | TRUE
156 | bus_MV_117_0_node_120 | 20 | n |  | TRUE
157 | bus_MV_117_0_node_121 | 20 | n |  | TRUE
158 | bus_MV_117_0_node_124 | 20 | n |  | TRUE
159 | bus_MV_117_0_node_152 | 20 | n |  | TRUE
160 | bus_MV_117_0_node_151 | 20 | n |  | TRUE
161 | bus_MV_117_0_node_150 | 20 | n |  | TRUE
162 | bus_MV_117_0_node_156 | 20 | n |  | TRUE
163 | bus_MV_117_0_node_160 | 20 | n |  | TRUE
164 | bus_MV_117_0_node_155 | 20 | n |  | TRUE
165 | bus_MV_117_0_node_147 | 20 | n |  | TRUE
166 | bus_MV_117_0_node_154 | 20 | n |  | TRUE
167 | bus_HV_117_0_node_134 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_117_0_load_0 | 0 | 0.05518 | 0.026725 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_117_0_load_37 | 2 | 0.12396 | 0.060035 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_117_0_load_39 | 3 | 0.10974 | 0.053152 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_117_0_load_1 | 5 | 0.15232 | 0.073771 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_117_0_load_4 | 9 | 0.091727 | 0.044426 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_117_0_load_70 | 10 | 0.1217 | 0.05894 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_117_0_load_32 | 11 | 0.080402 | 0.03894 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_117_0_load_38 | 12 | 0.15874 | 0.076883 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_117_0_load_169 | 14 | 0.096146 | 0.046566 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_117_0_load_50 | 15 | 0.14897 | 0.072147 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_117_0_load_43 | 16 | 0.1631 | 0.078994 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_117_0_load_6 | 18 | 0.19411 | 0.094013 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_117_0_load_7 | 20 | 0.14595 | 0.070686 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_117_0_load_13 | 26 | 0.15118 | 0.073221 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_117_0_load_53 | 30 | 0.099027 | 0.047961 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_117_0_load_30 | 31 | 0.15429 | 0.074724 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_117_0_load_15 | 32 | 0.11001 | 0.053281 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_117_0_load_17 | 33 | 0.13572 | 0.06573 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_117_0_load_59 | 34 | 0.13442 | 0.065104 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_117_0_load_165 | 36 | 0.13927 | 0.06745 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_117_0_load_42 | 40 | 0.12297 | 0.059557 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_117_0_load_167 | 42 | 0.1118 | 0.054148 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_117_0_load_34 | 44 | 0.12371 | 0.059917 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_117_0_load_18 | 45 | 0.15977 | 0.07738 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_117_0_load_20 | 46 | 0.15442 | 0.074789 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_117_0_load_21 | 47 | 0.10234 | 0.049563 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_117_0_load_23 | 48 | 0.16286 | 0.078876 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_117_0_load_24 | 52 | 0.16054 | 0.077752 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_117_0_load_153 | 54 | 0.10169 | 0.049253 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_117_0_load_31 | 55 | 0.15615 | 0.075628 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_117_0_load_73 | 56 | 0.15454 | 0.074848 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_117_0_load_33 | 60 | 0.099309 | 0.048097 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_117_0_load_54 | 61 | 0.096143 | 0.046564 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_117_0_load_166 | 63 | 0.076721 | 0.037158 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_117_0_load_44 | 64 | 0.12443 | 0.060267 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_117_0_load_47 | 65 | 0.13089 | 0.063393 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_117_0_load_164 | 68 | 0.14494 | 0.070196 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_117_0_load_60 | 70 | 0.12873 | 0.062345 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_117_0_load_62 | 71 | 0.10075 | 0.048796 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_117_0_load_61 | 72 | 0.096956 | 0.046958 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_117_0_load_65 | 73 | 0.11937 | 0.057813 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_117_0_load_69 | 78 | 0.095706 | 0.046352 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_117_0_load_170 | 79 | 0.14598 | 0.070702 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_117_0_load_148 | 80 | 0.14164 | 0.0686 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_117_0_load_74 | 81 | 0.16145 | 0.078195 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_117_0_load_77 | 84 | 0.12466 | 0.060376 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_117_0_load_132 | 87 | 0.05346 | 0.025892 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_117_0_load_79 | 88 | 0.081057 | 0.039258 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_117_0_load_146 | 89 | 0.063946 | 0.030971 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_117_0_load_80 | 90 | 0.080168 | 0.038827 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_117_0_load_115 | 96 | 0.15199 | 0.073611 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_117_0_load_136 | 99 | 0.15555 | 0.075335 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_117_0_load_168 | 100 | 0.14396 | 0.069722 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_117_0_load_125 | 103 | 0.14866 | 0.071999 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_117_0_load_87 | 104 | 0.15695 | 0.076014 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_117_0_load_141 | 106 | 0.092213 | 0.044661 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_117_0_load_92 | 109 | 0.13392 | 0.064861 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_117_0_load_137 | 110 | 0.097957 | 0.047443 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_117_0_load_161 | 114 | 0.099112 | 0.048002 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_117_0_load_143 | 116 | 0.10289 | 0.049834 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_117_0_load_145 | 118 | 0.055512 | 0.026886 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_117_0_load_95 | 119 | 0.076402 | 0.037003 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_117_0_load_89 | 121 | 0.1203 | 0.058265 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_117_0_load_127 | 124 | 0.55077 | 0.26675 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_117_0_load_109 | 126 | 0.091553 | 0.044341 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_117_0_load_104 | 127 | 0.14596 | 0.070691 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_117_0_load_106 | 129 | 0.10717 | 0.051903 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_117_0_load_105 | 130 | 0.051477 | 0.024931 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_117_0_load_171 | 131 | 0.14351 | 0.069503 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_117_0_load_98 | 133 | 0.05917 | 0.028657 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_117_0_load_107 | 134 | 0.1572 | 0.076138 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_117_0_load_159 | 136 | 0.21096 | 0.10217 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_117_0_load_157 | 137 | 0.15201 | 0.073621 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_117_0_load_162 | 141 | 0.124 | 0.060058 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_117_0_load_135 | 142 | 0.15604 | 0.075575 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_117_0_load_111 | 143 | 0.12519 | 0.060635 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_117_0_load_119 | 148 | 0.12035 | 0.058289 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_117_0_load_163 | 149 | 0.10489 | 0.050801 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_117_0_load_129 | 153 | 0.1604 | 0.077686 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_117_0_load_144 | 154 | 0.14005 | 0.067827 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_117_0_load_118 | 155 | 0.095526 | 0.046265 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_117_0_load_120 | 156 | 0.10621 | 0.051439 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_117_0_load_152 | 159 | 0.10169 | 0.049251 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_117_0_load_150 | 161 | 0.11772 | 0.057016 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_117_0_load_160 | 163 | 0.072305 | 0.035019 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_117_0_load_147 | 165 | 0.1506 | 0.072939 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_117_0_load_154 | 166 | 0.27035 | 0.13094 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 86 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_117_0_line_0 |  | 0 | 1 | 4.791 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_117_0_line_1 |  | 1 | 2 | 0.045676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_117_0_line_2 |  | 2 | 12 | 0.14035 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_117_0_line_3 |  | 3 | 4 | 0.087036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_117_0_line_4 |  | 4 | 62 | 0.075658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_117_0_line_5 |  | 5 | 6 | 0.31584 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_117_0_line_6 |  | 6 | 7 | 0.61233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_117_0_line_7 |  | 6 | 8 | 0.67813 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_117_0_line_8 |  | 7 | 18 | 0.12602 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_117_0_line_9 |  | 8 | 9 | 0.03647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_117_0_line_10 |  | 9 | 10 | 1.2891 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_117_0_line_11 |  | 10 | 11 | 0.24949 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_117_0_line_12 |  | 10 | 12 | 0.24021 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_117_0_line_13 |  | 11 | 58 | 0.082827 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_117_0_line_14 |  | 12 | 60 | 0.10931 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_117_0_line_15 |  | 13 | 14 | 0.60017 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_117_0_line_16 |  | 13 | 15 | 0.098738 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
17 | MV_117_0_line_17 |  | 13 | 16 | 0.090222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_117_0_line_18 |  | 13 | 17 | 0.070769 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_117_0_line_19 |  | 14 | 59 | 0.13254 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_117_0_line_20 |  | 15 | 19 | 0.031974 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
21 | MV_117_0_line_21 |  | 16 | 40 | 0.1243 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_117_0_line_22 |  | 17 | 49 | 0.10509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_117_0_line_23 |  | 19 | 65 | 0.011486 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
24 | MV_117_0_line_24 |  | 20 | 21 | 0.013598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_117_0_line_25 |  | 20 | 22 | 0.02024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_117_0_line_26 |  | 21 | 23 | 0.066267 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_117_0_line_27 |  | 22 | 24 | 0.037008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_117_0_line_28 |  | 22 | 25 | 0.15985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_117_0_line_29 |  | 23 | 26 | 0.004491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_117_0_line_30 |  | 23 | 27 | 0.085637 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_117_0_line_31 |  | 24 | 28 | 0.066994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_117_0_line_32 |  | 24 | 29 | 0.085956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_117_0_line_33 |  | 24 | 30 | 0.035588 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_117_0_line_34 |  | 25 | 31 | 0.023155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_117_0_line_35 |  | 27 | 32 | 0.031731 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_117_0_line_36 |  | 27 | 33 | 0.14253 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_117_0_line_37 |  | 28 | 34 | 0.020299 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_117_0_line_38 |  | 28 | 35 | 0.075106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_117_0_line_39 |  | 29 | 36 | 0.034037 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_117_0_line_40 |  | 29 | 37 | 0.042204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_117_0_line_41 |  | 32 | 38 | 0.095836 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_117_0_line_42 |  | 33 | 39 | 0.15809 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_117_0_line_43 |  | 35 | 64 | 0.037367 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_117_0_line_44 |  | 36 | 50 | 0.005483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_117_0_line_45 |  | 37 | 45 | 0.013923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_117_0_line_46 |  | 38 | 41 | 0.11462 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_117_0_line_47 |  | 39 | 43 | 0.079521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_117_0_line_48 |  | 39 | 44 | 0.05155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_117_0_line_49 |  | 39 | 42 | 0.036138 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_117_0_line_50 |  | 40 | 62 | 0.042095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_117_0_line_51 |  | 41 | 63 | 0.048624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_117_0_line_52 |  | 43 | 57 | 0.01487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_117_0_line_53 |  | 45 | 46 | 0.071388 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_117_0_line_54 |  | 46 | 47 | 0.026179 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_117_0_line_55 |  | 47 | 48 | 0.041161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_117_0_line_56 |  | 48 | 49 | 0.087588 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_117_0_line_57 |  | 49 | 51 | 0.068346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_117_0_line_58 |  | 50 | 53 | 0.031883 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_117_0_line_59 |  | 51 | 54 | 0.026732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_117_0_line_60 |  | 52 | 53 | 0.007996 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_117_0_line_61 |  | 55 | 56 | 0.11874 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_117_0_line_62 |  | 56 | 57 | 0.061365 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_117_0_line_63 |  | 57 | 61 | 0.027927 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_117_0_line_64 |  | 58 | 59 | 0.11058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_117_0_line_65 |  | 65 | 66 | 0.020979 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
66 | MV_117_0_line_66 |  | 66 | 67 | 0.041172 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
67 | MV_117_0_line_67 |  | 67 | 68 | 0.03183 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
68 | MV_117_0_line_68 |  | 68 | 69 | 0.036639 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
69 | MV_117_0_line_69 |  | 69 | 72 | 0.058216 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
70 | MV_117_0_line_70 |  | 70 | 71 | 0.083335 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
71 | MV_117_0_line_71 |  | 70 | 72 | 0.084922 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
72 | MV_117_0_line_72 |  | 71 | 73 | 0.28916 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
73 | MV_117_0_line_73 |  | 73 | 74 | 0.12956 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
74 | MV_117_0_line_74 |  | 74 | 75 | 0.22079 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
75 | MV_117_0_line_75 |  | 75 | 76 | 0.16406 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
76 | MV_117_0_line_76 |  | 75 | 77 | 0.19684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_117_0_line_77 |  | 76 | 79 | 0.009252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_117_0_line_78 |  | 76 | 80 | 0.32233 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
79 | MV_117_0_line_79 |  | 77 | 78 | 0.01716 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_117_0_line_80 |  | 80 | 165 | 0.065663 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
81 | MV_117_0_line_81 |  | 81 | 82 | 0.11666 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_117_0_line_82 |  | 82 | 83 | 0.19367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_117_0_line_83 |  | 82 | 84 | 0.3686 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_117_0_line_84 |  | 83 | 88 | 0.091159 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_117_0_line_85 |  | 83 | 85 | 0.61111 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_117_0_line_86 |  | 85 | 86 | 0.27474 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
87 | MV_117_0_line_87 |  | 85 | 87 | 0.2686 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
88 | MV_117_0_line_88 |  | 86 | 89 | 0.24849 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
89 | MV_117_0_line_89 |  | 87 | 118 | 0.4296 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_117_0_line_90 |  | 87 | 93 | 0.13677 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
91 | MV_117_0_line_91 |  | 89 | 165 | 0.40544 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
92 | MV_117_0_line_92 |  | 90 | 91 | 0.075973 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
93 | MV_117_0_line_93 |  | 90 | 92 | 0.13306 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
94 | MV_117_0_line_94 |  | 91 | 93 | 0.30021 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
95 | MV_117_0_line_95 |  | 92 | 94 | 0.62252 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
96 | MV_117_0_line_96 |  | 94 | 97 | 0.14491 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
97 | MV_117_0_line_97 |  | 94 | 95 | 0.35908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_117_0_line_98 |  | 95 | 96 | 0.057489 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_117_0_line_99 |  | 96 | 101 | 0.074889 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_117_0_line_100 |  | 97 | 102 | 0.034875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_117_0_line_101 |  | 97 | 103 | 0.021267 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_117_0_line_102 |  | 98 | 99 | 0.033989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_117_0_line_103 |  | 98 | 100 | 0.14582 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
104 | MV_117_0_line_104 |  | 100 | 117 | 0.045723 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_117_0_line_105 |  | 101 | 117 | 0.076266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_117_0_line_106 |  | 102 | 162 | 0.056712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_117_0_line_107 |  | 102 | 163 | 0.0056214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_117_0_line_108 |  | 103 | 124 | 0.036022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_117_0_line_109 |  | 104 | 105 | 0.047495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_117_0_line_110 |  | 105 | 106 | 0.095632 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_117_0_line_111 |  | 106 | 115 | 0.007166 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_117_0_line_112 |  | 107 | 108 | 0.41125 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_117_0_line_113 |  | 107 | 109 | 0.20756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_117_0_line_114 |  | 108 | 129 | 0.040166 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
115 | MV_117_0_line_115 |  | 108 | 130 | 0.2661 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_117_0_line_116 |  | 108 | 120 | 0.38321 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_117_0_line_117 |  | 109 | 127 | 0.20298 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_117_0_line_118 |  | 110 | 111 | 0.057176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_117_0_line_119 |  | 110 | 112 | 0.21072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_117_0_line_120 |  | 111 | 113 | 0.80692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_117_0_line_121 |  | 112 | 119 | 1.401 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
122 | MV_117_0_line_122 |  | 113 | 114 | 0.12064 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_117_0_line_123 |  | 114 | 116 | 0.24662 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
124 | MV_117_0_line_124 |  | 115 | 116 | 0.07612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_117_0_line_125 |  | 117 | 151 | 0.12162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_117_0_line_126 |  | 119 | 120 | 0.007208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_117_0_line_127 |  | 121 | 122 | 0.042708 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_117_0_line_128 |  | 122 | 123 | 0.1402 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_117_0_line_129 |  | 123 | 125 | 0.074329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_117_0_line_130 |  | 123 | 126 | 0.053491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_117_0_line_131 |  | 125 | 131 | 0.005097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_117_0_line_132 |  | 125 | 132 | 0.07423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_117_0_line_133 |  | 126 | 134 | 0.018298 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_117_0_line_134 |  | 127 | 128 | 0.048586 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_117_0_line_135 |  | 128 | 138 | 0.11936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_117_0_line_136 |  | 132 | 133 | 0.007224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_117_0_line_137 |  | 133 | 138 | 0.12215 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
138 | MV_117_0_line_138 |  | 134 | 139 | 0.041367 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
139 | MV_117_0_line_139 |  | 135 | 136 | 0.020249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_117_0_line_140 |  | 135 | 137 | 0.062055 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_117_0_line_141 |  | 136 | 162 | 0.04465 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_117_0_line_142 |  | 137 | 159 | 0.016297 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
143 | MV_117_0_line_143 |  | 139 | 140 | 0.22574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_117_0_line_144 |  | 140 | 141 | 0.030638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_117_0_line_145 |  | 140 | 142 | 0.053084 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_117_0_line_146 |  | 140 | 143 | 0.074397 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
147 | MV_117_0_line_147 |  | 143 | 146 | 0.01123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_117_0_line_148 |  | 143 | 144 | 0.019214 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
149 | MV_117_0_line_149 |  | 144 | 145 | 0.071042 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
150 | MV_117_0_line_150 |  | 145 | 148 | 0.009797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_117_0_line_151 |  | 146 | 147 | 0.043753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_117_0_line_152 |  | 147 | 149 | 0.009634 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_117_0_line_153 |  | 149 | 150 | 0.026391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_117_0_line_154 |  | 150 | 158 | 0.035541 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_117_0_line_155 |  | 150 | 157 | 0.038126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_117_0_line_156 |  | 151 | 154 | 0.026357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_117_0_line_157 |  | 151 | 152 | 0.207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_117_0_line_158 |  | 152 | 153 | 0.015242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_117_0_line_159 |  | 155 | 156 | 0.07474 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
160 | MV_117_0_line_160 |  | 156 | 157 | 0.019169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_117_0_line_161 |  | 158 | 159 | 0.034514 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_117_0_line_162 |  | 158 | 160 | 0.04689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_117_0_line_163 |  | 160 | 161 | 0.027121 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
164 | MV_117_0_line_164 |  | 162 | 164 | 0.10357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_117_0_line_165 |  | 164 | 166 | 0.018222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_117_0_trafo_134 | 25 MVA 110/20 kV | 167 | 86 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2635877.8087 | 1114843.9512
1 | 2631486.8618 | 1116760.5263
2 | 2631465.031 | 1116792.0734
3 | 2630970.0401 | 1115669.973
4 | 2630972.6002 | 1115756.7631
5 | 2630526.4255 | 1118812.035
6 | 2630270.5636 | 1118640.1925
7 | 2630040.4119 | 1118282.9803
8 | 2630766.5463 | 1118177.7441
9 | 2630798.8982 | 1118160.733
10 | 2631107.6459 | 1116909.1564
11 | 2631006.1048 | 1116681.2664
12 | 2631343.0909 | 1116861.5662
13 | 2630844.1551 | 1115932.0306
14 | 2630725.2513 | 1116520.3014
15 | 2630758.776 | 1115915.9447
16 | 2630903.978 | 1115886.4786
17 | 2630802.3853 | 1115989.1583
18 | 2629935.924 | 1118212.5285
19 | 2630744.4923 | 1115887.3246
20 | 2630977.3658 | 1116173.5752
21 | 2630970.6638 | 1116161.735
22 | 2630961.8981 | 1116186.6806
23 | 2631010.5746 | 1116117.9834
24 | 2630935.5364 | 1116160.722
25 | 2630958.3776 | 1116300.1753
26 | 2631008.4255 | 1116114.0371
27 | 2631092.8276 | 1116094.1478
28 | 2630896.7324 | 1116208.6262
29 | 2630901.2417 | 1116103.852
30 | 2630902.1552 | 1116173.0581
31 | 2630936.4687 | 1116294.2718
32 | 2631089.7703 | 1116062.5718
33 | 2631215.8508 | 1116166.1267
34 | 2630880.2726 | 1116219.5257
35 | 2630836.3323 | 1116180.0379
36 | 2630876.5609 | 1116082.7379
37 | 2630926.7904 | 1116107.6507
38 | 2631062.2095 | 1115970.7844
39 | 2631100.7882 | 1116274.535
40 | 2630861.0379 | 1115769.8347
41 | 2631102.2489 | 1115882.7563
42 | 2631080.2288 | 1116244.8147
43 | 2631067.6608 | 1116342.8775
44 | 2631127.0928 | 1116318.9033
45 | 2630931.466 | 1116094.5346
46 | 2630979.137 | 1116041.3954
47 | 2630968.5286 | 1116017.4625
48 | 2630946.1387 | 1115984.5266
49 | 2630875.5386 | 1116036.3649
50 | 2630876.473 | 1116077.2569
51 | 2630848.9521 | 1116078.7066
52 | 2630881.1861 | 1116050.7009
53 | 2630887.2194 | 1116055.9676
54 | 2630831.7445 | 1116060.51
55 | 2630951.2468 | 1116476.7612
56 | 2631014.0801 | 1116376.009
57 | 2631072.2005 | 1116356.3187
58 | 2630943.9108 | 1116627.0772
59 | 2630843.5229 | 1116580.1203
60 | 2631326.4513 | 1116753.5259
61 | 2631100.0764 | 1116354.6384
62 | 2630899.0169 | 1115752.5415
63 | 2631134.1747 | 1115846.0348
64 | 2630807.7475 | 1116204.1049
65 | 2630741.6614 | 1115876.1936
66 | 2630735.0458 | 1115856.2834
67 | 2630721.2687 | 1115817.5163
68 | 2630702.0576 | 1115792.2286
69 | 2630679.1343 | 1115763.6316
70 | 2630622.8166 | 1115633.3483
71 | 2630540.6104 | 1115647.0187
72 | 2630648.7655 | 1115714.2089
73 | 2630258.3025 | 1115584.4511
74 | 2630195.9888 | 1115698.0424
75 | 2629996.574 | 1115638.5237
76 | 2629960.7157 | 1115497.2422
77 | 2629990.9005 | 1115750.7854
78 | 2629976.7276 | 1115741.1106
79 | 2629966.768 | 1115503.6197
80 | 2629654.1712 | 1115397.6201
81 | 2629793.3383 | 1114170.684
82 | 2629702.2097 | 1114242.8961
83 | 2629571.0844 | 1114329.0772
84 | 2629922.9516 | 1114538.0954
85 | 2629157.3765 | 1114778.8581
86 | 2629240.8465 | 1114938.9067
87 | 2628927.8518 | 1114698.6976
88 | 2629589.1186 | 1114239.7201
89 | 2629297.4679 | 1115111.333
90 | 2628681.5535 | 1114303.9974
91 | 2628716.7188 | 1114371.1307
92 | 2628601.2808 | 1114197.8765
93 | 2628851.7914 | 1114603.4878
94 | 2628327.1846 | 1113996.9017
95 | 2628453.7276 | 1114274.6996
96 | 2628396.6447 | 1114281.5247
97 | 2628213.0563 | 1114086.193
98 | 2628552.7605 | 1114511.7059
99 | 2628584.8091 | 1114522.9329
100 | 2628430.215 | 1114432.68
101 | 2628393.0516 | 1114356.2899
102 | 2628205.9907 | 1114116.0419
103 | 2628197.1675 | 1114072.0788
104 | 2627294.5845 | 1109296.2853
105 | 2627307.1849 | 1109342.0428
106 | 2627331.7471 | 1109434.4665
107 | 2627957.5382 | 1112926.1171
108 | 2627786.7506 | 1112559.5824
109 | 2627978.4471 | 1113132.117
110 | 2627323.4804 | 1110682.6919
111 | 2627338.4632 | 1110627.5982
112 | 2627227.8558 | 1110868.6674
113 | 2627272.0045 | 1109849.9744
114 | 2627327.8546 | 1109753.4099
115 | 2627334.9874 | 1109440.8621
116 | 2627366.9882 | 1109509.9187
117 | 2628384.4967 | 1114432.0102
118 | 2628781.9895 | 1115102.7741
119 | 2627592.4924 | 1112221.36
120 | 2627593.9126 | 1112228.4256
121 | 2627912.6594 | 1113405.5628
122 | 2627900.7008 | 1113446.5618
123 | 2627844.7078 | 1113517.2959
124 | 2628182.1193 | 1114039.384
125 | 2627803.2155 | 1113497.9183
126 | 2627862.8756 | 1113567.5988
127 | 2627779.5726 | 1113172.7467
128 | 2627768.1344 | 1113219.9626
129 | 2627825.9735 | 1112568.2329
130 | 2627520.9537 | 1112546.8659
131 | 2627799.6616 | 1113501.5817
132 | 2627800.7083 | 1113446.7256
133 | 2627797.6103 | 1113440.197
134 | 2627868.663 | 1113584.9509
135 | 2628142.0115 | 1114057.7157
136 | 2628134.3729 | 1114075.5945
137 | 2628093.066 | 1114019.5699
138 | 2627745.3115 | 1113329.8135
139 | 2627881.8359 | 1113624.1644
140 | 2628018.9769 | 1113797.1047
141 | 2627992.5985 | 1113801.6076
142 | 2628040.2269 | 1113748.4597
143 | 2628057.3034 | 1113860.8693
144 | 2628064.5985 | 1113843.0941
145 | 2628134.7641 | 1113831.9687
146 | 2628047.7999 | 1113866.8951
147 | 2628065.224 | 1113906.5844
148 | 2628141.0308 | 1113839.5126
149 | 2628067.7603 | 1113915.8786
150 | 2628076.8897 | 1113940.6443
151 | 2628346.6622 | 1114522.3233
152 | 2628429.2591 | 1114699.365
153 | 2628435.9203 | 1114713.0809
154 | 2628333.1289 | 1114544.8381
155 | 2628188.2905 | 1113939.8846
156 | 2628115.3654 | 1113923.5137
157 | 2628102.7263 | 1113937.9514
158 | 2628086.3153 | 1113974.7829
159 | 2628101.6383 | 1114005.7091
160 | 2628044.7599 | 1113996.6685
161 | 2628042.3493 | 1114023.682
162 | 2628157.2482 | 1114110.8908
163 | 2628211.1513 | 1114118.2707
164 | 2628186.7022 | 1114155.5388
165 | 2629634.783 | 1115336.2723
166 | 2628175.1448 | 1114141.4505
167 | 2629240.8465 | 1114938.9067

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98557 | -0.26522 | 0.05518 | 0.026725
1 | 0.98608 | -0.26076 | 0 | 0
2 | 0.98608 | -0.26078 | 0.12396 | 0.060035
3 | 0.98859 | -0.24416 | 0.10974 | 0.053152
4 | 0.9886 | -0.24427 | 0 | 0
5 | 0.98473 | -0.27228 | 0.15232 | 0.073771
6 | 0.98479 | -0.2728 | 0 | 0
7 | 0.98464 | -0.27162 | 0 | 0
8 | 0.98524 | -0.26856 | 0 | 0
9 | 0.98526 | -0.26866 | 0.091727 | 0.044426
10 | 0.98634 | -0.25893 | 0.1217 | 0.05894
11 | 0.98682 | -0.25514 | 0.080402 | 0.03894
12 | 0.98613 | -0.26038 | 0.15874 | 0.076883
13 | 0.98872 | -0.2444 | 0 | 0
14 | 0.98736 | -0.25507 | 0.096146 | 0.046566
15 | 0.98895 | -0.24177 | 0.14897 | 0.072147
16 | 0.98868 | -0.244 | 0.1631 | 0.078994
17 | 0.98834 | -0.24701 | 0 | 0
18 | 0.98459 | -0.27193 | 0.19411 | 0.094013
19 | 0.98903 | -0.24089 | 0 | 0
20 | 0.9865 | -0.24452 | 0.14595 | 0.070686
21 | 0.98648 | -0.24435 | 0 | 0
22 | 0.98654 | -0.24482 | 0 | 0
23 | 0.98639 | -0.24348 | 0 | 0
24 | 0.9866 | -0.24543 | 0 | 0
25 | 0.9865 | -0.24454 | 0 | 0
26 | 0.98639 | -0.24347 | 0.15118 | 0.073221
27 | 0.98623 | -0.24457 | 0 | 0
28 | 0.98658 | -0.24523 | 0 | 0
29 | 0.9868 | -0.24718 | 0 | 0
30 | 0.9866 | -0.24547 | 0.099027 | 0.047961
31 | 0.9865 | -0.2445 | 0.15429 | 0.074724
32 | 0.98622 | -0.24451 | 0.11001 | 0.053281
33 | 0.98601 | -0.246 | 0.13572 | 0.06573
34 | 0.98658 | -0.2452 | 0.13442 | 0.065104
35 | 0.98657 | -0.24512 | 0 | 0
36 | 0.98679 | -0.24706 | 0.13927 | 0.06745
37 | 0.98691 | -0.24819 | 0 | 0
38 | 0.98621 | -0.24463 | 0 | 0
39 | 0.98581 | -0.24731 | 0 | 0
40 | 0.98862 | -0.24441 | 0.12297 | 0.059557
41 | 0.98619 | -0.24454 | 0 | 0
42 | 0.9858 | -0.24736 | 0.1118 | 0.054148
43 | 0.98577 | -0.24692 | 0 | 0
44 | 0.9858 | -0.24723 | 0.12371 | 0.059917
45 | 0.98695 | -0.24852 | 0.15977 | 0.07738
46 | 0.98726 | -0.24639 | 0.15442 | 0.074789
47 | 0.98738 | -0.24555 | 0.10234 | 0.049563
48 | 0.98751 | -0.24674 | 0.16286 | 0.078876
49 | 0.98797 | -0.24366 | 0 | 0
50 | 0.98679 | -0.24705 | 0 | 0
51 | 0.98796 | -0.24358 | 0 | 0
52 | 0.98678 | -0.24697 | 0.16054 | 0.077752
53 | 0.98678 | -0.24699 | 0 | 0
54 | 0.98796 | -0.24355 | 0.10169 | 0.049253
55 | 0.98569 | -0.24732 | 0.15615 | 0.075628
56 | 0.98572 | -0.24708 | 0.15454 | 0.074848
57 | 0.98576 | -0.24685 | 0 | 0
58 | 0.98693 | -0.25606 | 0 | 0
59 | 0.98708 | -0.25727 | 0 | 0
60 | 0.98611 | -0.26052 | 0.099309 | 0.048097
61 | 0.98576 | -0.24688 | 0.096143 | 0.046564
62 | 0.98861 | -0.24436 | 0 | 0
63 | 0.98619 | -0.2445 | 0.076721 | 0.037158
64 | 0.98656 | -0.24518 | 0.12443 | 0.060267
65 | 0.98906 | -0.24058 | 0.13089 | 0.063393
66 | 0.98911 | -0.23998 | 0 | 0
67 | 0.98922 | -0.23882 | 0 | 0
68 | 0.9893 | -0.23792 | 0.14494 | 0.070196
69 | 0.98939 | -0.23685 | 0 | 0
70 | 0.99003 | -0.22265 | 0.12873 | 0.062345
71 | 0.99053 | -0.21008 | 0.10075 | 0.048796
72 | 0.98954 | -0.23515 | 0.096956 | 0.046958
73 | 0.99227 | -0.1657 | 0.11937 | 0.057813
74 | 0.99307 | -0.14541 | 0 | 0
75 | 0.9937 | -0.13846 | 0 | 0
76 | 0.99417 | -0.13317 | 0 | 0
77 | 0.99368 | -0.13826 | 0 | 0
78 | 0.99367 | -0.13828 | 0.095706 | 0.046352
79 | 0.99417 | -0.13315 | 0.14598 | 0.070702
80 | 0.99625 | -0.080383 | 0.14164 | 0.0686
81 | 0.99868 | -0.011707 | 0.16145 | 0.078195
82 | 0.9987 | -0.011922 | 0 | 0
83 | 0.99877 | -0.012518 | 0 | 0
84 | 0.99861 | -0.012486 | 0.12466 | 0.060376
85 | 0.9992 | -0.0093686 | 0 | 0
86 | 1 | 0 | -11.3031 | -5.224
87 | 0.99847 | -0.017878 | 0.05346 | 0.025892
88 | 0.99876 | -0.012608 | 0.081057 | 0.039258
89 | 0.99921 | -0.0086252 | 0.063946 | 0.030971
90 | 0.99711 | -0.033683 | 0.080168 | 0.038827
91 | 0.99731 | -0.031352 | 0 | 0
92 | 0.99635 | -0.053242 | 0 | 0
93 | 0.99811 | -0.022108 | 0 | 0
94 | 0.99471 | -0.071964 | 0 | 0
95 | 0.99437 | -0.069105 | 0 | 0
96 | 0.99429 | -0.0697 | 0.15199 | 0.073611
97 | 0.99401 | -0.089881 | 0 | 0
98 | 0.9941 | -0.069175 | 0 | 0
99 | 0.99409 | -0.069112 | 0.15555 | 0.075335
100 | 0.99415 | -0.068886 | 0.14396 | 0.069722
101 | 0.99423 | -0.069216 | 0 | 0
102 | 0.99386 | -0.088629 | 0 | 0
103 | 0.994 | -0.089702 | 0.14866 | 0.071999
104 | 0.98691 | -0.093397 | 0.15695 | 0.076014
105 | 0.98692 | -0.093487 | 0 | 0
106 | 0.98695 | -0.093291 | 0.092213 | 0.044661
107 | 0.9902 | -0.083342 | 0 | 0
108 | 0.98979 | -0.080431 | 0 | 0
109 | 0.9904 | -0.084713 | 0.13392 | 0.064861
110 | 0.98771 | -0.09688 | 0.097957 | 0.047443
111 | 0.98768 | -0.096659 | 0 | 0
112 | 0.98786 | -0.097902 | 0 | 0
113 | 0.98721 | -0.093016 | 0 | 0
114 | 0.98714 | -0.092386 | 0.099112 | 0.048002
115 | 0.98695 | -0.093312 | 0 | 0
116 | 0.98697 | -0.093534 | 0.10289 | 0.049834
117 | 0.99417 | -0.068715 | 0 | 0
118 | 0.99842 | -0.018176 | 0.055512 | 0.026886
119 | 0.98932 | -0.084462 | 0.076402 | 0.037003
120 | 0.98933 | -0.084502 | 0 | 0
121 | 0.99144 | -0.082503 | 0.1203 | 0.058265
122 | 0.99145 | -0.082565 | 0 | 0
123 | 0.99147 | -0.082746 | 0 | 0
124 | 0.99397 | -0.089463 | 0.55077 | 0.26675
125 | 0.99135 | -0.081865 | 0 | 0
126 | 0.99156 | -0.083438 | 0.091553 | 0.044341
127 | 0.99076 | -0.08156 | 0.14596 | 0.070691
128 | 0.99082 | -0.082036 | 0 | 0
129 | 0.98978 | -0.080484 | 0.10717 | 0.051903
130 | 0.98976 | -0.080604 | 0.051477 | 0.024931
131 | 0.99135 | -0.081856 | 0.14351 | 0.069503
132 | 0.99124 | -0.081106 | 0 | 0
133 | 0.99123 | -0.081032 | 0.05917 | 0.028657
134 | 0.9916 | -0.083694 | 0.1572 | 0.076138
135 | 0.99338 | -0.084605 | 0 | 0
136 | 0.99345 | -0.085205 | 0.21096 | 0.10217
137 | 0.99304 | -0.087174 | 0.15201 | 0.073621
138 | 0.99099 | -0.083191 | 0 | 0
139 | 0.99173 | -0.082637 | 0 | 0
140 | 0.9922 | -0.086183 | 0 | 0
141 | 0.99219 | -0.086137 | 0.124 | 0.060058
142 | 0.99218 | -0.086285 | 0.15604 | 0.075575
143 | 0.99247 | -0.083988 | 0.12519 | 0.060635
144 | 0.99247 | -0.084017 | 0 | 0
145 | 0.99245 | -0.084123 | 0 | 0
146 | 0.9925 | -0.084233 | 0 | 0
147 | 0.99262 | -0.085186 | 0 | 0
148 | 0.99245 | -0.084109 | 0.12035 | 0.058289
149 | 0.99265 | -0.085395 | 0.10489 | 0.050801
150 | 0.99273 | -0.086002 | 0 | 0
151 | 0.99413 | -0.06833 | 0 | 0
152 | 0.99408 | -0.067965 | 0 | 0
153 | 0.99408 | -0.067936 | 0.1604 | 0.077686
154 | 0.99412 | -0.068286 | 0.14005 | 0.067827
155 | 0.9927 | -0.085952 | 0.095526 | 0.046265
156 | 0.99271 | -0.085864 | 0.10621 | 0.051439
157 | 0.99272 | -0.085911 | 0 | 0
158 | 0.99284 | -0.086901 | 0 | 0
159 | 0.99295 | -0.087818 | 0.10169 | 0.049251
160 | 0.99283 | -0.086835 | 0 | 0
161 | 0.99283 | -0.086875 | 0.11772 | 0.057016
162 | 0.99362 | -0.086638 | 0 | 0
163 | 0.99386 | -0.088625 | 0.072305 | 0.035019
164 | 0.99359 | -0.08631 | 0 | 0
165 | 0.99645 | -0.07817 | 0.1506 | 0.072939
166 | 0.99358 | -0.086251 | 0.27035 | 0.13094
167 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.05518 | -0.026725 | 0.055206 | 0.021183 | 2.6497e-05 | -0.0055419 | 0.0017958 | 0.0017311 | 0.0017958 | 0.98557 | -0.26522 | 0.98608 | -0.26076 | 0.85514
1 | -0.055206 | -0.021183 | 0.055206 | 0.020122 | 1.8156e-07 | -0.0010604 | 0.0017311 | 0.0017202 | 0.0017311 | 0.98608 | -0.26076 | 0.98608 | -0.26078 | 0.78684
2 | -0.17916 | -0.080157 | 0.17917 | 0.08 | 8.2534e-06 | -0.00015776 | 0.005746 | 0.005744 | 0.005746 | 0.98608 | -0.26078 | 0.98613 | -0.26038 | 2.7362
3 | -0.10974 | -0.053152 | 0.10975 | 0.051121 | 1.4626e-06 | -0.0020305 | 0.0035607 | 0.0035352 | 0.0035607 | 0.98859 | -0.24416 | 0.9886 | -0.24427 | 1.6185
4 | -0.10975 | -0.051121 | 0.10975 | 0.049356 | 1.2546e-06 | -0.0017651 | 0.0035352 | 0.0035138 | 0.0035352 | 0.9886 | -0.24427 | 0.98861 | -0.24436 | 1.6069
5 | -0.15232 | -0.073771 | 0.15233 | 0.066461 | 1.0188e-05 | -0.0073099 | 0.0049614 | 0.0048717 | 0.0049614 | 0.98473 | -0.27228 | 0.98479 | -0.2728 | 2.2552
6 | 0.19415 | 0.079705 | -0.19412 | -0.093873 | 3.177e-05 | -0.014167 | 0.0061522 | 0.0063217 | 0.0063217 | 0.98479 | -0.2728 | 0.98464 | -0.27162 | 2.8735
7 | -0.34648 | -0.14617 | 0.34663 | 0.14547 | 0.0001467 | -0.00069359 | 0.011023 | 0.011014 | 0.011023 | 0.98479 | -0.2728 | 0.98524 | -0.26856 | 5.2492
8 | 0.19412 | 0.093873 | -0.19411 | -0.094013 | 8.9758e-06 | -0.00014023 | 0.0063217 | 0.0063236 | 0.0063236 | 0.98464 | -0.27162 | 0.98459 | -0.27193 | 3.0112
9 | -0.34663 | -0.14547 | 0.34663 | 0.14463 | 5.9014e-06 | -0.00084351 | 0.011014 | 0.011005 | 0.011014 | 0.98524 | -0.26856 | 0.98526 | -0.26866 | 5.0065
10 | -0.43836 | -0.18905 | 0.43881 | 0.18784 | 0.0004488 | -0.0012144 | 0.013987 | 0.01397 | 0.013987 | 0.98526 | -0.26866 | 0.98634 | -0.25893 | 6.6606
11 | -0.99782 | -0.45141 | 0.99827 | 0.45141 | 0.00045664 | -3.8736e-06 | 0.032053 | 0.032049 | 0.032053 | 0.98634 | -0.25893 | 0.98682 | -0.25514 | 15.2633
12 | 0.43731 | 0.20463 | -0.43723 | -0.20485 | 8.5479e-05 | -0.00022538 | 0.014131 | 0.014134 | 0.014134 | 0.98634 | -0.25893 | 0.98613 | -0.26038 | 6.7306
13 | -1.0787 | -0.49035 | 1.0788 | 0.48846 | 0.00013276 | -0.0018866 | 0.034662 | 0.034639 | 0.034662 | 0.98682 | -0.25514 | 0.98693 | -0.25606 | 15.7554
14 | 0.099311 | 0.047972 | -0.099309 | -0.048097 | 2.0312e-06 | -0.00012563 | 0.0032286 | 0.0032302 | 0.0032302 | 0.98613 | -0.26038 | 0.98611 | -0.26052 | 1.5382
15 | 1.1769 | 0.53278 | -1.1754 | -0.53253 | 0.0015217 | 0.00025372 | 0.03772 | 0.037728 | 0.037728 | 0.98872 | -0.2444 | 0.98736 | -0.25507 | 17.9658
16 | -4.3339 | -2.0235 | 4.3348 | 2.0209 | 0.00092976 | -0.0026365 | 0.13965 | 0.13961 | 0.13965 | 0.98872 | -0.2444 | 0.98895 | -0.24177 | 38.5767
17 | 0.39585 | 0.18469 | -0.39583 | -0.18679 | 1.9631e-05 | -0.0020999 | 0.012754 | 0.01278 | 0.01278 | 0.98872 | -0.2444 | 0.98868 | -0.244 | 5.809
18 | 2.7611 | 1.306 | -2.7601 | -1.3055 | 0.0010028 | 0.00054555 | 0.089178 | 0.089179 | 0.089179 | 0.98872 | -0.2444 | 0.98834 | -0.24701 | 42.4663
19 | 1.0793 | 0.48596 | -1.079 | -0.48594 | 0.00028281 | 2.2938e-05 | 0.034606 | 0.034608 | 0.034608 | 0.98736 | -0.25507 | 0.98708 | -0.25727 | 16.4799
20 | -4.4837 | -2.093 | 4.4841 | 2.0922 | 0.00032216 | -0.00083878 | 0.14444 | 0.14442 | 0.14444 | 0.98895 | -0.24177 | 0.98903 | -0.24089 | 39.8999
21 | 0.23273 | 0.10779 | -0.23272 | -0.10793 | 1.2423e-05 | -0.00013725 | 0.0074888 | 0.0074906 | 0.0074906 | 0.98868 | -0.244 | 0.98862 | -0.24441 | 3.5669
22 | 2.7601 | 1.3055 | -2.7589 | -1.3076 | 0.0011162 | -0.002119 | 0.089179 | 0.08921 | 0.08921 | 0.98834 | -0.24701 | 0.98797 | -0.24366 | 40.5499
23 | -4.4841 | -2.0922 | 4.4842 | 2.0919 | 0.00011571 | -0.00030137 | 0.14442 | 0.14442 | 0.14442 | 0.98903 | -0.24089 | 0.98906 | -0.24058 | 39.8963
24 | 1.1166 | 0.53011 | -1.1166 | -0.53042 | 2.3752e-05 | -0.00030891 | 0.03617 | 0.036174 | 0.036174 | 0.9865 | -0.24452 | 0.98648 | -0.24435 | 16.4426
25 | -1.2625 | -0.6008 | 1.2626 | 0.60034 | 4.5227e-05 | -0.0004569 | 0.040915 | 0.040909 | 0.040915 | 0.9865 | -0.24452 | 0.98654 | -0.24482 | 18.5977
26 | 1.1166 | 0.53042 | -1.1165 | -0.53193 | 0.00011582 | -0.0015052 | 0.036174 | 0.036193 | 0.036193 | 0.98648 | -0.24435 | 0.98639 | -0.24348 | 16.4514
27 | -1.4169 | -0.67081 | 1.417 | 0.66998 | 0.00010394 | -0.00082919 | 0.045872 | 0.045861 | 0.045872 | 0.98654 | -0.24482 | 0.9866 | -0.24543 | 20.8509
28 | 0.15429 | 0.070473 | -0.15429 | -0.074186 | 5.3056e-06 | -0.0037128 | 0.0049635 | 0.0050096 | 0.0050096 | 0.98654 | -0.24482 | 0.9865 | -0.24454 | 2.2771
29 | 0.15118 | 0.073117 | -0.15118 | -0.073221 | 1.4483e-07 | -0.00010429 | 0.0049148 | 0.0049161 | 0.0049161 | 0.98639 | -0.24348 | 0.98639 | -0.24347 | 2.2346
30 | 0.96528 | 0.45881 | -0.96513 | -0.45881 | 0.00014928 | -5.949e-06 | 0.031278 | 0.03128 | 0.03128 | 0.98639 | -0.24348 | 0.98623 | -0.24457 | 14.8951
31 | 0.25887 | 0.12156 | -0.25886 | -0.12311 | 6.2769e-06 | -0.0015551 | 0.0083678 | 0.0083872 | 0.0083872 | 0.9866 | -0.24543 | 0.98658 | -0.24523 | 3.8124
32 | -1.7749 | -0.83946 | 1.7753 | 0.83757 | 0.00037854 | -0.0018858 | 0.057448 | 0.057423 | 0.057448 | 0.9866 | -0.24543 | 0.9868 | -0.24718 | 26.1126
33 | 0.099028 | 0.04792 | -0.099027 | -0.047961 | 6.5709e-07 | -4.0942e-05 | 0.0032189 | 0.0032194 | 0.0032194 | 0.9866 | -0.24543 | 0.9866 | -0.24547 | 1.5331
34 | 0.15429 | 0.074186 | -0.15429 | -0.074724 | 7.7683e-07 | -0.0005378 | 0.0050096 | 0.0050164 | 0.0050164 | 0.9865 | -0.24454 | 0.9865 | -0.2445 | 2.2802
35 | 0.18674 | 0.085801 | -0.18673 | -0.086537 | 1.535e-06 | -0.00073643 | 0.0060152 | 0.0060243 | 0.0060243 | 0.98623 | -0.24457 | 0.98622 | -0.24451 | 2.7383
36 | 0.77839 | 0.37301 | -0.77823 | -0.37308 | 0.00016212 | -6.3921e-05 | 0.025265 | 0.025267 | 0.025267 | 0.98623 | -0.24457 | 0.98601 | -0.246 | 12.032
37 | 0.13442 | 0.064632 | -0.13442 | -0.065104 | 5.1686e-07 | -0.00047159 | 0.0043643 | 0.0043702 | 0.0043702 | 0.98658 | -0.24523 | 0.98658 | -0.2452 | 1.9865
38 | 0.12444 | 0.058479 | -0.12444 | -0.060224 | 1.6316e-06 | -0.0017449 | 0.0040231 | 0.0040451 | 0.0040451 | 0.98658 | -0.24523 | 0.98657 | -0.24512 | 1.8387
39 | 0.29981 | 0.14336 | -0.29981 | -0.14415 | 4.2989e-06 | -0.00079007 | 0.0097217 | 0.0097317 | 0.0097317 | 0.9868 | -0.24718 | 0.98679 | -0.24706 | 4.4235
40 | -2.0751 | -0.98093 | 2.0753 | 0.98003 | 0.00025397 | -0.00090602 | 0.067144 | 0.067132 | 0.067144 | 0.9868 | -0.24718 | 0.98691 | -0.24819 | 30.5202
41 | 0.076723 | 0.033257 | -0.076722 | -0.033367 | 1.0235e-06 | -0.00011064 | 0.0024477 | 0.002449 | 0.002449 | 0.98622 | -0.24451 | 0.98621 | -0.24463 | 1.1662
42 | 0.64252 | 0.30735 | -0.64239 | -0.30745 | 0.00012249 | -0.00010672 | 0.020852 | 0.020855 | 0.020855 | 0.98601 | -0.246 | 0.98581 | -0.24731 | 9.9308
43 | 0.12444 | 0.060224 | -0.12443 | -0.060267 | 1.0895e-06 | -4.2736e-05 | 0.0040451 | 0.0040456 | 0.0040456 | 0.98657 | -0.24512 | 0.98656 | -0.24518 | 1.9265
44 | 0.16054 | 0.076698 | -0.16054 | -0.076826 | 1.9838e-07 | -0.00012742 | 0.0052049 | 0.0052065 | 0.0052065 | 0.98679 | -0.24706 | 0.98679 | -0.24705 | 2.3666
45 | -2.0753 | -0.98003 | 2.0754 | 0.97973 | 8.3762e-05 | -0.00029895 | 0.067132 | 0.067128 | 0.067132 | 0.98691 | -0.24819 | 0.98695 | -0.24852 | 30.5146
46 | 0.076722 | 0.033367 | -0.076721 | -0.036029 | 9.296e-07 | -0.0026614 | 0.002449 | 0.0024811 | 0.0024811 | 0.98621 | -0.24463 | 0.98619 | -0.24454 | 1.1278
47 | 0.40688 | 0.19463 | -0.40686 | -0.19647 | 1.8551e-05 | -0.0018396 | 0.013207 | 0.013231 | 0.013231 | 0.98581 | -0.24731 | 0.98577 | -0.24692 | 6.014
48 | 0.12371 | 0.058721 | -0.12371 | -0.059917 | 1.1108e-06 | -0.0011958 | 0.0040101 | 0.0040253 | 0.0040253 | 0.98581 | -0.24731 | 0.9858 | -0.24723 | 1.8297
49 | 0.1118 | 0.054107 | -0.1118 | -0.054148 | 8.519e-07 | -4.1393e-05 | 0.0036371 | 0.0036377 | 0.0036377 | 0.98581 | -0.24731 | 0.9858 | -0.24736 | 1.7322
50 | 0.10975 | 0.048374 | -0.10975 | -0.049356 | 6.9153e-07 | -0.00098211 | 0.0035021 | 0.0035138 | 0.0035138 | 0.98862 | -0.24441 | 0.98861 | -0.24436 | 1.5972
51 | 0.076721 | 0.036029 | -0.076721 | -0.037158 | 4.0186e-07 | -0.001129 | 0.0024811 | 0.0024953 | 0.0024953 | 0.98619 | -0.24454 | 0.98619 | -0.2445 | 1.1342
52 | 0.40686 | 0.19647 | -0.40685 | -0.19681 | 3.4763e-06 | -0.00034397 | 0.013231 | 0.013235 | 0.013235 | 0.98577 | -0.24692 | 0.98576 | -0.24685 | 6.016
53 | -2.2352 | -1.0571 | 2.2358 | 1.0574 | 0.00066524 | 0.00033364 | 0.07232 | 0.072319 | 0.07232 | 0.98695 | -0.24852 | 0.98726 | -0.24639 | 34.4382
54 | -2.3903 | -1.1322 | 2.3905 | 1.1324 | 0.00027896 | 0.00014427 | 0.077336 | 0.077336 | 0.077336 | 0.98726 | -0.24639 | 0.98738 | -0.24555 | 36.8266
55 | -2.4929 | -1.1819 | 2.4932 | 1.1811 | 0.00035745 | -0.00085222 | 0.08066 | 0.080648 | 0.08066 | 0.98738 | -0.24555 | 0.98751 | -0.24674 | 36.6635
56 | -2.6561 | -1.26 | 2.6572 | 1.2606 | 0.0011525 | 0.00061986 | 0.085937 | 0.085936 | 0.085937 | 0.98751 | -0.24674 | 0.98797 | -0.24366 | 40.9225
57 | 0.1017 | 0.047037 | -0.10169 | -0.04863 | 9.8387e-07 | -0.0015925 | 0.0032739 | 0.0032937 | 0.0032937 | 0.98797 | -0.24366 | 0.98796 | -0.24358 | 1.4971
58 | 0.16054 | 0.076826 | -0.16054 | -0.077567 | 1.1559e-06 | -0.00074091 | 0.0052065 | 0.0052159 | 0.0052159 | 0.98679 | -0.24705 | 0.98678 | -0.24699 | 2.3709
59 | 0.10169 | 0.04863 | -0.10169 | -0.049253 | 3.8808e-07 | -0.00062286 | 0.0032937 | 0.0033016 | 0.0033016 | 0.98796 | -0.24358 | 0.98796 | -0.24355 | 1.5007
60 | -0.16054 | -0.077752 | 0.16054 | 0.077567 | 2.9053e-07 | -0.00018581 | 0.0052183 | 0.0052159 | 0.0052183 | 0.98678 | -0.24697 | 0.98678 | -0.24699 | 2.3719
61 | -0.15615 | -0.075628 | 0.15616 | 0.075493 | 5.4604e-06 | -0.00013431 | 0.0050813 | 0.0050795 | 0.0050813 | 0.98569 | -0.24732 | 0.98572 | -0.24708 | 2.4197
62 | -0.3107 | -0.15034 | 0.31071 | 0.15028 | 1.117e-05 | -6.4187e-05 | 0.010108 | 0.010107 | 0.010108 | 0.98572 | -0.24708 | 0.98576 | -0.24685 | 4.8135
63 | 0.096143 | 0.046532 | -0.096143 | -0.046564 | 4.8688e-07 | -3.2091e-05 | 0.0031279 | 0.0031283 | 0.0031283 | 0.98576 | -0.24685 | 0.98576 | -0.24688 | 1.4897
64 | -1.0788 | -0.48846 | 1.079 | 0.48594 | 0.00017696 | -0.0025195 | 0.034639 | 0.034608 | 0.034639 | 0.98693 | -0.25606 | 0.98708 | -0.25727 | 15.7449
65 | -4.6151 | -2.1553 | 4.6153 | 2.1547 | 0.00022393 | -0.00054135 | 0.14866 | 0.14866 | 0.14866 | 0.98906 | -0.24058 | 0.98911 | -0.23998 | 41.0674
66 | -4.6153 | -2.1547 | 4.6157 | 2.1537 | 0.00043941 | -0.0010627 | 0.14866 | 0.14864 | 0.14866 | 0.98911 | -0.23998 | 0.98922 | -0.23882 | 41.065
67 | -4.6157 | -2.1537 | 4.6161 | 2.1529 | 0.00033963 | -0.00082182 | 0.14864 | 0.14863 | 0.14864 | 0.98922 | -0.23882 | 0.9893 | -0.23792 | 41.0603
68 | -4.761 | -2.223 | 4.7614 | 2.2221 | 0.00041597 | -0.00092801 | 0.15332 | 0.15331 | 0.15332 | 0.9893 | -0.23792 | 0.98939 | -0.23685 | 42.3546
69 | -4.7614 | -2.2221 | 4.7621 | 2.2206 | 0.00066078 | -0.0014751 | 0.15331 | 0.15328 | 0.15331 | 0.98939 | -0.23685 | 0.98954 | -0.23515 | 42.3505
70 | -4.9897 | -2.332 | 4.9917 | 2.3342 | 0.001973 | 0.002154 | 0.1606 | 0.16059 | 0.1606 | 0.99003 | -0.22265 | 0.99053 | -0.21008 | 45.8845
71 | 4.861 | 2.2697 | -4.859 | -2.2676 | 0.0019076 | 0.0020773 | 0.15643 | 0.15643 | 0.15643 | 0.99003 | -0.22265 | 0.98954 | -0.23515 | 44.6934
72 | -5.0924 | -2.383 | 5.0995 | 2.3908 | 0.0071268 | 0.0077944 | 0.16386 | 0.16385 | 0.16386 | 0.99053 | -0.21008 | 0.99227 | -0.1657 | 46.8162
73 | -5.2189 | -2.4486 | 5.2222 | 2.4522 | 0.0033453 | 0.0036659 | 0.16771 | 0.16771 | 0.16771 | 0.99227 | -0.1657 | 0.99307 | -0.14541 | 47.9173
74 | -5.2222 | -2.4522 | 5.2252 | 2.447 | 0.0029978 | -0.0052961 | 0.16771 | 0.16762 | 0.16771 | 0.99307 | -0.14541 | 0.9937 | -0.13846 | 46.3283
75 | -5.321 | -2.4886 | 5.3233 | 2.4848 | 0.0023067 | -0.0038841 | 0.17065 | 0.17058 | 0.17065 | 0.9937 | -0.13846 | 0.99417 | -0.13317 | 47.1403
76 | 0.095708 | 0.041692 | -0.095706 | -0.046332 | 2.461e-06 | -0.0046399 | 0.0030327 | 0.0030891 | 0.0030891 | 0.9937 | -0.13846 | 0.99368 | -0.13826 | 1.4041
77 | 0.14598 | 0.070484 | -0.14598 | -0.070702 | 2.7382e-07 | -0.00021825 | 0.004707 | 0.0047098 | 0.0047098 | 0.99417 | -0.13317 | 0.99417 | -0.13315 | 2.1408
78 | -5.4692 | -2.5552 | 5.4783 | 2.5652 | 0.0090912 | 0.0099973 | 0.17529 | 0.17528 | 0.17529 | 0.99417 | -0.13317 | 0.99625 | -0.080383 | 50.0818
79 | 0.095706 | 0.046332 | -0.095706 | -0.046352 | 2.9177e-07 | -2.0045e-05 | 0.0030891 | 0.0030893 | 0.0030893 | 0.99368 | -0.13826 | 0.99367 | -0.13828 | 1.4711
80 | -5.62 | -2.6338 | 5.621 | 2.6324 | 0.0010256 | -0.0014909 | 0.17984 | 0.17981 | 0.17984 | 0.99625 | -0.080383 | 0.99645 | -0.07817 | 49.6799
81 | -0.16145 | -0.078195 | 0.16146 | 0.075419 | 4.1598e-06 | -0.0027769 | 0.0051855 | 0.005151 | 0.0051855 | 0.99868 | -0.011707 | 0.9987 | -0.011922 | 2.357
82 | -0.28613 | -0.13536 | 0.28615 | 0.13076 | 2.1511e-05 | -0.0046061 | 0.0091494 | 0.0090932 | 0.0091494 | 0.9987 | -0.011922 | 0.99877 | -0.012518 | 4.1588
83 | 0.12467 | 0.059944 | -0.12466 | -0.060376 | 1.0515e-05 | -0.00043227 | 0.0039986 | 0.0040041 | 0.0040041 | 0.9987 | -0.011922 | 0.99861 | -0.012486 | 1.9067
84 | 0.081058 | 0.03915 | -0.081057 | -0.039258 | 1.1e-06 | -0.00010787 | 0.0026018 | 0.0026031 | 0.0026031 | 0.99877 | -0.012518 | 0.99876 | -0.012608 | 1.2396
85 | -0.36721 | -0.16991 | 0.36736 | 0.16927 | 0.0001488 | -0.00063487 | 0.011695 | 0.011686 | 0.011695 | 0.99877 | -0.012518 | 0.9992 | -0.0093686 | 5.5688
86 | -5.4328 | -2.4753 | 5.4367 | 2.4687 | 0.0039452 | -0.0065509 | 0.17248 | 0.17237 | 0.17248 | 0.9992 | -0.0093686 | 1 | 0 | 47.6462
87 | 5.0654 | 2.306 | -5.062 | -2.3128 | 0.0033565 | -0.006754 | 0.16079 | 0.1609 | 0.1609 | 0.9992 | -0.0093686 | 0.99847 | -0.017878 | 44.4486
88 | 5.8524 | 2.7448 | -5.8482 | -2.7503 | 0.0041815 | -0.0054793 | 0.1866 | 0.18671 | 0.18671 | 1 | 0 | 0.99921 | -0.0086252 | 51.5766
89 | 0.055515 | 0.026376 | -0.055512 | -0.026886 | 2.4256e-06 | -0.00050974 | 0.001777 | 0.0017834 | 0.0017834 | 0.99847 | -0.017878 | 0.99842 | -0.018176 | 0.84922
90 | 4.9531 | 2.2605 | -4.9514 | -2.264 | 0.0016374 | -0.003486 | 0.15741 | 0.15747 | 0.15747 | 0.99847 | -0.017878 | 0.99811 | -0.022108 | 43.499
91 | 5.7843 | 2.7193 | -5.7716 | -2.7053 | 0.012691 | 0.014009 | 0.18465 | 0.18466 | 0.18466 | 0.99921 | -0.0086252 | 0.99645 | -0.07817 | 52.7603
92 | -4.9469 | -2.2735 | 4.9478 | 2.2716 | 0.00091149 | -0.0019294 | 0.15762 | 0.15759 | 0.15762 | 0.99711 | -0.033683 | 0.99731 | -0.031352 | 43.5418
93 | 4.8668 | 2.2347 | -4.8638 | -2.2315 | 0.0029363 | 0.0031924 | 0.15504 | 0.15505 | 0.15505 | 0.99711 | -0.033683 | 0.99635 | -0.053242 | 44.2986
94 | -4.9478 | -2.2716 | 4.9514 | 2.264 | 0.0035983 | -0.0076371 | 0.15759 | 0.15747 | 0.15759 | 0.99731 | -0.031352 | 0.99811 | -0.022108 | 43.5332
95 | 4.8638 | 2.2315 | -4.8566 | -2.2474 | 0.0072399 | -0.015904 | 0.15505 | 0.1553 | 0.1553 | 0.99635 | -0.053242 | 0.99471 | -0.071964 | 42.9011
96 | 4.1042 | 1.905 | -4.1019 | -1.9025 | 0.0022938 | 0.0024435 | 0.13131 | 0.13131 | 0.13131 | 0.99471 | -0.071964 | 0.99401 | -0.089881 | 37.5183
97 | 0.75239 | 0.34246 | -0.75211 | -0.35086 | 0.00027708 | -0.008398 | 0.02399 | 0.024093 | 0.024093 | 0.99471 | -0.071964 | 0.99437 | -0.069105 | 10.9516
98 | 0.75211 | 0.35086 | -0.75205 | -0.35089 | 5.9462e-05 | -3.061e-05 | 0.024093 | 0.024094 | 0.024094 | 0.99437 | -0.069105 | 0.99429 | -0.0697 | 11.4735
99 | 0.60007 | 0.27728 | -0.60003 | -0.27903 | 3.6866e-05 | -0.0017567 | 0.019192 | 0.019214 | 0.019214 | 0.99429 | -0.0697 | 0.99423 | -0.069216 | 8.7334
100 | 3.4024 | 1.5651 | -3.4019 | -1.5658 | 0.00055081 | -0.00065922 | 0.10876 | 0.10877 | 0.10877 | 0.99401 | -0.089881 | 0.99386 | -0.088629 | 49.4427
101 | 0.69946 | 0.33741 | -0.69945 | -0.33791 | 1.4445e-05 | -0.00049742 | 0.022553 | 0.02256 | 0.02256 | 0.99401 | -0.089881 | 0.994 | -0.089702 | 10.2544
102 | 0.15555 | 0.074534 | -0.15555 | -0.075335 | 1.1406e-06 | -0.00080163 | 0.0050087 | 0.0050188 | 0.0050188 | 0.9941 | -0.069175 | 0.99409 | -0.069112 | 2.2813
103 | -0.15555 | -0.074534 | 0.15556 | 0.074366 | 6.5149e-06 | -0.00016796 | 0.0050087 | 0.0050066 | 0.0050087 | 0.9941 | -0.069175 | 0.99415 | -0.068886 | 2.3851
104 | -0.29951 | -0.14409 | 0.29952 | 0.14404 | 7.5876e-06 | -4.9196e-05 | 0.0096512 | 0.0096505 | 0.0096512 | 0.99415 | -0.068886 | 0.99417 | -0.068715 | 4.5958
105 | 0.60003 | 0.27903 | -0.59999 | -0.28082 | 3.7629e-05 | -0.0017887 | 0.019214 | 0.019236 | 0.019236 | 0.99423 | -0.069216 | 0.99417 | -0.068715 | 8.7435
106 | 3.3296 | 1.5309 | -3.3287 | -1.532 | 0.00085793 | -0.0010827 | 0.10644 | 0.10646 | 0.10646 | 0.99386 | -0.088629 | 0.99362 | -0.086638 | 48.3904
107 | 0.072305 | 0.034886 | -0.072305 | -0.035019 | 4.0845e-08 | -0.00013256 | 0.0023318 | 0.0023335 | 0.0023335 | 0.99386 | -0.088629 | 0.99386 | -0.088625 | 1.0607
108 | 0.55079 | 0.26591 | -0.55077 | -0.26675 | 1.5182e-05 | -0.00084523 | 0.017763 | 0.017773 | 0.017773 | 0.994 | -0.089702 | 0.99397 | -0.089463 | 8.0788
109 | -0.15695 | -0.076014 | 0.15695 | 0.07491 | 1.6453e-06 | -0.001104 | 0.0051009 | 0.0050869 | 0.0051009 | 0.98691 | -0.093397 | 0.98692 | -0.093487 | 2.3186
110 | -0.15695 | -0.07491 | 0.15696 | 0.074802 | 4.4079e-06 | -0.00010844 | 0.0050869 | 0.0050855 | 0.0050869 | 0.98692 | -0.093487 | 0.98695 | -0.093291 | 2.4224
111 | -0.24917 | -0.11946 | 0.24917 | 0.1193 | 6.2477e-07 | -0.00016647 | 0.0080824 | 0.0080803 | 0.0080824 | 0.98695 | -0.093291 | 0.98695 | -0.093312 | 3.6738
112 | 0.78598 | 0.33718 | -0.78564 | -0.34671 | 0.00034284 | -0.0095217 | 0.024934 | 0.025045 | 0.025045 | 0.9902 | -0.083342 | 0.98979 | -0.080431 | 11.3843
113 | -0.78598 | -0.33718 | 0.78615 | 0.33238 | 0.00017188 | -0.0048091 | 0.024934 | 0.024878 | 0.024934 | 0.9902 | -0.083342 | 0.9904 | -0.084713 | 11.3334
114 | 0.10717 | 0.051856 | -0.10717 | -0.051903 | 8.6294e-07 | -4.6434e-05 | 0.0034722 | 0.0034728 | 0.0034728 | 0.98979 | -0.080431 | 0.98978 | -0.080484 | 1.6537
115 | 0.051478 | 0.024621 | -0.051477 | -0.024931 | 1.3163e-06 | -0.00031038 | 0.0016643 | 0.0016682 | 0.0016682 | 0.98979 | -0.080431 | 0.98976 | -0.080604 | 0.79438
116 | 0.62699 | 0.27023 | -0.62672 | -0.27051 | 0.0002708 | -0.00027836 | 0.019913 | 0.019918 | 0.019918 | 0.98979 | -0.080431 | 0.98933 | -0.084502 | 9.4847
117 | -0.92007 | -0.39724 | 0.92038 | 0.39719 | 0.00030855 | -4.4512e-05 | 0.02921 | 0.029208 | 0.02921 | 0.9904 | -0.084713 | 0.99076 | -0.08156 | 13.9097
118 | 0.45151 | 0.19227 | -0.4515 | -0.1936 | 1.5719e-05 | -0.0013271 | 0.014343 | 0.014358 | 0.014358 | 0.98771 | -0.09688 | 0.98768 | -0.096659 | 6.5265
119 | -0.54947 | -0.23971 | 0.54956 | 0.23483 | 8.6077e-05 | -0.0048835 | 0.017521 | 0.017464 | 0.017521 | 0.98771 | -0.09688 | 0.98786 | -0.097902 | 7.9641
120 | 0.4515 | 0.1936 | -0.45127 | -0.21232 | 0.00022551 | -0.018718 | 0.014358 | 0.014583 | 0.014583 | 0.98768 | -0.096659 | 0.98721 | -0.093016 | 6.6288
121 | -0.54956 | -0.23483 | 0.55032 | 0.23367 | 0.00076049 | -0.0011582 | 0.017464 | 0.017445 | 0.017464 | 0.98786 | -0.097902 | 0.98932 | -0.084462 | 8.3162
122 | 0.45127 | 0.21232 | -0.45124 | -0.21511 | 3.4334e-05 | -0.0027968 | 0.014583 | 0.014619 | 0.014619 | 0.98721 | -0.093016 | 0.98714 | -0.092386 | 6.6448
123 | 0.35213 | 0.16711 | -0.35207 | -0.16736 | 5.7104e-05 | -0.00025107 | 0.011398 | 0.011402 | 0.011402 | 0.98714 | -0.092386 | 0.98697 | -0.093534 | 5.4294
124 | -0.24917 | -0.1193 | 0.24918 | 0.11753 | 6.6166e-06 | -0.0017684 | 0.0080803 | 0.008058 | 0.0080803 | 0.98695 | -0.093312 | 0.98697 | -0.093534 | 3.6728
125 | 0.30047 | 0.13678 | -0.30046 | -0.13965 | 1.4974e-05 | -0.0028655 | 0.0095862 | 0.009621 | 0.009621 | 0.99417 | -0.068715 | 0.99413 | -0.06833 | 4.3732
126 | -0.62672 | -0.27067 | 0.62672 | 0.27051 | 3.8179e-06 | -0.00016731 | 0.01992 | 0.019918 | 0.01992 | 0.98932 | -0.084462 | 0.98933 | -0.084502 | 9.0544
127 | -0.1203 | -0.058265 | 0.1203 | 0.057263 | 8.6084e-07 | -0.0010021 | 0.003892 | 0.0038794 | 0.003892 | 0.99144 | -0.082503 | 0.99145 | -0.082565 | 1.7691
128 | -0.1203 | -0.057263 | 0.12031 | 0.053973 | 2.7873e-06 | -0.0032897 | 0.0038794 | 0.0038392 | 0.0038794 | 0.99145 | -0.082565 | 0.99147 | -0.082746 | 1.7634
129 | 1.2698 | 0.55851 | -1.2697 | -0.56021 | 0.00016196 | -0.0016963 | 0.04039 | 0.040411 | 0.040411 | 0.99147 | -0.082746 | 0.99135 | -0.081865 | 18.3685
130 | -1.3901 | -0.61248 | 1.3903 | 0.61127 | 0.00013965 | -0.0012141 | 0.044229 | 0.044215 | 0.044229 | 0.99147 | -0.082746 | 0.99156 | -0.083438 | 20.1042
131 | 0.14351 | 0.069383 | -0.14351 | -0.069503 | 1.4666e-07 | -0.00011956 | 0.0046416 | 0.0046431 | 0.0046431 | 0.99135 | -0.081865 | 0.99135 | -0.081856 | 2.1105
132 | 1.1262 | 0.49082 | -1.126 | -0.49253 | 0.00012688 | -0.001704 | 0.035772 | 0.035793 | 0.035793 | 0.99135 | -0.081865 | 0.99124 | -0.081106 | 16.2694
133 | -1.4818 | -0.65561 | 1.4819 | 0.6552 | 5.4357e-05 | -0.00041344 | 0.047174 | 0.047169 | 0.047174 | 0.99156 | -0.083438 | 0.9916 | -0.083694 | 21.4428
134 | -1.0663 | -0.46788 | 1.0664 | 0.46677 | 7.4639e-05 | -0.0011166 | 0.033929 | 0.033916 | 0.033929 | 0.99076 | -0.08156 | 0.99082 | -0.082036 | 15.4223
135 | -1.0664 | -0.46677 | 1.0666 | 0.46402 | 0.00018311 | -0.0027439 | 0.033916 | 0.033883 | 0.033916 | 0.99082 | -0.082036 | 0.99099 | -0.083191 | 15.4162
136 | 1.126 | 0.49253 | -1.126 | -0.49269 | 1.2356e-05 | -0.00016581 | 0.035793 | 0.035795 | 0.035795 | 0.99124 | -0.081106 | 0.99123 | -0.081032 | 16.2703
137 | 1.0668 | 0.46403 | -1.0666 | -0.46402 | 0.00024984 | 1.3253e-05 | 0.033881 | 0.033883 | 0.033883 | 0.99123 | -0.081032 | 0.99099 | -0.083191 | 16.1348
138 | -1.6391 | -0.73133 | 1.6393 | 0.73141 | 0.00020122 | 7.7476e-05 | 0.052251 | 0.052251 | 0.052251 | 0.9916 | -0.083694 | 0.99173 | -0.082637 | 24.8817
139 | -2.8466 | -1.303 | 2.8468 | 1.3026 | 0.00022373 | -0.00041076 | 0.090977 | 0.090971 | 0.090977 | 0.99338 | -0.084605 | 0.99345 | -0.085205 | 41.3531
140 | 2.8466 | 1.303 | -2.8457 | -1.3025 | 0.00091511 | 0.00050012 | 0.090977 | 0.090978 | 0.090978 | 0.99338 | -0.084605 | 0.99304 | -0.087174 | 43.3227
141 | -3.0578 | -1.4048 | 3.0584 | 1.4039 | 0.00056984 | -0.0008833 | 0.097781 | 0.097768 | 0.097781 | 0.99345 | -0.085205 | 0.99362 | -0.086638 | 44.4458
142 | 2.6937 | 1.2289 | -2.6935 | -1.2288 | 0.0002151 | 0.00011555 | 0.086069 | 0.086069 | 0.086069 | 0.99304 | -0.087174 | 0.99295 | -0.087818 | 40.9854
143 | -1.6393 | -0.73141 | 1.6401 | 0.72635 | 0.00082176 | -0.0050597 | 0.052251 | 0.052188 | 0.052251 | 0.99173 | -0.082637 | 0.9922 | -0.086183 | 23.7504
144 | 0.124 | 0.059338 | -0.124 | -0.060058 | 6.5579e-07 | -0.00071995 | 0.0039996 | 0.0040087 | 0.0040087 | 0.9922 | -0.086183 | 0.99219 | -0.086137 | 1.8221
145 | 0.15605 | 0.075514 | -0.15604 | -0.075575 | 2.4064e-06 | -6.0879e-05 | 0.0050437 | 0.0050445 | 0.0050445 | 0.9922 | -0.086183 | 0.99218 | -0.086285 | 2.4022
146 | -1.9202 | -0.8612 | 1.9207 | 0.86143 | 0.00049691 | 0.00022379 | 0.061228 | 0.061227 | 0.061228 | 0.9922 | -0.086183 | 0.99247 | -0.083988 | 29.156
147 | -2.1662 | -0.98002 | 2.1663 | 0.97977 | 7.1696e-05 | -0.00024285 | 0.069155 | 0.069152 | 0.069155 | 0.99247 | -0.083988 | 0.9925 | -0.084233 | 31.4342
148 | 0.12036 | 0.057954 | -0.12035 | -0.057977 | 5.1684e-07 | -2.227e-05 | 0.0038854 | 0.0038857 | 0.0038857 | 0.99247 | -0.083988 | 0.99247 | -0.084017 | 1.8503
149 | 0.12035 | 0.057977 | -0.12035 | -0.058059 | 1.9117e-06 | -8.2339e-05 | 0.0038857 | 0.0038868 | 0.0038868 | 0.99247 | -0.084017 | 0.99245 | -0.084123 | 1.8508
150 | 0.12035 | 0.058059 | -0.12035 | -0.058289 | 1.9774e-07 | -0.00023034 | 0.0038868 | 0.0038897 | 0.0038897 | 0.99245 | -0.084123 | 0.99245 | -0.084109 | 1.768
151 | -2.1663 | -0.97977 | 2.1666 | 0.97883 | 0.00027927 | -0.00094633 | 0.069152 | 0.06914 | 0.069152 | 0.9925 | -0.084233 | 0.99262 | -0.085186 | 31.4328
152 | -2.1666 | -0.97883 | 2.1666 | 0.97862 | 6.1479e-05 | -0.00020841 | 0.06914 | 0.069137 | 0.06914 | 0.99262 | -0.085186 | 0.99265 | -0.085395 | 31.4272
153 | -2.2715 | -1.0294 | 2.2717 | 1.0289 | 0.0001853 | -0.00056597 | 0.072525 | 0.072518 | 0.072525 | 0.99265 | -0.085395 | 0.99273 | -0.086002 | 32.966
154 | -2.4734 | -1.1251 | 2.4737 | 1.1244 | 0.0002962 | -0.0007485 | 0.079017 | 0.079007 | 0.079017 | 0.99273 | -0.086002 | 0.99284 | -0.086901 | 35.9167
155 | 0.20174 | 0.09627 | -0.20174 | -0.097166 | 2.1542e-06 | -0.00089647 | 0.0065001 | 0.0065113 | 0.0065113 | 0.99273 | -0.086002 | 0.99272 | -0.085911 | 2.9597
156 | 0.14005 | 0.067205 | -0.14005 | -0.067827 | 7.1716e-07 | -0.00062172 | 0.0045107 | 0.0045185 | 0.0045185 | 0.99413 | -0.06833 | 0.99412 | -0.068286 | 2.0539
157 | 0.16041 | 0.072444 | -0.1604 | -0.077326 | 7.3027e-06 | -0.0048822 | 0.005111 | 0.005171 | 0.005171 | 0.99413 | -0.06833 | 0.99408 | -0.067965 | 2.3504
158 | 0.1604 | 0.077326 | -0.1604 | -0.077686 | 5.4456e-07 | -0.00035946 | 0.005171 | 0.0051755 | 0.0051755 | 0.99408 | -0.067965 | 0.99408 | -0.067936 | 2.3525
159 | -0.095526 | -0.046265 | 0.095527 | 0.046178 | 1.2681e-06 | -8.7134e-05 | 0.0030865 | 0.0030854 | 0.0030865 | 0.9927 | -0.085952 | 0.99271 | -0.085864 | 1.4698
160 | -0.20173 | -0.097617 | 0.20174 | 0.097166 | 1.0859e-06 | -0.00045071 | 0.006517 | 0.0065113 | 0.006517 | 0.99271 | -0.085864 | 0.99272 | -0.085911 | 2.9623
161 | -2.5915 | -1.1803 | 2.5918 | 1.1795 | 0.00031582 | -0.00071871 | 0.082795 | 0.082785 | 0.082795 | 0.99284 | -0.086901 | 0.99295 | -0.087818 | 37.6341
162 | 0.11772 | 0.055881 | -0.11772 | -0.056984 | 9.0195e-07 | -0.0011033 | 0.003789 | 0.0038028 | 0.0038028 | 0.99284 | -0.086901 | 0.99283 | -0.086835 | 1.7286
163 | 0.11772 | 0.056984 | -0.11772 | -0.057016 | 6.9888e-07 | -3.1477e-05 | 0.0038028 | 0.0038032 | 0.0038032 | 0.99283 | -0.086835 | 0.99283 | -0.086875 | 1.8111
164 | 0.27036 | 0.12807 | -0.27035 | -0.13051 | 1.0482e-05 | -0.0024383 | 0.0086914 | 0.008722 | 0.008722 | 0.99362 | -0.086638 | 0.99359 | -0.08631 | 3.9646
165 | 0.27035 | 0.13051 | -0.27035 | -0.13094 | 1.8518e-06 | -0.00042897 | 0.008722 | 0.0087275 | 0.0087275 | 0.99359 | -0.08631 | 0.99358 | -0.086251 | 3.967

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 11.3031 | 5.224

## res_load
| p_mw | q_mvar
0 | 0.05518 | 0.026725
1 | 0.12396 | 0.060035
2 | 0.10974 | 0.053152
3 | 0.15232 | 0.073771
4 | 0.091727 | 0.044426
5 | 0.1217 | 0.05894
6 | 0.080402 | 0.03894
7 | 0.15874 | 0.076883
8 | 0.096146 | 0.046566
9 | 0.14897 | 0.072147
10 | 0.1631 | 0.078994
11 | 0.19411 | 0.094013
12 | 0.14595 | 0.070686
13 | 0.15118 | 0.073221
14 | 0.099027 | 0.047961
15 | 0.15429 | 0.074724
16 | 0.11001 | 0.053281
17 | 0.13572 | 0.06573
18 | 0.13442 | 0.065104
19 | 0.13927 | 0.06745
20 | 0.12297 | 0.059557
21 | 0.1118 | 0.054148
22 | 0.12371 | 0.059917
23 | 0.15977 | 0.07738
24 | 0.15442 | 0.074789
25 | 0.10234 | 0.049563
26 | 0.16286 | 0.078876
27 | 0.16054 | 0.077752
28 | 0.10169 | 0.049253
29 | 0.15615 | 0.075628
30 | 0.15454 | 0.074848
31 | 0.099309 | 0.048097
32 | 0.096143 | 0.046564
33 | 0.076721 | 0.037158
34 | 0.12443 | 0.060267
35 | 0.13089 | 0.063393
36 | 0.14494 | 0.070196
37 | 0.12873 | 0.062345
38 | 0.10075 | 0.048796
39 | 0.096956 | 0.046958
40 | 0.11937 | 0.057813
41 | 0.095706 | 0.046352
42 | 0.14598 | 0.070702
43 | 0.14164 | 0.0686
44 | 0.16145 | 0.078195
45 | 0.12466 | 0.060376
46 | 0.05346 | 0.025892
47 | 0.081057 | 0.039258
48 | 0.063946 | 0.030971
49 | 0.080168 | 0.038827
50 | 0.15199 | 0.073611
51 | 0.15555 | 0.075335
52 | 0.14396 | 0.069722
53 | 0.14866 | 0.071999
54 | 0.15695 | 0.076014
55 | 0.092213 | 0.044661
56 | 0.13392 | 0.064861
57 | 0.097957 | 0.047443
58 | 0.099112 | 0.048002
59 | 0.10289 | 0.049834
60 | 0.055512 | 0.026886
61 | 0.076402 | 0.037003
62 | 0.1203 | 0.058265
63 | 0.55077 | 0.26675
64 | 0.091553 | 0.044341
65 | 0.14596 | 0.070691
66 | 0.10717 | 0.051903
67 | 0.051477 | 0.024931
68 | 0.14351 | 0.069503
69 | 0.05917 | 0.028657
70 | 0.1572 | 0.076138
71 | 0.21096 | 0.10217
72 | 0.15201 | 0.073621
73 | 0.124 | 0.060058
74 | 0.15604 | 0.075575
75 | 0.12519 | 0.060635
76 | 0.12035 | 0.058289
77 | 0.10489 | 0.050801
78 | 0.1604 | 0.077686
79 | 0.14005 | 0.067827
80 | 0.095526 | 0.046265
81 | 0.10621 | 0.051439
82 | 0.10169 | 0.049251
83 | 0.11772 | 0.057016
84 | 0.072305 | 0.035019
85 | 0.1506 | 0.072939
86 | 0.27035 | 0.13094

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1