## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_118_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_118_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_118_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_118_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_118_0_node_5 | 20 | n |  | TRUE
5 | bus_MV_118_0_node_131 | 20 | n |  | TRUE
6 | bus_MV_118_0_node_11 | 20 | n |  | TRUE
7 | bus_MV_118_0_node_15 | 20 | n |  | TRUE
8 | bus_MV_118_0_node_8 | 20 | n |  | TRUE
9 | bus_MV_118_0_node_10 | 20 | n |  | TRUE
10 | bus_MV_118_0_node_9 | 20 | n |  | TRUE
11 | bus_MV_118_0_node_159 | 20 | n |  | TRUE
12 | bus_MV_118_0_node_6 | 20 | n |  | TRUE
13 | bus_MV_118_0_node_7 | 20 | n |  | TRUE
14 | bus_MV_118_0_node_96 | 20 | n |  | TRUE
15 | bus_MV_118_0_node_152 | 20 | n |  | TRUE
16 | bus_MV_118_0_node_164 | 20 | n |  | TRUE
17 | bus_MV_118_0_node_66 | 20 | n |  | TRUE
18 | bus_MV_118_0_node_95 | 20 | n |  | TRUE
19 | bus_MV_118_0_node_97 | 20 | n |  | TRUE
20 | bus_MV_118_0_node_98 | 20 | n |  | TRUE
21 | bus_MV_118_0_node_99 | 20 | n |  | TRUE
22 | bus_MV_118_0_node_100 | 20 | n |  | TRUE
23 | bus_MV_118_0_node_160 | 20 | n |  | TRUE
24 | bus_MV_118_0_node_161 | 20 | n |  | TRUE
25 | bus_MV_118_0_node_12 | 20 | n |  | TRUE
26 | bus_MV_118_0_node_14 | 20 | n |  | TRUE
27 | bus_MV_118_0_node_13 | 20 | n |  | TRUE
28 | bus_MV_118_0_node_16 | 20 | n |  | TRUE
29 | bus_MV_118_0_node_33 | 20 | n |  | TRUE
30 | bus_MV_118_0_node_34 | 20 | n |  | TRUE
31 | bus_MV_118_0_node_125 | 20 | n |  | TRUE
32 | bus_MV_118_0_node_128 | 20 | n |  | TRUE
33 | bus_MV_118_0_node_18 | 20 | n |  | TRUE
34 | bus_MV_118_0_node_31 | 20 | n |  | TRUE
35 | bus_MV_118_0_node_20 | 20 | n |  | TRUE
36 | bus_MV_118_0_node_21 | 20 | n |  | TRUE
37 | bus_MV_118_0_node_23 | 20 | n |  | TRUE
38 | bus_MV_118_0_node_22 | 20 | n |  | TRUE
39 | bus_MV_118_0_node_170 | 20 | n |  | TRUE
40 | bus_MV_118_0_node_17 | 20 | n |  | TRUE
41 | bus_MV_118_0_node_19 | 20 | n |  | TRUE
42 | bus_MV_118_0_node_25 | 20 | n |  | TRUE
43 | bus_MV_118_0_node_168 | 20 | n |  | TRUE
44 | bus_MV_118_0_node_28 | 20 | n |  | TRUE
45 | bus_MV_118_0_node_24 | 20 | n |  | TRUE
46 | bus_MV_118_0_node_26 | 20 | n |  | TRUE
47 | bus_MV_118_0_node_27 | 20 | n |  | TRUE
48 | bus_MV_118_0_node_129 | 20 | n |  | TRUE
49 | bus_MV_118_0_node_124 | 20 | n |  | TRUE
50 | bus_MV_118_0_node_123 | 20 | n |  | TRUE
51 | bus_MV_118_0_node_134 | 20 | n |  | TRUE
52 | bus_MV_118_0_node_130 | 20 | n |  | TRUE
53 | bus_MV_118_0_node_135 | 20 | n |  | TRUE
54 | bus_MV_118_0_node_127 | 20 | n |  | TRUE
55 | bus_MV_118_0_node_30 | 20 | n |  | TRUE
56 | bus_MV_118_0_node_32 | 20 | n |  | TRUE
57 | bus_MV_118_0_node_46 | 20 | n |  | TRUE
58 | bus_MV_118_0_node_44 | 20 | n |  | TRUE
59 | bus_MV_118_0_node_45 | 20 | n |  | TRUE
60 | bus_MV_118_0_node_48 | 20 | n |  | TRUE
61 | bus_MV_118_0_node_51 | 20 | n |  | TRUE
62 | bus_MV_118_0_node_126 | 20 | n |  | TRUE
63 | bus_MV_118_0_node_133 | 20 | n |  | TRUE
64 | bus_MV_118_0_node_132 | 20 | n |  | TRUE
65 | bus_MV_118_0_node_136 | 20 | n |  | TRUE
66 | bus_MV_118_0_node_35 | 20 | n |  | TRUE
67 | bus_MV_118_0_node_37 | 20 | n |  | TRUE
68 | bus_MV_118_0_node_38 | 20 | n |  | TRUE
69 | bus_MV_118_0_node_36 | 20 | n |  | TRUE
70 | bus_MV_118_0_node_39 | 20 | n |  | TRUE
71 | bus_MV_118_0_node_40 | 20 | n |  | TRUE
72 | bus_MV_118_0_node_87 | 20 | n |  | TRUE
73 | bus_MV_118_0_node_86 | 20 | n |  | TRUE
74 | bus_MV_118_0_node_56 | 20 | n |  | TRUE
75 | bus_MV_118_0_node_58 | 20 | n |  | TRUE
76 | bus_MV_118_0_node_115 | 20 | n |  | TRUE
77 | bus_MV_118_0_node_167 | 20 | n |  | TRUE
78 | bus_MV_118_0_node_57 | 20 | n |  | TRUE
79 | bus_MV_118_0_node_59 | 20 | n |  | TRUE
80 | bus_MV_118_0_node_112 | 20 | n |  | TRUE
81 | bus_MV_118_0_node_41 | 20 | n |  | TRUE
82 | bus_MV_118_0_node_42 | 20 | n |  | TRUE
83 | bus_MV_118_0_node_43 | 20 | n |  | TRUE
84 | bus_MV_118_0_node_154 | 20 | n |  | TRUE
85 | bus_MV_118_0_node_83 | 20 | n |  | TRUE
86 | bus_MV_118_0_node_84 | 20 | n |  | TRUE
87 | bus_MV_118_0_node_82 | 20 | n |  | TRUE
88 | bus_MV_118_0_node_61 | 20 | n |  | TRUE
89 | bus_MV_118_0_node_153 | 20 | n |  | TRUE
90 | bus_MV_118_0_node_122 | 20 | n |  | TRUE
91 | bus_MV_118_0_node_62 | 20 | n |  | TRUE
92 | bus_MV_118_0_node_63 | 20 | n |  | TRUE
93 | bus_MV_118_0_node_162 | 20 | n |  | TRUE
94 | bus_MV_118_0_node_85 | 20 | n |  | TRUE
95 | bus_MV_118_0_node_52 | 20 | n |  | TRUE
96 | bus_MV_118_0_node_137 | 20 | n |  | TRUE
97 | bus_MV_118_0_node_54 | 20 | n |  | TRUE
98 | bus_MV_118_0_node_50 | 20 | n |  | TRUE
99 | bus_MV_118_0_node_72 | 20 | n |  | TRUE
100 | bus_MV_118_0_node_73 | 20 | n |  | TRUE
101 | bus_MV_118_0_node_71 | 20 | n |  | TRUE
102 | bus_MV_118_0_node_93 | 20 | n |  | TRUE
103 | bus_MV_118_0_node_53 | 20 | n |  | TRUE
104 | bus_MV_118_0_node_55 | 20 | n |  | TRUE
105 | bus_MV_118_0_node_60 | 20 | n |  | TRUE
106 | bus_MV_118_0_node_169 | 20 | n |  | TRUE
107 | bus_MV_118_0_node_67 | 20 | n |  | TRUE
108 | bus_MV_118_0_node_65 | 20 | n |  | TRUE
109 | bus_MV_118_0_node_64 | 20 | n |  | TRUE
110 | bus_MV_118_0_node_68 | 20 | n |  | TRUE
111 | bus_MV_118_0_node_69 | 20 | n |  | TRUE
112 | bus_MV_118_0_node_157 | 20 | n |  | TRUE
113 | bus_MV_118_0_node_108 | 20 | n |  | TRUE
114 | bus_MV_118_0_node_119 | 20 | n |  | TRUE
115 | bus_MV_118_0_node_70 | 20 | n |  | TRUE
116 | bus_MV_118_0_node_156 | 20 | n |  | TRUE
117 | bus_MV_118_0_node_91 | 20 | n |  | TRUE
118 | bus_MV_118_0_node_92 | 20 | n |  | TRUE
119 | bus_MV_118_0_node_155 | 20 | n |  | TRUE
120 | bus_MV_118_0_node_74 | 20 | n |  | TRUE
121 | bus_MV_118_0_node_75 | 20 | n |  | TRUE
122 | bus_MV_118_0_node_77 | 20 | n |  | TRUE
123 | bus_MV_118_0_node_165 | 20 | n |  | TRUE
124 | bus_MV_118_0_node_78 | 20 | n |  | TRUE
125 | bus_MV_118_0_node_120 | 20 | n |  | TRUE
126 | bus_MV_118_0_node_76 | 20 | n |  | TRUE
127 | bus_MV_118_0_node_80 | 20 | n |  | TRUE
128 | bus_MV_118_0_node_166 | 20 | n |  | TRUE
129 | bus_MV_118_0_node_81 | 20 | n |  | TRUE
130 | bus_MV_118_0_node_88 | 20 | n |  | TRUE
131 | bus_MV_118_0_node_89 | 20 | n |  | TRUE
132 | bus_MV_118_0_node_90 | 20 | n |  | TRUE
133 | bus_MV_118_0_node_147 | 20 | n |  | TRUE
134 | bus_MV_118_0_node_148 | 20 | n |  | TRUE
135 | bus_MV_118_0_node_94 | 20 | n |  | TRUE
136 | bus_MV_118_0_node_163 | 20 | n |  | TRUE
137 | bus_MV_118_0_node_110 | 20 | n |  | TRUE
138 | bus_MV_118_0_node_111 | 20 | n |  | TRUE
139 | bus_MV_118_0_node_109 | 20 | n |  | TRUE
140 | bus_MV_118_0_node_106 | 20 | n |  | TRUE
141 | bus_MV_118_0_node_103 | 20 | n |  | TRUE
142 | bus_MV_118_0_node_105 | 20 | n |  | TRUE
143 | bus_MV_118_0_node_104 | 20 | n |  | TRUE
144 | bus_MV_118_0_node_107 | 20 | n |  | TRUE
145 | bus_MV_118_0_node_149 | 20 | n |  | TRUE
146 | bus_MV_118_0_node_145 | 20 | n |  | TRUE
147 | bus_MV_118_0_node_144 | 20 | n |  | TRUE
148 | bus_MV_118_0_node_121 | 20 | n |  | TRUE
149 | bus_MV_118_0_node_116 | 20 | n |  | TRUE
150 | bus_MV_118_0_node_117 | 20 | n |  | TRUE
151 | bus_MV_118_0_node_118 | 20 | n |  | TRUE
152 | bus_MV_118_0_node_138 | 20 | n |  | TRUE
153 | bus_MV_118_0_node_139 | 20 | n |  | TRUE
154 | bus_MV_118_0_node_150 | 20 | n |  | TRUE
155 | bus_MV_118_0_node_140 | 20 | n |  | TRUE
156 | bus_MV_118_0_node_141 | 20 | n |  | TRUE
157 | bus_MV_118_0_node_142 | 20 | n |  | TRUE
158 | bus_MV_118_0_node_143 | 20 | n |  | TRUE
159 | bus_MV_118_0_node_146 | 20 | n |  | TRUE
160 | bus_MV_118_0_node_151 | 20 | n |  | TRUE
161 | bus_HV_118_0_node_32 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_118_0_load_0 | 0 | 0.22542 | 0.10918 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_118_0_load_5 | 4 | 0.20502 | 0.099295 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_118_0_load_131 | 5 | 0.080519 | 0.038997 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_118_0_load_11 | 6 | 0.12405 | 0.06008 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_118_0_load_8 | 8 | 0.17559 | 0.085043 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_118_0_load_159 | 11 | 0.13961 | 0.067616 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_118_0_load_6 | 12 | 0.18741 | 0.090765 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_118_0_load_164 | 16 | 0.10908 | 0.052829 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_118_0_load_95 | 18 | 0.29927 | 0.14494 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_118_0_load_100 | 22 | 0.19687 | 0.09535 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_118_0_load_160 | 23 | 0.59535 | 0.28834 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_118_0_load_161 | 24 | 0.28692 | 0.13896 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_118_0_load_12 | 25 | 0.11115 | 0.05383 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_118_0_load_34 | 30 | 0.11445 | 0.055429 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_118_0_load_128 | 32 | 2.2145 | 1.0725 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_118_0_load_20 | 35 | 0.3306 | 0.16012 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_118_0_load_170 | 39 | 0.28645 | 0.13873 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_118_0_load_17 | 40 | 0.053361 | 0.025844 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_118_0_load_168 | 43 | 0.297 | 0.14384 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_118_0_load_24 | 45 | 0.39835 | 0.19293 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_118_0_load_129 | 48 | 0.24342 | 0.11789 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_118_0_load_124 | 49 | 0.16042 | 0.077694 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_118_0_load_123 | 50 | 0.076205 | 0.036908 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_118_0_load_134 | 51 | 0.071979 | 0.034861 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_118_0_load_130 | 52 | 0.36589 | 0.17721 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_118_0_load_135 | 53 | 0.07196 | 0.034852 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_118_0_load_127 | 54 | 1.7312 | 0.83847 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_118_0_load_30 | 55 | 0.37612 | 0.18216 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_118_0_load_44 | 58 | 0.36962 | 0.17902 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_118_0_load_48 | 60 | 0.33913 | 0.16425 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_118_0_load_51 | 61 | 0.36123 | 0.17495 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_118_0_load_132 | 64 | 0.073272 | 0.035487 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_118_0_load_136 | 65 | 0.37439 | 0.18132 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_118_0_load_35 | 66 | 0.28303 | 0.13708 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_118_0_load_37 | 67 | 0.091804 | 0.044463 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_118_0_load_38 | 68 | 0.84273 | 0.40815 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_118_0_load_86 | 73 | 0.29628 | 0.14349 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_118_0_load_115 | 76 | 0.13901 | 0.067325 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_118_0_load_167 | 77 | 0.24605 | 0.11917 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_118_0_load_112 | 80 | 0.15488 | 0.075014 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_118_0_load_41 | 81 | 0.37318 | 0.18074 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_118_0_load_82 | 87 | 0.41058 | 0.19885 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_118_0_load_61 | 88 | 0.11332 | 0.054883 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_118_0_load_153 | 89 | 0.069285 | 0.033556 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_118_0_load_122 | 90 | 0.1903 | 0.092166 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_118_0_load_62 | 91 | 0.21643 | 0.10482 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_118_0_load_63 | 92 | 0.071796 | 0.034773 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_118_0_load_162 | 93 | 0.24216 | 0.11729 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_118_0_load_137 | 96 | 0.083506 | 0.040444 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_118_0_load_54 | 97 | 0.22239 | 0.10771 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_118_0_load_73 | 100 | 0.22691 | 0.1099 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_118_0_load_71 | 101 | 0.18862 | 0.091352 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_118_0_load_55 | 104 | 0.15238 | 0.073802 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_118_0_load_60 | 105 | 0.22892 | 0.11087 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_118_0_load_169 | 106 | 0.30096 | 0.14576 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_118_0_load_67 | 107 | 0.20477 | 0.099173 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_118_0_load_65 | 108 | 0.195 | 0.094445 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_118_0_load_64 | 109 | 0.13225 | 0.064051 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_118_0_load_157 | 112 | 0.28062 | 0.13591 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_118_0_load_156 | 116 | 0.28667 | 0.13884 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_118_0_load_91 | 117 | 0.29244 | 0.14163 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_118_0_load_155 | 119 | 0.079693 | 0.038597 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_118_0_load_74 | 120 | 0.40812 | 0.19766 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_118_0_load_165 | 123 | 0.23623 | 0.11441 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_118_0_load_80 | 127 | 0.20412 | 0.098858 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_118_0_load_166 | 128 | 0.072869 | 0.035292 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_118_0_load_81 | 129 | 0.17364 | 0.084097 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_118_0_load_88 | 130 | 0.34628 | 0.16771 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_118_0_load_147 | 133 | 0.080754 | 0.039111 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_118_0_load_163 | 136 | 0.39785 | 0.19269 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_118_0_load_109 | 139 | 0.3521 | 0.17053 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_118_0_load_103 | 141 | 0.28905 | 0.13999 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_118_0_load_149 | 145 | 0.088416 | 0.042822 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_118_0_load_145 | 146 | 0.15007 | 0.072682 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_118_0_load_144 | 147 | 0.17063 | 0.082641 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_118_0_load_121 | 148 | 0.33421 | 0.16187 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_118_0_load_116 | 149 | 0.38279 | 0.18539 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_118_0_load_138 | 152 | 0.13441 | 0.065099 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_118_0_load_150 | 154 | 0.070625 | 0.034205 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_118_0_load_142 | 157 | 0.08891 | 0.043061 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_118_0_load_143 | 158 | 0.068589 | 0.033219 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_118_0_load_146 | 159 | 0.083112 | 0.040253 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_118_0_load_151 | 160 | 0.30943 | 0.14986 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_118_0_line_0 |  | 0 | 1 | 0.046089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_118_0_line_1 |  | 0 | 2 | 0.17874 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_118_0_line_2 |  | 1 | 3 | 0.32254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_118_0_line_3 |  | 2 | 4 | 0.072655 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_118_0_line_4 |  | 3 | 8 | 0.056972 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_118_0_line_5 |  | 5 | 6 | 1.3346 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_118_0_line_6 |  | 5 | 7 | 0.0085325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_118_0_line_7 |  | 6 | 9 | 0.14537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_118_0_line_8 |  | 7 | 27 | 0.3387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_118_0_line_9 |  | 8 | 10 | 0.060634 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_118_0_line_10 |  | 9 | 10 | 0.37605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_118_0_line_11 |  | 11 | 12 | 0.87792 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_118_0_line_12 |  | 12 | 13 | 0.054313 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
13 | MV_118_0_line_13 |  | 12 | 14 | 1.0205 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
14 | MV_118_0_line_14 |  | 13 | 15 | 0.87929 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
15 | MV_118_0_line_15 |  | 14 | 18 | 0.000989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_118_0_line_16 |  | 15 | 16 | 0.014293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_118_0_line_17 |  | 15 | 17 | 0.93314 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
18 | MV_118_0_line_18 |  | 17 | 108 | 0.17425 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
19 | MV_118_0_line_19 |  | 18 | 19 | 0.066624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_118_0_line_20 |  | 19 | 20 | 0.18141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_118_0_line_21 |  | 19 | 21 | 0.66208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_118_0_line_22 |  | 20 | 22 | 0.15328 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_118_0_line_23 |  | 20 | 23 | 0.31648 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_118_0_line_24 |  | 21 | 90 | 0.072003 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_118_0_line_25 |  | 23 | 24 | 0.057758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_118_0_line_26 |  | 25 | 26 | 0.059753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_118_0_line_27 |  | 25 | 27 | 0.070846 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_118_0_line_28 |  | 26 | 28 | 0.74284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_118_0_line_29 |  | 28 | 35 | 0.042104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_118_0_line_30 |  | 28 | 36 | 0.063112 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_118_0_line_31 |  | 28 | 37 | 0.17101 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_118_0_line_32 |  | 29 | 30 | 0.11881 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_118_0_line_33 |  | 29 | 31 | 0.14572 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_118_0_line_34 |  | 29 | 32 | 0.65636 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
35 | MV_118_0_line_35 |  | 29 | 33 | 0.99038 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_118_0_line_36 |  | 29 | 34 | 0.98757 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
37 | MV_118_0_line_37 |  | 30 | 46 | 0.055277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_118_0_line_38 |  | 31 | 62 | 0.07947 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_118_0_line_39 |  | 32 | 54 | 0.008969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_118_0_line_40 |  | 33 | 40 | 0.078906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_118_0_line_41 |  | 34 | 56 | 0.98992 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
42 | MV_118_0_line_42 |  | 34 | 55 | 0.15834 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_118_0_line_43 |  | 36 | 38 | 0.3026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_118_0_line_44 |  | 37 | 39 | 0.078905 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_118_0_line_45 |  | 38 | 43 | 0.062478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_118_0_line_46 |  | 41 | 42 | 0.17061 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_118_0_line_47 |  | 41 | 43 | 0.058119 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_118_0_line_48 |  | 42 | 44 | 0.26813 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_118_0_line_49 |  | 42 | 45 | 0.14421 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_118_0_line_50 |  | 44 | 49 | 0.035818 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_118_0_line_51 |  | 44 | 50 | 0.026108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_118_0_line_52 |  | 44 | 51 | 0.052272 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_118_0_line_53 |  | 46 | 47 | 0.2143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_118_0_line_54 |  | 47 | 48 | 0.022986 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_118_0_line_55 |  | 48 | 52 | 0.018971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_118_0_line_56 |  | 51 | 53 | 0.018086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_118_0_line_57 |  | 53 | 65 | 0.065634 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_118_0_line_58 |  | 56 | 57 | 0.30179 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
59 | MV_118_0_line_59 |  | 56 | 58 | 0.016466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_118_0_line_60 |  | 57 | 61 | 0.031581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_118_0_line_61 |  | 57 | 59 | 0.78763 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
62 | MV_118_0_line_62 |  | 59 | 60 | 0.026548 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
63 | MV_118_0_line_63 |  | 60 | 85 | 0.4657 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
64 | MV_118_0_line_64 |  | 61 | 95 | 0.051964 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_118_0_line_65 |  | 62 | 63 | 0.039598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_118_0_line_66 |  | 62 | 64 | 0.012599 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_118_0_line_67 |  | 63 | 65 | 0.000545 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_118_0_line_68 |  | 66 | 67 | 0.041924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_118_0_line_69 |  | 66 | 68 | 0.058883 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_118_0_line_70 |  | 66 | 69 | 0.018565 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_118_0_line_71 |  | 69 | 70 | 0.8222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_118_0_line_72 |  | 69 | 71 | 0.43704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_118_0_line_73 |  | 70 | 72 | 0.60643 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_118_0_line_74 |  | 70 | 73 | 0.13465 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_118_0_line_75 |  | 71 | 74 | 0.73781 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_118_0_line_76 |  | 71 | 75 | 0.16257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_118_0_line_77 |  | 71 | 76 | 0.073283 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_118_0_line_78 |  | 72 | 77 | 0.049356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_118_0_line_79 |  | 74 | 78 | 0.11322 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_118_0_line_80 |  | 74 | 79 | 0.20475 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_118_0_line_81 |  | 75 | 80 | 0.084788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_118_0_line_82 |  | 78 | 104 | 0.057387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_118_0_line_83 |  | 79 | 105 | 0.006448 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_118_0_line_84 |  | 81 | 82 | 0.07303 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_118_0_line_85 |  | 82 | 83 | 0.39413 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
86 | MV_118_0_line_86 |  | 82 | 84 | 1.0604 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
87 | MV_118_0_line_87 |  | 83 | 86 | 0.31159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_118_0_line_88 |  | 83 | 87 | 0.058325 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
89 | MV_118_0_line_89 |  | 84 | 92 | 0.1011 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
90 | MV_118_0_line_90 |  | 85 | 94 | 0.1891 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
91 | MV_118_0_line_91 |  | 85 | 87 | 0.046327 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
92 | MV_118_0_line_92 |  | 86 | 93 | 0.006118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_118_0_line_93 |  | 88 | 89 | 0.97144 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_118_0_line_94 |  | 89 | 91 | 0.1109 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_118_0_line_95 |  | 91 | 109 | 0.038427 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_118_0_line_96 |  | 91 | 92 | 0.088461 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
97 | MV_118_0_line_97 |  | 91 | 108 | 0.056759 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
98 | MV_118_0_line_98 |  | 94 | 117 | 0.023935 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
99 | MV_118_0_line_99 |  | 95 | 103 | 0.20602 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_118_0_line_100 |  | 96 | 97 | 0.24852 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
101 | MV_118_0_line_101 |  | 97 | 103 | 0.007856 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_118_0_line_102 |  | 98 | 99 | 0.10002 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
103 | MV_118_0_line_103 |  | 98 | 100 | 0.017863 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
104 | MV_118_0_line_104 |  | 99 | 101 | 0.019113 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
105 | MV_118_0_line_105 |  | 100 | 102 | 0.28387 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
106 | MV_118_0_line_106 |  | 101 | 115 | 0.11095 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
107 | MV_118_0_line_107 |  | 102 | 119 | 0.030122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_118_0_line_108 |  | 102 | 118 | 0.097723 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
109 | MV_118_0_line_109 |  | 105 | 106 | 0.27449 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_118_0_line_110 |  | 106 | 107 | 0.19081 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_118_0_line_111 |  | 107 | 110 | 0.005767 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_118_0_line_112 |  | 110 | 111 | 0.21846 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_118_0_line_113 |  | 111 | 115 | 0.29901 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
114 | MV_118_0_line_114 |  | 111 | 116 | 0.013495 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
115 | MV_118_0_line_115 |  | 112 | 113 | 0.12035 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_118_0_line_116 |  | 112 | 114 | 0.009168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_118_0_line_117 |  | 113 | 116 | 0.0059612 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
118 | MV_118_0_line_118 |  | 113 | 142 | 0.069988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_118_0_line_119 |  | 114 | 151 | 0.11312 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_118_0_line_120 |  | 117 | 118 | 0.062656 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
121 | MV_118_0_line_121 |  | 120 | 121 | 0.037845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_118_0_line_122 |  | 121 | 122 | 0.15057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_118_0_line_123 |  | 121 | 123 | 0.25358 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
124 | MV_118_0_line_124 |  | 122 | 128 | 0.019932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_118_0_line_125 |  | 122 | 126 | 0.2119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_118_0_line_126 |  | 123 | 124 | 0.53755 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
127 | MV_118_0_line_127 |  | 123 | 125 | 0.009671 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_118_0_line_128 |  | 124 | 129 | 0.019062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_118_0_line_129 |  | 125 | 150 | 0.51383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_118_0_line_130 |  | 126 | 127 | 0.07928 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
131 | MV_118_0_line_131 |  | 130 | 131 | 0.057169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_118_0_line_132 |  | 131 | 132 | 0.27297 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_118_0_line_133 |  | 132 | 133 | 0.024607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_118_0_line_134 |  | 133 | 134 | 0.019907 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_118_0_line_135 |  | 134 | 154 | 0.045253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_118_0_line_136 |  | 134 | 145 | 0.027232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_118_0_line_137 |  | 135 | 136 | 0.021154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_118_0_line_138 |  | 135 | 137 | 0.25676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_118_0_line_139 |  | 137 | 138 | 0.056044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_118_0_line_140 |  | 137 | 139 | 0.070283 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_118_0_line_141 |  | 138 | 148 | 0.032265 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
142 | MV_118_0_line_142 |  | 139 | 140 | 0.005377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_118_0_line_143 |  | 140 | 144 | 0.071384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_118_0_line_144 |  | 140 | 143 | 0.090106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_118_0_line_145 |  | 141 | 142 | 0.054901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_118_0_line_146 |  | 141 | 143 | 0.094412 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
147 | MV_118_0_line_147 |  | 144 | 145 | 0.0036604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_118_0_line_148 |  | 146 | 147 | 0.029425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_118_0_line_149 |  | 147 | 157 | 0.0219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_118_0_line_150 |  | 149 | 150 | 0.005278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_118_0_line_151 |  | 150 | 151 | 0.55892 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_118_0_line_152 |  | 151 | 152 | 0.014145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_118_0_line_153 |  | 152 | 153 | 0.0403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_118_0_line_154 |  | 153 | 155 | 0.007451 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_118_0_line_155 |  | 153 | 156 | 0.057095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_118_0_line_156 |  | 154 | 160 | 0.01299 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_118_0_line_157 |  | 155 | 157 | 0.016737 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_118_0_line_158 |  | 156 | 158 | 0.019436 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_118_0_line_159 |  | 158 | 159 | 0.015463 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_118_0_trafo_32 | 25 MVA 110/20 kV | 161 | 56 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2613963.3732 | 1171501.7957
1 | 2614004.0998 | 1171523.3787
2 | 2613800.8151 | 1171576.1145
3 | 2614224.2417 | 1171670.4237
4 | 2613758.1313 | 1171634.402
5 | 2614707.8042 | 1169955.9532
6 | 2614314.9739 | 1171231.417
7 | 2614700.6843 | 1169951.5447
8 | 2614251.8875 | 1171620.6083
9 | 2614440.9186 | 1171302.3086
10 | 2614284.0804 | 1171569.4031
11 | 2613942.6309 | 1172995.4685
12 | 2614703.9327 | 1172558.245
13 | 2614718.1766 | 1172519.0377
14 | 2615374.5031 | 1173327.5518
15 | 2615421.9744 | 1171991.953
16 | 2615433.5938 | 1172000.3203
17 | 2615985.9362 | 1171495.6939
18 | 2615375.4671 | 1173327.3208
19 | 2615417.9738 | 1173369.5953
20 | 2615324.9918 | 1173480.4587
21 | 2615954.6062 | 1173098.0658
22 | 2615195.7802 | 1173562.9066
23 | 2615551 | 1173702.0055
24 | 2615593.1449 | 1173662.5109
25 | 2614746.3058 | 1169579.8135
26 | 2614794.3612 | 1169574.951
27 | 2614703.8321 | 1169636.5161
28 | 2615105.0912 | 1169283.03
29 | 2615709.0052 | 1169655.3492
30 | 2615615.9036 | 1169729.1556
31 | 2615640.1013 | 1169526.9498
32 | 2615720.4325 | 1170311.6091
33 | 2616289.5706 | 1168852.986
34 | 2616547.5888 | 1170122.3723
35 | 2615145.7937 | 1169294.2266
36 | 2615103.1656 | 1169346.1124
37 | 2615138.8436 | 1169115.3859
38 | 2615300.3749 | 1169448.2498
39 | 2615204.3031 | 1169071.3284
40 | 2616367.4991 | 1168845.7712
41 | 2615399.1639 | 1169496.5589
42 | 2615334.0483 | 1169614.1966
43 | 2615341.07 | 1169494.8433
44 | 2615538.5625 | 1169596.4556
45 | 2615380.7026 | 1169750.6507
46 | 2615575.3693 | 1169766.8475
47 | 2615453.0097 | 1169877.7996
48 | 2615473.6865 | 1169887.8408
49 | 2615566.9517 | 1169576.9182
50 | 2615564.2428 | 1169601.1631
51 | 2615509.5631 | 1169552.9649
52 | 2615490.7512 | 1169896.1279
53 | 2615495.2662 | 1169541.888
54 | 2615711.6798 | 1170313.5668
55 | 2616658.7525 | 1170009.6217
56 | 2617281.998 | 1170406.0988
57 | 2617358.4752 | 1170203.0384
58 | 2617298.0852 | 1170409.3133
59 | 2617584.4429 | 1170633.5887
60 | 2617601.104 | 1170649.601
61 | 2617370.0665 | 1170173.6681
62 | 2615584.7591 | 1169520.5811
63 | 2615553.2163 | 1169509.9388
64 | 2615574.8292 | 1169512.8274
65 | 2615552.7032 | 1169510.1264
66 | 2618915.5045 | 1169953.0412
67 | 2618898.3431 | 1169991.2921
68 | 2618969.2287 | 1169977.1447
69 | 2618923.1038 | 1169936.1033
70 | 2618943.3526 | 1169433.7243
71 | 2618636.4777 | 1170041.1184
72 | 2618727.7435 | 1168988.5813
73 | 2618962.7254 | 1169300.4736
74 | 2618428.6525 | 1169882.5213
75 | 2618621.6819 | 1170142.2237
76 | 2618701.4646 | 1170009.0147
77 | 2618744.3706 | 1168942.2319
78 | 2618317.275 | 1169902.8586
79 | 2618363.302 | 1170076.5641
80 | 2618660.4977 | 1170217.6263
81 | 2617401.6202 | 1171396.0988
82 | 2617341.2875 | 1171354.9485
83 | 2617599.8976 | 1171127.8057
84 | 2616282.8116 | 1171291.1965
85 | 2617701.9728 | 1171104.2484
86 | 2617833.2492 | 1171185.8991
87 | 2617656.5975 | 1171114.1314
88 | 2616677.8977 | 1172285.1017
89 | 2616275.3984 | 1171400.9692
90 | 2615912.8023 | 1173039.3699
91 | 2616167.7464 | 1171374.3149
92 | 2616181.801 | 1171286.977
93 | 2617833.9327 | 1171179.8203
94 | 2617888.1026 | 1171075.3725
95 | 2617399.3016 | 1170130.7085
96 | 2617734.921 | 1170126.7377
97 | 2617538.718 | 1169974.2004
98 | 2618063.9748 | 1170740.9171
99 | 2618134.3773 | 1170669.8816
100 | 2618051.7568 | 1170753.9759
101 | 2618132.8503 | 1170653.6465
102 | 2618041.7345 | 1171037.6671
103 | 2617530.8914 | 1169974.1109
104 | 2618320.0938 | 1169846.472
105 | 2618367.1039 | 1170081.7784
106 | 2618238.8602 | 1170324.4669
107 | 2618357.0324 | 1170474.2793
108 | 2616140.6753 | 1171423.8502
109 | 2616131.4723 | 1171361.6318
110 | 2618358.8441 | 1170479.7542
111 | 2618447.5923 | 1170630.6238
112 | 2618580.0759 | 1170618.6582
113 | 2618462.2873 | 1170643.3752
114 | 2618588.626 | 1170622.0307
115 | 2618239.4557 | 1170622.9084
116 | 2618457.7849 | 1170639.4683
117 | 2617912.0869 | 1171074.3766
118 | 2617974.6693 | 1171071.3503
119 | 2618011.6129 | 1171037.7367
120 | 2619172.0026 | 1170475.6074
121 | 2619197.0028 | 1170447.1393
122 | 2619269.737 | 1170427.3615
123 | 2619116.4198 | 1170206.7059
124 | 2619628.3428 | 1170370.7019
125 | 2619108.3117 | 1170201.3997
126 | 2619421.793 | 1170409.4074
127 | 2619477.853 | 1170353.349
128 | 2619283.9218 | 1170441.4029
129 | 2619641.3873 | 1170384.6292
130 | 2618774.0024 | 1171007.8007
131 | 2618730.8946 | 1171045.3077
132 | 2618512.7701 | 1170986.8372
133 | 2618494.9895 | 1170969.8262
134 | 2618480.6135 | 1170956.0562
135 | 2618173.302 | 1171062.3973
136 | 2618152.1025 | 1171063.2227
137 | 2618385.8912 | 1170974.7536
138 | 2618399.8017 | 1171016.2059
139 | 2618405.0539 | 1170907.1335
140 | 2618408.6843 | 1170903.1759
141 | 2618431.9987 | 1170743.9444
142 | 2618458.3545 | 1170696.012
143 | 2618402.2724 | 1170833.5544
144 | 2618458.3036 | 1170934.6881
145 | 2618460.9464 | 1170937.2207
146 | 2618597.3654 | 1170672.9362
147 | 2618621.1328 | 1170655.5931
148 | 2618394.9003 | 1171048.096
149 | 2618697.3684 | 1170369.6953
150 | 2618702.6335 | 1170369.1558
151 | 2618694.4769 | 1170591.3205
152 | 2618683.9566 | 1170600.776
153 | 2618659.562 | 1170630.6544
154 | 2618510.8991 | 1170922.4785
155 | 2618652.5389 | 1170633.2006
156 | 2618715.9694 | 1170627.2277
157 | 2618638.5215 | 1170642.2819
158 | 2618702.7253 | 1170640.3742
159 | 2618693.0502 | 1170652.2726
160 | 2618518.6608 | 1170912.0619
161 | 2617281.998 | 1170406.0988

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98749 | -0.039434 | 0.22542 | 0.10918
1 | 0.98752 | -0.03967 | 0 | 0
2 | 0.98742 | -0.039916 | 0 | 0
3 | 0.98769 | -0.041232 | 0 | 0
4 | 0.9874 | -0.039738 | 0.20502 | 0.099295
5 | 0.99007 | -0.029603 | 0.080519 | 0.038997
6 | 0.98819 | -0.044541 | 0.12405 | 0.06008
7 | 0.99008 | -0.029673 | 0 | 0
8 | 0.98774 | -0.040875 | 0.17559 | 0.085043
9 | 0.98808 | -0.043674 | 0 | 0
10 | 0.98779 | -0.041281 | 0 | 0
11 | 0.98955 | -0.2997 | 0.13961 | 0.067616
12 | 0.98979 | -0.29815 | 0.18741 | 0.090765
13 | 0.98984 | -0.29752 | 0 | 0
14 | 0.98788 | -0.34667 | 0 | 0
15 | 0.99098 | -0.23312 | 0 | 0
16 | 0.99098 | -0.2331 | 0.10908 | 0.052829
17 | 0.99159 | -0.23013 | 0 | 0
18 | 0.98788 | -0.34665 | 0.29927 | 0.14494
19 | 0.98777 | -0.34572 | 0 | 0
20 | 0.98752 | -0.34336 | 0 | 0
21 | 0.98761 | -0.34458 | 0 | 0
22 | 0.98746 | -0.34373 | 0.19687 | 0.09535
23 | 0.98697 | -0.34686 | 0.59535 | 0.28834
24 | 0.98695 | -0.34666 | 0.28692 | 0.13896
25 | 0.99054 | -0.031459 | 0.11115 | 0.05383
26 | 0.99061 | -0.031998 | 0 | 0
27 | 0.99043 | -0.032376 | 0 | 0
28 | 0.99148 | -0.03824 | 0 | 0
29 | 0.99571 | -0.043111 | 0 | 0
30 | 0.99554 | -0.044235 | 0.11445 | 0.055429
31 | 0.99485 | -0.049565 | 0 | 0
32 | 0.99261 | -0.11887 | 2.2145 | 1.0725
33 | 0.99561 | -0.043963 | 0 | 0
34 | 0.99823 | -0.032408 | 0 | 0
35 | 0.99146 | -0.038072 | 0.3306 | 0.16012
36 | 0.99167 | -0.036749 | 0 | 0
37 | 0.99139 | -0.038845 | 0 | 0
38 | 0.99226 | -0.041292 | 0 | 0
39 | 0.99134 | -0.039124 | 0.28645 | 0.13873
40 | 0.99561 | -0.043917 | 0.053361 | 0.025844
41 | 0.99259 | -0.040584 | 0 | 0
42 | 0.99299 | -0.043679 | 0 | 0
43 | 0.99238 | -0.042212 | 0.297 | 0.14384
44 | 0.99375 | -0.049741 | 0 | 0
45 | 0.99287 | -0.044385 | 0.39835 | 0.19293
46 | 0.9955 | -0.043853 | 0 | 0
47 | 0.99534 | -0.042325 | 0 | 0
48 | 0.99532 | -0.042157 | 0.24342 | 0.11789
49 | 0.99374 | -0.049673 | 0.16042 | 0.077694
50 | 0.99375 | -0.049718 | 0.076205 | 0.036908
51 | 0.994 | -0.047817 | 0.071979 | 0.034861
52 | 0.99531 | -0.042073 | 0.36589 | 0.17721
53 | 0.99406 | -0.048287 | 0.07196 | 0.034852
54 | 0.99259 | -0.11868 | 1.7312 | 0.83847
55 | 0.99812 | -0.033132 | 0.37612 | 0.18216
56 | 1 | 0 | -22.2925 | -10.1998
57 | 0.99911 | -0.016662 | 0 | 0
58 | 0.99999 | 7.2609e-05 | 0.36962 | 0.17902
59 | 0.99688 | -0.057952 | 0 | 0
60 | 0.99681 | -0.05934 | 0.33913 | 0.16425
61 | 0.99908 | -0.016421 | 0.36123 | 0.17495
62 | 0.99454 | -0.047013 | 0 | 0
63 | 0.99439 | -0.045771 | 0 | 0
64 | 0.99454 | -0.047002 | 0.073272 | 0.035487
65 | 0.99439 | -0.045754 | 0.37439 | 0.18132
66 | 0.9836 | -0.24302 | 0.28303 | 0.13708
67 | 0.98359 | -0.24297 | 0.091804 | 0.044463
68 | 0.98353 | -0.24241 | 0.84273 | 0.40815
69 | 0.98364 | -0.24273 | 0 | 0
70 | 0.98307 | -0.23856 | 0 | 0
71 | 0.98463 | -0.25103 | 0 | 0
72 | 0.98288 | -0.23703 | 0 | 0
73 | 0.98299 | -0.23906 | 0.29628 | 0.14349
74 | 0.98658 | -0.26666 | 0 | 0
75 | 0.9846 | -0.25076 | 0 | 0
76 | 0.98462 | -0.25091 | 0.13901 | 0.067325
77 | 0.98287 | -0.23689 | 0.24605 | 0.11917
78 | 0.98654 | -0.26689 | 0 | 0
79 | 0.98745 | -0.25972 | 0 | 0
80 | 0.98458 | -0.25061 | 0.15488 | 0.075014
81 | 0.99342 | -0.16906 | 0.37318 | 0.18074
82 | 0.99348 | -0.16873 | 0 | 0
83 | 0.99375 | -0.16351 | 0 | 0
84 | 0.992 | -0.22015 | 0 | 0
85 | 0.99388 | -0.15931 | 0 | 0
86 | 0.99365 | -0.16267 | 0 | 0
87 | 0.99385 | -0.16005 | 0.41058 | 0.19885
88 | 0.99149 | -0.23091 | 0.11332 | 0.054883
89 | 0.99171 | -0.22951 | 0.069285 | 0.033556
90 | 0.98759 | -0.34441 | 0.1903 | 0.092166
91 | 0.99174 | -0.22925 | 0.21643 | 0.10482
92 | 0.99186 | -0.22506 | 0.071796 | 0.034773
93 | 0.99365 | -0.16265 | 0.24216 | 0.11729
94 | 0.99352 | -0.166 | 0 | 0
95 | 0.99905 | -0.016637 | 0 | 0
96 | 0.99892 | -0.016146 | 0.083506 | 0.040444
97 | 0.99897 | -0.015892 | 0.22239 | 0.10771
98 | 0.9918 | -0.22038 | 0 | 0
99 | 0.99162 | -0.22368 | 0 | 0
100 | 0.99184 | -0.21979 | 0.22691 | 0.1099
101 | 0.99159 | -0.22432 | 0.18862 | 0.091352
102 | 0.99303 | -0.17922 | 0 | 0
103 | 0.99897 | -0.015921 | 0 | 0
104 | 0.98653 | -0.26679 | 0.15238 | 0.073802
105 | 0.98747 | -0.25986 | 0.22892 | 0.11087
106 | 0.98876 | -0.24978 | 0.30096 | 0.14576
107 | 0.98978 | -0.24208 | 0.20477 | 0.099173
108 | 0.9917 | -0.22948 | 0.195 | 0.094445
109 | 0.99174 | -0.22919 | 0.13225 | 0.064051
110 | 0.9898 | -0.24226 | 0 | 0
111 | 0.99062 | -0.24905 | 0 | 0
112 | 0.99002 | -0.25361 | 0.28062 | 0.13591
113 | 0.99059 | -0.24949 | 0 | 0
114 | 0.98999 | -0.2534 | 0 | 0
115 | 0.99115 | -0.23942 | 0 | 0
116 | 0.99061 | -0.24932 | 0.28667 | 0.13884
117 | 0.99348 | -0.16685 | 0.29244 | 0.14163
118 | 0.99321 | -0.17588 | 0 | 0
119 | 0.99302 | -0.17919 | 0.079693 | 0.038597
120 | 0.98753 | -0.23746 | 0.40812 | 0.19766
121 | 0.98755 | -0.23764 | 0 | 0
122 | 0.98749 | -0.2372 | 0 | 0
123 | 0.98789 | -0.23527 | 0.23623 | 0.11441
124 | 0.9877 | -0.23646 | 0 | 0
125 | 0.9879 | -0.23539 | 0 | 0
126 | 0.98744 | -0.23671 | 0 | 0
127 | 0.98741 | -0.23691 | 0.20412 | 0.098858
128 | 0.98749 | -0.23719 | 0.072869 | 0.035292
129 | 0.9877 | -0.23642 | 0.17364 | 0.084097
130 | 0.98936 | -0.24416 | 0.34628 | 0.16771
131 | 0.98938 | -0.2444 | 0 | 0
132 | 0.9895 | -0.24547 | 0 | 0
133 | 0.98951 | -0.24557 | 0.080754 | 0.039111
134 | 0.98952 | -0.24566 | 0 | 0
135 | 0.9894 | -0.2461 | 0 | 0
136 | 0.98939 | -0.246 | 0.39785 | 0.19269
137 | 0.98953 | -0.24729 | 0 | 0
138 | 0.98951 | -0.24706 | 0 | 0
139 | 0.98963 | -0.2466 | 0.3521 | 0.17053
140 | 0.98964 | -0.24667 | 0 | 0
141 | 0.99023 | -0.24623 | 0.28905 | 0.13999
142 | 0.99039 | -0.24767 | 0 | 0
143 | 0.98987 | -0.24872 | 0 | 0
144 | 0.98956 | -0.24595 | 0 | 0
145 | 0.98955 | -0.24591 | 0.088416 | 0.042822
146 | 0.98961 | -0.25007 | 0.15007 | 0.072682
147 | 0.98962 | -0.25013 | 0.17063 | 0.082641
148 | 0.98949 | -0.24719 | 0.33421 | 0.16187
149 | 0.98862 | -0.24168 | 0.38279 | 0.18539
150 | 0.98862 | -0.2417 | 0 | 0
151 | 0.98968 | -0.25071 | 0 | 0
152 | 0.98967 | -0.25059 | 0.13441 | 0.065099
153 | 0.98964 | -0.25033 | 0 | 0
154 | 0.9895 | -0.24545 | 0.070625 | 0.034205
155 | 0.98963 | -0.25029 | 0 | 0
156 | 0.98963 | -0.25023 | 0 | 0
157 | 0.98963 | -0.25021 | 0.08891 | 0.043061
158 | 0.98962 | -0.25019 | 0.068589 | 0.033219
159 | 0.98962 | -0.25018 | 0.083112 | 0.040253
160 | 0.9895 | -0.2454 | 0.30943 | 0.14986
161 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.43046 | -0.20658 | 0.43047 | 0.20551 | 1.1975e-05 | -0.0010695 | 0.013958 | 0.013944 | 0.013958 | 0.98749 | -0.039434 | 0.98752 | -0.03967 | 6.3445
1 | 0.20504 | 0.097406 | -0.20502 | -0.097605 | 1.4029e-05 | -0.00019927 | 0.0066359 | 0.0066385 | 0.0066385 | 0.98749 | -0.039434 | 0.98742 | -0.039916 | 3.1612
2 | -0.43047 | -0.20551 | 0.43056 | 0.19803 | 8.3163e-05 | -0.0074866 | 0.013944 | 0.013851 | 0.013944 | 0.98752 | -0.03967 | 0.98769 | -0.041232 | 6.3383
3 | 0.20502 | 0.097605 | -0.20502 | -0.099295 | 4.2882e-06 | -0.00169 | 0.0066385 | 0.0066599 | 0.0066599 | 0.98742 | -0.039916 | 0.9874 | -0.039738 | 3.0272
4 | -0.43056 | -0.19803 | 0.43058 | 0.19797 | 1.9474e-05 | -5.4156e-05 | 0.013851 | 0.01385 | 0.013851 | 0.98769 | -0.041232 | 0.98774 | -0.040875 | 6.5958
5 | 0.73181 | 0.32888 | -0.73051 | -0.32962 | 0.0013023 | -0.00074309 | 0.023393 | 0.023412 | 0.023412 | 0.99007 | -0.029603 | 0.98819 | -0.044541 | 11.1485
6 | -0.81233 | -0.36787 | 0.81234 | 0.36768 | 7.6999e-06 | -0.00019741 | 0.026001 | 0.025998 | 0.026001 | 0.99007 | -0.029603 | 0.99008 | -0.029673 | 11.8185
7 | 0.60646 | 0.26954 | -0.60639 | -0.27291 | 7.3095e-05 | -0.0033673 | 0.019387 | 0.019428 | 0.019428 | 0.98819 | -0.044541 | 0.98808 | -0.043674 | 8.8307
8 | -0.81234 | -0.36768 | 0.81264 | 0.35984 | 0.00030451 | -0.0078397 | 0.025998 | 0.025904 | 0.025998 | 0.99008 | -0.029673 | 0.99043 | -0.032376 | 11.8174
9 | -0.60617 | -0.28302 | 0.6062 | 0.28161 | 3.0915e-05 | -0.0014033 | 0.019552 | 0.019534 | 0.019552 | 0.98774 | -0.040875 | 0.98779 | -0.041281 | 8.887
10 | 0.60639 | 0.27291 | -0.6062 | -0.28161 | 0.00019051 | -0.0087067 | 0.019428 | 0.019534 | 0.019534 | 0.98808 | -0.043674 | 0.98779 | -0.041281 | 8.8791
11 | -0.13961 | -0.067616 | 0.13964 | 0.06661 | 3.194e-05 | -0.0010065 | 0.0045253 | 0.0045123 | 0.0045253 | 0.98955 | -0.2997 | 0.98979 | -0.29815 | 2.1549
12 | -1.8991 | -0.89428 | 1.8992 | 0.89253 | 9.8291e-05 | -0.0017541 | 0.061223 | 0.0612 | 0.061223 | 0.98979 | -0.29815 | 0.98984 | -0.29752 | 16.9123
13 | 1.5721 | 0.73691 | -1.5697 | -0.73541 | 0.002403 | 0.0014946 | 0.050638 | 0.050653 | 0.050653 | 0.98979 | -0.29815 | 0.98788 | -0.34667 | 14.4723
14 | -1.8992 | -0.89253 | 1.9004 | 0.8945 | 0.0011754 | 0.0019686 | 0.0612 | 0.061185 | 0.0612 | 0.98984 | -0.29752 | 0.99098 | -0.23312 | 9.4884
15 | 1.5697 | 0.73541 | -1.5697 | -0.73544 | 3.3877e-06 | -2.204e-05 | 0.050653 | 0.050653 | 0.050653 | 0.98788 | -0.34667 | 0.98788 | -0.34665 | 23.0243
16 | 0.10908 | 0.052494 | -0.10908 | -0.052829 | 2.3755e-07 | -0.00033506 | 0.0035263 | 0.0035305 | 0.0035305 | 0.99098 | -0.23312 | 0.99098 | -0.2331 | 1.6048
17 | -2.0095 | -0.94699 | 2.0107 | 0.89005 | 0.0011943 | -0.056941 | 0.064711 | 0.064014 | 0.064711 | 0.99098 | -0.23312 | 0.99159 | -0.23013 | 10.1428
18 | -2.0107 | -0.89005 | 2.0109 | 0.87941 | 0.00022021 | -0.010643 | 0.064014 | 0.063888 | 0.064014 | 0.99159 | -0.23013 | 0.9917 | -0.22948 | 10.0335
19 | 1.2704 | 0.59049 | -1.2703 | -0.592 | 0.00014913 | -0.001508 | 0.040938 | 0.040957 | 0.040957 | 0.98788 | -0.34665 | 0.98777 | -0.34572 | 18.6167
20 | 1.0799 | 0.51692 | -1.0796 | -0.52106 | 0.00029695 | -0.0041368 | 0.03499 | 0.035043 | 0.035043 | 0.98777 | -0.34572 | 0.98752 | -0.34336 | 15.9288
21 | 0.19033 | 0.075079 | -0.1903 | -0.09049 | 3.2523e-05 | -0.015411 | 0.0059796 | 0.0061593 | 0.0061593 | 0.98777 | -0.34572 | 0.98761 | -0.34458 | 2.7997
22 | 0.19688 | 0.095179 | -0.19687 | -0.09535 | 1.1164e-05 | -0.00017144 | 0.0063926 | 0.0063949 | 0.0063949 | 0.98752 | -0.34336 | 0.98746 | -0.34373 | 3.0452
23 | 0.88274 | 0.42588 | -0.88227 | -0.42596 | 0.00046295 | -7.8269e-05 | 0.028651 | 0.028655 | 0.028655 | 0.98752 | -0.34336 | 0.98697 | -0.34686 | 13.6454
24 | 0.1903 | 0.09049 | -0.1903 | -0.092166 | 3.6592e-06 | -0.0016757 | 0.0061593 | 0.0061805 | 0.0061805 | 0.98761 | -0.34458 | 0.98759 | -0.34441 | 2.8093
25 | 0.28692 | 0.13762 | -0.28692 | -0.13896 | 6.6919e-06 | -0.0013413 | 0.0093075 | 0.0093245 | 0.0093245 | 0.98697 | -0.34686 | 0.98695 | -0.34666 | 4.2384
26 | -0.92387 | -0.41364 | 0.92394 | 0.41226 | 6.9381e-05 | -0.0013793 | 0.0295 | 0.029483 | 0.0295 | 0.99054 | -0.031459 | 0.99061 | -0.031998 | 13.4091
27 | 0.81273 | 0.35981 | -0.81264 | -0.35984 | 8.4696e-05 | -2.9924e-05 | 0.025903 | 0.025904 | 0.025904 | 0.99054 | -0.031459 | 0.99043 | -0.032376 | 12.3352
28 | -0.92394 | -0.41226 | 0.9248 | 0.39509 | 0.00085607 | -0.017166 | 0.029483 | 0.02928 | 0.029483 | 0.99061 | -0.031998 | 0.99148 | -0.03824 | 13.4015
29 | 0.33061 | 0.15913 | -0.3306 | -0.16012 | 6.4223e-06 | -0.0009863 | 0.010683 | 0.010695 | 0.010695 | 0.99148 | -0.03824 | 0.99146 | -0.038072 | 4.8616
30 | -1.5419 | -0.69269 | 1.5422 | 0.69278 | 0.00027236 | 9.6516e-05 | 0.049215 | 0.049214 | 0.049215 | 0.99148 | -0.03824 | 0.99167 | -0.036749 | 23.4358
31 | 0.28648 | 0.13846 | -0.28646 | -0.13865 | 2.6157e-05 | -0.00018428 | 0.0092643 | 0.0092668 | 0.0092668 | 0.99148 | -0.03824 | 0.99139 | -0.038845 | 4.4128
32 | 0.72402 | 0.34313 | -0.7239 | -0.3432 | 0.00011423 | -6.9049e-05 | 0.023229 | 0.02323 | 0.02323 | 0.99571 | -0.043111 | 0.99554 | -0.044235 | 11.0621
33 | 3.0755 | 1.4105 | -3.073 | -1.4091 | 0.0024983 | 0.0013926 | 0.098095 | 0.098097 | 0.098097 | 0.99571 | -0.043111 | 0.99485 | -0.049565 | 46.7128
34 | 3.9556 | 1.9212 | -3.9458 | -1.9108 | 0.0097944 | 0.010387 | 0.12749 | 0.1275 | 0.1275 | 0.99571 | -0.043111 | 0.99261 | -0.11887 | 36.4288
35 | 0.053366 | 0.022808 | -0.053361 | -0.023976 | 5.0356e-06 | -0.0011689 | 0.0016826 | 0.0016962 | 0.0016962 | 0.99571 | -0.043111 | 0.99561 | -0.043963 | 0.80772
36 | -7.8085 | -3.6977 | 7.8276 | 3.6467 | 0.019088 | -0.050927 | 0.25048 | 0.24972 | 0.25048 | 0.99571 | -0.043111 | 0.99823 | -0.032408 | 39.2605
37 | 0.60946 | 0.28778 | -0.60943 | -0.28907 | 2.8209e-05 | -0.0012996 | 0.019543 | 0.01956 | 0.01956 | 0.99554 | -0.044235 | 0.9955 | -0.043853 | 8.8907
38 | 3.073 | 1.4091 | -3.072 | -1.4107 | 0.0010212 | -0.0015744 | 0.098097 | 0.09812 | 0.09812 | 0.99485 | -0.049565 | 0.99454 | -0.047013 | 44.5998
39 | 1.7313 | 0.83827 | -1.7312 | -0.83847 | 3.7471e-05 | -0.00019987 | 0.055941 | 0.055943 | 0.055943 | 0.99261 | -0.11887 | 0.99259 | -0.11868 | 25.4288
40 | 0.053361 | 0.023976 | -0.053361 | -0.025844 | 3.0712e-07 | -0.0018674 | 0.0016962 | 0.0017191 | 0.0017191 | 0.99561 | -0.043963 | 0.99561 | -0.043917 | 0.78141
41 | -8.2037 | -3.8287 | 8.2161 | 3.7646 | 0.012373 | -0.064141 | 0.26181 | 0.26089 | 0.26181 | 0.99823 | -0.032408 | 1 | 0 | 31.0933
42 | 0.37616 | 0.182 | -0.37612 | -0.18216 | 4.1205e-05 | -0.00016252 | 0.012084 | 0.012087 | 0.012087 | 0.99823 | -0.032408 | 0.99812 | -0.033132 | 5.7556
43 | -1.5422 | -0.69278 | 1.5431 | 0.68596 | 0.00097676 | -0.0068196 | 0.049214 | 0.04913 | 0.049214 | 0.99167 | -0.036749 | 0.99226 | -0.041292 | 22.3701
44 | 0.28646 | 0.13865 | -0.28645 | -0.13873 | 1.2074e-05 | -8.5014e-05 | 0.0092668 | 0.009268 | 0.009268 | 0.99139 | -0.038845 | 0.99134 | -0.039124 | 4.4133
45 | -1.5431 | -0.68596 | 1.5433 | 0.68455 | 0.00020126 | -0.0014092 | 0.04913 | 0.049113 | 0.04913 | 0.99226 | -0.041292 | 0.99238 | -0.042212 | 22.3318
46 | -1.8407 | -0.82855 | 1.8415 | 0.82477 | 0.00078434 | -0.0037823 | 0.058707 | 0.058659 | 0.058707 | 0.99259 | -0.040584 | 0.99299 | -0.043679 | 26.6848
47 | 1.8407 | 0.82855 | -1.8403 | -0.8284 | 0.00035689 | 0.0001552 | 0.058707 | 0.058707 | 0.058707 | 0.99259 | -0.040584 | 0.99238 | -0.042212 | 27.9559
48 | -2.2399 | -1.0176 | 2.2417 | 1.0118 | 0.0018291 | -0.0057748 | 0.071521 | 0.071445 | 0.071521 | 0.99299 | -0.043679 | 0.99375 | -0.049741 | 32.5094
49 | 0.39839 | 0.19279 | -0.39835 | -0.19293 | 4.2543e-05 | -0.00014309 | 0.012867 | 0.012869 | 0.012869 | 0.99299 | -0.043679 | 0.99287 | -0.044385 | 6.1279
50 | 0.16042 | 0.07685 | -0.16042 | -0.077694 | 1.2793e-06 | -0.00084416 | 0.0051672 | 0.0051778 | 0.0051778 | 0.99375 | -0.049741 | 0.99374 | -0.049673 | 2.3536
51 | 0.076205 | 0.036292 | -0.076205 | -0.036908 | 2.102e-07 | -0.00061553 | 0.0024519 | 0.0024596 | 0.0024596 | 0.99375 | -0.049741 | 0.99375 | -0.049718 | 1.118
52 | -2.4783 | -1.1249 | 2.4789 | 1.1252 | 0.00058216 | 0.00030301 | 0.079062 | 0.079062 | 0.079062 | 0.99375 | -0.049741 | 0.994 | -0.047817 | 37.6487
53 | 0.60943 | 0.28907 | -0.60932 | -0.29411 | 0.00010981 | -0.0050374 | 0.01956 | 0.019623 | 0.019623 | 0.9955 | -0.043853 | 0.99534 | -0.042325 | 8.9195
54 | 0.60932 | 0.29411 | -0.60931 | -0.29465 | 1.182e-05 | -0.00054019 | 0.019623 | 0.01963 | 0.01963 | 0.99534 | -0.042325 | 0.99532 | -0.042157 | 8.9227
55 | 0.36589 | 0.17676 | -0.36589 | -0.17721 | 3.5194e-06 | -0.00044766 | 0.011786 | 0.011791 | 0.011791 | 0.99532 | -0.042157 | 0.99531 | -0.042073 | 5.3596
56 | -2.5509 | -1.1601 | 2.551 | 1.1597 | 0.00015991 | -0.00037925 | 0.081384 | 0.081378 | 0.081384 | 0.994 | -0.047817 | 0.99406 | -0.048287 | 36.9925
57 | -2.623 | -1.1946 | 2.6238 | 1.195 | 0.00081923 | 0.00043569 | 0.0837 | 0.083699 | 0.0837 | 0.99406 | -0.048287 | 0.99439 | -0.045754 | 39.857
58 | 13.6928 | 6.2461 | -13.6824 | -6.2595 | 0.010431 | -0.013461 | 0.43446 | 0.43474 | 0.43474 | 1 | 0 | 0.99911 | -0.016662 | 51.6314
59 | 0.36963 | 0.17862 | -0.36962 | -0.17902 | 3.0885e-06 | -0.00039222 | 0.011851 | 0.011856 | 0.011856 | 1 | 0 | 0.99999 | 7.2609e-05 | 5.389
60 | 0.66718 | 0.31692 | -0.66716 | -0.31766 | 1.9211e-05 | -0.00074696 | 0.021341 | 0.021351 | 0.021351 | 0.99911 | -0.016662 | 0.99908 | -0.016421 | 9.7049
61 | 13.0152 | 5.9426 | -12.9905 | -5.9799 | 0.024675 | -0.037283 | 0.4134 | 0.41412 | 0.41412 | 0.99911 | -0.016662 | 0.99688 | -0.057952 | 49.1829
62 | 12.9905 | 5.9799 | -12.9897 | -5.9812 | 0.00083322 | -0.0012507 | 0.41412 | 0.41414 | 0.41414 | 0.99688 | -0.057952 | 0.99681 | -0.05934 | 49.1858
63 | 12.6506 | 5.8169 | -12.6236 | -5.779 | 0.026988 | 0.03788 | 0.40323 | 0.40325 | 0.40325 | 0.99681 | -0.05934 | 0.99388 | -0.15931 | 49.1767
64 | 0.30593 | 0.14271 | -0.30592 | -0.14277 | 8.8094e-06 | -5.64e-05 | 0.0097542 | 0.0097549 | 0.0097549 | 0.99908 | -0.016421 | 0.99905 | -0.016637 | 4.6452
65 | 2.9987 | 1.3755 | -2.9982 | -1.3763 | 0.00048482 | -0.0007912 | 0.095761 | 0.095772 | 0.095772 | 0.99454 | -0.047013 | 0.99439 | -0.045771 | 43.5327
66 | 0.073273 | 0.03519 | -0.073272 | -0.035487 | 9.3771e-08 | -0.0002975 | 0.0023594 | 0.0023631 | 0.0023631 | 0.99454 | -0.047013 | 0.99454 | -0.047002 | 1.0741
67 | 2.9982 | 1.3763 | -2.9982 | -1.3763 | 6.6734e-06 | -1.0887e-05 | 0.095772 | 0.095772 | 0.095772 | 0.99439 | -0.045771 | 0.99439 | -0.045754 | 43.5327
68 | 0.091805 | 0.043494 | -0.091804 | -0.044463 | 4.9955e-07 | -0.00096827 | 0.0029815 | 0.0029937 | 0.0029937 | 0.9836 | -0.24302 | 0.98359 | -0.24297 | 1.3608
69 | 0.84279 | 0.40681 | -0.84273 | -0.40815 | 5.9338e-05 | -0.0013425 | 0.027466 | 0.027483 | 0.027483 | 0.9836 | -0.24302 | 0.98353 | -0.24241 | 12.4923
70 | -1.2176 | -0.58738 | 1.2177 | 0.58739 | 5.207e-05 | 1.1172e-05 | 0.039677 | 0.039676 | 0.039677 | 0.9836 | -0.24302 | 0.98364 | -0.24273 | 18.8936
71 | 0.54274 | 0.22852 | -0.54241 | -0.24741 | 0.00033203 | -0.018885 | 0.017282 | 0.017506 | 0.017506 | 0.98364 | -0.24273 | 0.98307 | -0.23856 | 7.9573
72 | -1.7604 | -0.81592 | 1.7623 | 0.80637 | 0.0018877 | -0.0095465 | 0.056943 | 0.056819 | 0.056943 | 0.98364 | -0.24273 | 0.98463 | -0.25103 | 25.8832
73 | 0.24611 | 0.10406 | -0.24606 | -0.11803 | 5.0891e-05 | -0.013975 | 0.0078462 | 0.0080152 | 0.0080152 | 0.98307 | -0.23856 | 0.98288 | -0.23703 | 3.6433
74 | 0.2963 | 0.14335 | -0.29628 | -0.14349 | 2.2417e-05 | -0.0001413 | 0.0096655 | 0.0096675 | 0.0096675 | 0.98307 | -0.23856 | 0.98299 | -0.23906 | 4.6035
75 | -2.0562 | -0.94129 | 2.0605 | 0.92546 | 0.0043161 | -0.015832 | 0.0663 | 0.066093 | 0.0663 | 0.98463 | -0.25103 | 0.98658 | -0.26666 | 30.1365
76 | 0.15489 | 0.069291 | -0.15489 | -0.073052 | 5.4205e-06 | -0.0037613 | 0.0049748 | 0.0050209 | 0.0050209 | 0.98463 | -0.25103 | 0.9846 | -0.25076 | 2.2822
77 | 0.13901 | 0.065629 | -0.13901 | -0.067325 | 1.9966e-06 | -0.0016957 | 0.0045069 | 0.0045283 | 0.0045283 | 0.98463 | -0.25103 | 0.98462 | -0.25091 | 2.0583
78 | 0.24606 | 0.11803 | -0.24605 | -0.11917 | 4.2407e-06 | -0.0011372 | 0.0080152 | 0.0080297 | 0.0080297 | 0.98288 | -0.23703 | 0.98287 | -0.23689 | 3.6499
79 | 0.15239 | 0.07234 | -0.15238 | -0.072469 | 4.9161e-06 | -0.00012847 | 0.0049358 | 0.0049375 | 0.0049375 | 0.98658 | -0.26666 | 0.98654 | -0.26689 | 2.3512
80 | -2.2129 | -0.9978 | 2.2147 | 0.99871 | 0.0018404 | 0.00091462 | 0.071028 | 0.071025 | 0.071028 | 0.98658 | -0.26666 | 0.98745 | -0.25972 | 33.8229
81 | 0.15489 | 0.073052 | -0.15488 | -0.075014 | 2.8676e-06 | -0.0019617 | 0.0050209 | 0.0050457 | 0.0050457 | 0.9846 | -0.25076 | 0.98458 | -0.25061 | 2.2935
82 | 0.15238 | 0.072469 | -0.15238 | -0.073802 | 1.8741e-06 | -0.001333 | 0.0049375 | 0.0049544 | 0.0049544 | 0.98654 | -0.26689 | 0.98653 | -0.26679 | 2.252
83 | -2.2147 | -0.99871 | 2.2148 | 0.99857 | 4.3423e-05 | -0.00013724 | 0.071025 | 0.071023 | 0.071025 | 0.98745 | -0.25972 | 0.98747 | -0.25986 | 32.2842
84 | -0.37318 | -0.18074 | 0.3732 | 0.18067 | 1.8889e-05 | -7.4214e-05 | 0.012049 | 0.012048 | 0.012049 | 0.99342 | -0.16906 | 0.99348 | -0.16873 | 5.7376
85 | -3.1859 | -1.443 | 3.1866 | 1.4139 | 0.00074228 | -0.029048 | 0.10162 | 0.10127 | 0.10162 | 0.99348 | -0.16873 | 0.99375 | -0.16351 | 12.0694
86 | 2.8127 | 1.2623 | -2.8096 | -1.2606 | 0.0030338 | 0.0016871 | 0.089581 | 0.089613 | 0.089613 | 0.99348 | -0.16873 | 0.992 | -0.22015 | 10.9284
87 | 0.24219 | 0.1098 | -0.24216 | -0.11714 | 2.5109e-05 | -0.0073387 | 0.0077247 | 0.0078152 | 0.0078152 | 0.99375 | -0.16351 | 0.99365 | -0.16267 | 3.5524
88 | -3.4288 | -1.5237 | 3.429 | 1.5239 | 0.00024695 | 0.00020842 | 0.109 | 0.10899 | 0.109 | 0.99375 | -0.16351 | 0.99385 | -0.16005 | 13.2921
89 | 2.8096 | 1.2606 | -2.8093 | -1.2604 | 0.00028936 | 0.00016143 | 0.089613 | 0.089616 | 0.089616 | 0.992 | -0.22015 | 0.99186 | -0.22506 | 10.9288
90 | 8.7838 | 4.0596 | -8.7811 | -4.0714 | 0.0027353 | -0.011756 | 0.28106 | 0.28123 | 0.28123 | 0.99388 | -0.15931 | 0.99352 | -0.166 | 33.4005
91 | 3.8397 | 1.7194 | -3.8396 | -1.7228 | 0.00012663 | -0.00338 | 0.1222 | 0.12224 | 0.12224 | 0.99388 | -0.15931 | 0.99385 | -0.16005 | 14.5176
92 | 0.24216 | 0.11714 | -0.24216 | -0.11729 | 4.9898e-07 | -0.00014408 | 0.0078152 | 0.0078171 | 0.0078171 | 0.99365 | -0.16267 | 0.99365 | -0.16265 | 3.5532
93 | -0.11332 | -0.054883 | 0.11334 | 0.053757 | 2.3169e-05 | -0.0011258 | 0.0036659 | 0.0036516 | 0.0036659 | 0.99149 | -0.23091 | 0.99171 | -0.22951 | 1.7457
94 | -0.18263 | -0.087313 | 0.18263 | 0.087188 | 6.8587e-06 | -0.00012592 | 0.0058924 | 0.0058908 | 0.0058924 | 0.99171 | -0.22951 | 0.99174 | -0.22925 | 2.8059
95 | 0.13225 | 0.063149 | -0.13225 | -0.064051 | 9.3604e-07 | -0.00090213 | 0.0042659 | 0.0042772 | 0.0042772 | 0.99174 | -0.22925 | 0.99174 | -0.22919 | 1.9442
96 | -2.7373 | -1.2256 | 2.7375 | 1.2257 | 0.00024026 | 0.0001226 | 0.087298 | 0.087295 | 0.087298 | 0.99174 | -0.22925 | 0.99186 | -0.22506 | 10.6461
97 | 2.206 | 0.97039 | -2.2059 | -0.97385 | 8.6356e-05 | -0.0034589 | 0.070149 | 0.07019 | 0.07019 | 0.99174 | -0.22925 | 0.9917 | -0.22948 | 11.0016
98 | 8.7811 | 4.0714 | -8.7808 | -4.0729 | 0.00034646 | -0.001487 | 0.28123 | 0.28125 | 0.28125 | 0.99352 | -0.166 | 0.99348 | -0.16685 | 33.4031
99 | 0.30592 | 0.14277 | -0.3059 | -0.14767 | 2.6334e-05 | -0.0049014 | 0.0097549 | 0.0098158 | 0.0098158 | 0.99905 | -0.016637 | 0.99897 | -0.015921 | 4.4617
100 | -0.083506 | -0.040444 | 0.083509 | 0.04015 | 3.1791e-06 | -0.00029407 | 0.0026813 | 0.0026776 | 0.0026813 | 0.99892 | -0.016146 | 0.99897 | -0.015892 | 1.2768
101 | -0.3059 | -0.14786 | 0.3059 | 0.14767 | 1.0107e-06 | -0.00018688 | 0.0098181 | 0.0098158 | 0.0098181 | 0.99897 | -0.015892 | 0.99897 | -0.015921 | 4.4628
102 | 8.1712 | 3.7786 | -8.1699 | -3.785 | 0.0012572 | -0.0063619 | 0.26203 | 0.26212 | 0.26212 | 0.9918 | -0.22038 | 0.99162 | -0.22368 | 31.1308
103 | -8.1712 | -3.7786 | 8.1714 | 3.7775 | 0.00022443 | -0.0011365 | 0.26203 | 0.26201 | 0.26203 | 0.9918 | -0.22038 | 0.99184 | -0.21979 | 31.1198
104 | 8.1699 | 3.785 | -8.1697 | -3.7862 | 0.00024033 | -0.0012153 | 0.26212 | 0.26214 | 0.26214 | 0.99162 | -0.22368 | 0.99159 | -0.22432 | 31.1328
105 | -8.3983 | -3.8874 | 8.4057 | 3.8973 | 0.0073396 | 0.0099026 | 0.26935 | 0.26934 | 0.26935 | 0.99184 | -0.21979 | 0.99303 | -0.17922 | 32.8475
106 | 7.9811 | 3.6948 | -7.9785 | -3.6914 | 0.0025922 | 0.0034708 | 0.25604 | 0.25604 | 0.25604 | 0.99159 | -0.22432 | 0.99115 | -0.23942 | 31.2246
107 | 0.079693 | 0.037888 | -0.079693 | -0.038597 | 2.6552e-07 | -0.00070912 | 0.0025652 | 0.0025741 | 0.0025741 | 0.99303 | -0.17922 | 0.99302 | -0.17919 | 1.17
108 | -8.4853 | -3.9352 | 8.4867 | 3.929 | 0.0013217 | -0.0061506 | 0.27191 | 0.27182 | 0.27191 | 0.99303 | -0.17922 | 0.99321 | -0.17588 | 32.2929
109 | -2.4437 | -1.1094 | 2.4467 | 1.111 | 0.0030102 | 0.0015656 | 0.078457 | 0.078453 | 0.078457 | 0.98747 | -0.25986 | 0.98876 | -0.24978 | 37.3604
110 | -2.7477 | -1.2568 | 2.7503 | 1.2582 | 0.0026454 | 0.0014341 | 0.088213 | 0.088211 | 0.088213 | 0.98876 | -0.24978 | 0.98978 | -0.24208 | 42.0063
111 | -2.9551 | -1.3574 | 2.9552 | 1.3573 | 6.9255e-05 | -0.00011435 | 0.094845 | 0.094843 | 0.094845 | 0.98978 | -0.24208 | 0.9898 | -0.24226 | 43.1113
112 | -2.9552 | -1.3573 | 2.9578 | 1.3529 | 0.0026217 | -0.0043367 | 0.094843 | 0.094781 | 0.094843 | 0.9898 | -0.24226 | 0.99062 | -0.24905 | 43.1105
113 | -7.9749 | -3.7105 | 7.9785 | 3.6914 | 0.0035911 | -0.019134 | 0.25632 | 0.25604 | 0.25632 | 0.99062 | -0.24905 | 0.99115 | -0.23942 | 30.4414
114 | 5.0171 | 2.3576 | -5.017 | -2.3585 | 6.4448e-05 | -0.00095264 | 0.16154 | 0.16155 | 0.16155 | 0.99062 | -0.24905 | 0.99061 | -0.24932 | 19.1866
115 | -2.4578 | -1.1451 | 2.4592 | 1.1458 | 0.0013404 | 0.00069866 | 0.079062 | 0.079061 | 0.079062 | 0.99002 | -0.25361 | 0.99059 | -0.24949 | 37.6488
116 | 2.1772 | 1.0092 | -2.1771 | -1.0094 | 5.9927e-05 | -0.00019677 | 0.069972 | 0.069975 | 0.069975 | 0.99002 | -0.25361 | 0.98999 | -0.2534 | 31.8066
117 | -4.7303 | -2.2198 | 4.7304 | 2.2197 | 6.676e-05 | -0.00015217 | 0.15227 | 0.15227 | 0.15227 | 0.99059 | -0.24949 | 0.99061 | -0.24932 | 42.0642
118 | 2.2711 | 1.0741 | -2.2706 | -1.0755 | 0.00050095 | -0.0014908 | 0.073212 | 0.073233 | 0.073233 | 0.99059 | -0.24949 | 0.99039 | -0.24767 | 33.2876
119 | 2.1771 | 1.0094 | -2.1764 | -1.0118 | 0.00073978 | -0.0024268 | 0.069975 | 0.070007 | 0.070007 | 0.98999 | -0.2534 | 0.98968 | -0.25071 | 31.8214
120 | 8.4883 | 3.9312 | -8.4867 | -3.929 | 0.0016498 | 0.0022286 | 0.27181 | 0.27182 | 0.27182 | 0.99348 | -0.16685 | 0.99321 | -0.17588 | 33.1483
121 | -0.40812 | -0.19766 | 0.40813 | 0.19678 | 8.8703e-06 | -0.00087858 | 0.013256 | 0.013245 | 0.013256 | 0.98753 | -0.23746 | 0.98755 | -0.23764 | 6.0254
122 | 0.27702 | 0.12517 | -0.277 | -0.12867 | 1.5948e-05 | -0.0035012 | 0.0088859 | 0.0089286 | 0.0089286 | 0.98755 | -0.23764 | 0.98749 | -0.2372 | 4.0584
123 | -0.68515 | -0.32195 | 0.68537 | 0.32179 | 0.0002212 | -0.00015678 | 0.022129 | 0.022125 | 0.022129 | 0.98755 | -0.23764 | 0.98789 | -0.23527 | 10.5376
124 | 0.072869 | 0.034828 | -0.072869 | -0.035292 | 1.487e-07 | -0.00046403 | 0.002361 | 0.0023669 | 0.0023669 | 0.98749 | -0.2372 | 0.98749 | -0.23719 | 1.0759
125 | 0.20413 | 0.09384 | -0.20412 | -0.098769 | 1.2316e-05 | -0.0049296 | 0.0065678 | 0.0066293 | 0.0066293 | 0.98749 | -0.2372 | 0.98744 | -0.23671 | 3.0133
126 | 0.17367 | 0.083046 | -0.17364 | -0.083653 | 3.0349e-05 | -0.00060715 | 0.0056253 | 0.0056332 | 0.0056332 | 0.98789 | -0.23527 | 0.9877 | -0.23646 | 2.6825
127 | -1.0953 | -0.51925 | 1.0953 | 0.51903 | 1.6196e-05 | -0.00022054 | 0.03542 | 0.035417 | 0.03542 | 0.98789 | -0.23527 | 0.9879 | -0.23539 | 16.1
128 | 0.17364 | 0.083653 | -0.17364 | -0.084097 | 8.0834e-07 | -0.00044376 | 0.0056332 | 0.0056388 | 0.0056388 | 0.9877 | -0.23646 | 0.9877 | -0.23642 | 2.5631
129 | -1.0953 | -0.51903 | 1.0961 | 0.5073 | 0.00085684 | -0.011728 | 0.035417 | 0.035269 | 0.035417 | 0.9879 | -0.23539 | 0.98862 | -0.2417 | 16.0988
130 | 0.20412 | 0.098769 | -0.20412 | -0.098858 | 6.2089e-06 | -8.839e-05 | 0.0066293 | 0.0066305 | 0.0066305 | 0.98744 | -0.23671 | 0.98741 | -0.23691 | 3.1574
131 | -0.34628 | -0.16771 | 0.34629 | 0.16638 | 9.6046e-06 | -0.0013333 | 0.011227 | 0.01121 | 0.011227 | 0.98936 | -0.24416 | 0.98938 | -0.2444 | 5.103
132 | -0.34629 | -0.16638 | 0.34634 | 0.16001 | 4.5465e-05 | -0.0063671 | 0.01121 | 0.01113 | 0.01121 | 0.98938 | -0.2444 | 0.9895 | -0.24547 | 5.0953
133 | -0.34634 | -0.16001 | 0.34634 | 0.15944 | 4.0671e-06 | -0.00057406 | 0.01113 | 0.011123 | 0.01113 | 0.9895 | -0.24547 | 0.98951 | -0.24557 | 5.0592
134 | -0.4271 | -0.19855 | 0.4271 | 0.19809 | 5.0154e-06 | -0.0004639 | 0.01374 | 0.013735 | 0.01374 | 0.98951 | -0.24557 | 0.98952 | -0.24566 | 6.2457
135 | 0.38006 | 0.18271 | -0.38005 | -0.18376 | 9.1532e-06 | -0.0010552 | 0.012302 | 0.012316 | 0.012316 | 0.98952 | -0.24566 | 0.9895 | -0.24545 | 5.598
136 | -0.80716 | -0.38079 | 0.80719 | 0.38016 | 2.4637e-05 | -0.00062935 | 0.026036 | 0.026028 | 0.026036 | 0.98952 | -0.24566 | 0.98955 | -0.24591 | 11.8347
137 | 0.39786 | 0.19219 | -0.39785 | -0.19269 | 4.6957e-06 | -0.00049303 | 0.012892 | 0.012898 | 0.012898 | 0.9894 | -0.2461 | 0.98939 | -0.246 | 5.8627
138 | -0.39786 | -0.19219 | 0.39791 | 0.18621 | 5.6633e-05 | -0.0059851 | 0.012892 | 0.012816 | 0.012892 | 0.9894 | -0.2461 | 0.98953 | -0.24729 | 5.8598
139 | 0.33423 | 0.16053 | -0.33422 | -0.16183 | 8.7674e-06 | -0.0013076 | 0.010817 | 0.010833 | 0.010833 | 0.98953 | -0.24729 | 0.98951 | -0.24706 | 4.9242
140 | -0.73214 | -0.34674 | 0.73221 | 0.3467 | 6.9936e-05 | -3.8359e-05 | 0.023633 | 0.023632 | 0.023633 | 0.98953 | -0.24729 | 0.98963 | -0.2466 | 11.2538
141 | 0.33422 | 0.16183 | -0.33421 | -0.16187 | 6.7469e-06 | -3.3487e-05 | 0.010833 | 0.010834 | 0.010834 | 0.98951 | -0.24706 | 0.98949 | -0.24719 | 5.159
142 | -1.0843 | -0.51723 | 1.0843 | 0.5171 | 8.8149e-06 | -0.00012312 | 0.035043 | 0.035042 | 0.035043 | 0.98963 | -0.2466 | 0.98964 | -0.24667 | 15.9288
143 | 0.89569 | 0.42126 | -0.89561 | -0.4229 | 7.9498e-05 | -0.0016455 | 0.028872 | 0.028893 | 0.028893 | 0.98964 | -0.24667 | 0.98956 | -0.24595 | 13.1332
144 | -1.98 | -0.93836 | 1.9805 | 0.9364 | 0.00049119 | -0.0019618 | 0.063914 | 0.063888 | 0.063914 | 0.98964 | -0.24667 | 0.98987 | -0.24872 | 29.0518
145 | -2.2702 | -1.0767 | 2.2706 | 1.0755 | 0.00039316 | -0.0011689 | 0.073249 | 0.073233 | 0.073249 | 0.99023 | -0.24623 | 0.99039 | -0.24767 | 33.2949
146 | 1.9812 | 0.93672 | -1.9805 | -0.9364 | 0.00068657 | 0.00031957 | 0.063886 | 0.063888 | 0.063888 | 0.99023 | -0.24623 | 0.98987 | -0.24872 | 30.4227
147 | 0.89561 | 0.4229 | -0.8956 | -0.42299 | 4.0796e-06 | -8.437e-05 | 0.028893 | 0.028894 | 0.028894 | 0.98956 | -0.24595 | 0.98955 | -0.24591 | 13.1337
148 | -0.15007 | -0.072682 | 0.15007 | 0.071994 | 9.2771e-07 | -0.00068776 | 0.004864 | 0.0048553 | 0.004864 | 0.98961 | -0.25007 | 0.98962 | -0.25013 | 2.2109
149 | -0.3207 | -0.15464 | 0.32071 | 0.15412 | 3.1516e-06 | -0.00051116 | 0.010386 | 0.010379 | 0.010386 | 0.98962 | -0.25013 | 0.98963 | -0.25021 | 4.7208
150 | -0.38279 | -0.18539 | 0.38279 | 0.18527 | 1.0867e-06 | -0.00012284 | 0.012419 | 0.012418 | 0.012419 | 0.98862 | -0.24168 | 0.98862 | -0.2417 | 5.6452
151 | -1.4789 | -0.69258 | 1.4806 | 0.68002 | 0.0016909 | -0.012555 | 0.047685 | 0.047525 | 0.047685 | 0.98862 | -0.2417 | 0.98968 | -0.25071 | 21.6751
152 | 0.69577 | 0.33178 | -0.69576 | -0.33211 | 9.5478e-06 | -0.00032796 | 0.022484 | 0.022488 | 0.022488 | 0.98968 | -0.25071 | 0.98967 | -0.25059 | 10.2218
153 | 0.56134 | 0.26701 | -0.56132 | -0.26794 | 1.7699e-05 | -0.00093715 | 0.018132 | 0.018143 | 0.018143 | 0.98967 | -0.25059 | 0.98964 | -0.25033 | 8.247
154 | 0.40962 | 0.19662 | -0.40962 | -0.19679 | 1.7476e-06 | -0.00017371 | 0.013254 | 0.013256 | 0.013256 | 0.98964 | -0.25033 | 0.98963 | -0.25029 | 6.0254
155 | 0.1517 | 0.071322 | -0.1517 | -0.072656 | 1.8287e-06 | -0.0013345 | 0.0048898 | 0.0049065 | 0.0049065 | 0.98964 | -0.25033 | 0.98963 | -0.25023 | 2.2302
156 | 0.30943 | 0.14956 | -0.30943 | -0.14986 | 1.744e-06 | -0.00030316 | 0.010026 | 0.01003 | 0.01003 | 0.9895 | -0.24545 | 0.9895 | -0.2454 | 4.5592
157 | 0.40962 | 0.19679 | -0.40962 | -0.19718 | 3.9278e-06 | -0.00039021 | 0.013256 | 0.013261 | 0.013261 | 0.98963 | -0.25029 | 0.98963 | -0.25021 | 6.0277
158 | 0.1517 | 0.072656 | -0.1517 | -0.073111 | 6.2537e-07 | -0.00045428 | 0.0049065 | 0.0049123 | 0.0049123 | 0.98963 | -0.25023 | 0.98962 | -0.25019 | 2.2328
159 | 0.083112 | 0.039891 | -0.083112 | -0.040253 | 1.4954e-07 | -0.00036152 | 0.0026892 | 0.0026938 | 0.0026938 | 0.98962 | -0.25019 | 0.98962 | -0.25018 | 1.2244

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 22.2925 | 10.1998

## res_load
| p_mw | q_mvar
0 | 0.22542 | 0.10918
1 | 0.20502 | 0.099295
2 | 0.080519 | 0.038997
3 | 0.12405 | 0.06008
4 | 0.17559 | 0.085043
5 | 0.13961 | 0.067616
6 | 0.18741 | 0.090765
7 | 0.10908 | 0.052829
8 | 0.29927 | 0.14494
9 | 0.19687 | 0.09535
10 | 0.59535 | 0.28834
11 | 0.28692 | 0.13896
12 | 0.11115 | 0.05383
13 | 0.11445 | 0.055429
14 | 2.2145 | 1.0725
15 | 0.3306 | 0.16012
16 | 0.28645 | 0.13873
17 | 0.053361 | 0.025844
18 | 0.297 | 0.14384
19 | 0.39835 | 0.19293
20 | 0.24342 | 0.11789
21 | 0.16042 | 0.077694
22 | 0.076205 | 0.036908
23 | 0.071979 | 0.034861
24 | 0.36589 | 0.17721
25 | 0.07196 | 0.034852
26 | 1.7312 | 0.83847
27 | 0.37612 | 0.18216
28 | 0.36962 | 0.17902
29 | 0.33913 | 0.16425
30 | 0.36123 | 0.17495
31 | 0.073272 | 0.035487
32 | 0.37439 | 0.18132
33 | 0.28303 | 0.13708
34 | 0.091804 | 0.044463
35 | 0.84273 | 0.40815
36 | 0.29628 | 0.14349
37 | 0.13901 | 0.067325
38 | 0.24605 | 0.11917
39 | 0.15488 | 0.075014
40 | 0.37318 | 0.18074
41 | 0.41058 | 0.19885
42 | 0.11332 | 0.054883
43 | 0.069285 | 0.033556
44 | 0.1903 | 0.092166
45 | 0.21643 | 0.10482
46 | 0.071796 | 0.034773
47 | 0.24216 | 0.11729
48 | 0.083506 | 0.040444
49 | 0.22239 | 0.10771
50 | 0.22691 | 0.1099
51 | 0.18862 | 0.091352
52 | 0.15238 | 0.073802
53 | 0.22892 | 0.11087
54 | 0.30096 | 0.14576
55 | 0.20477 | 0.099173
56 | 0.195 | 0.094445
57 | 0.13225 | 0.064051
58 | 0.28062 | 0.13591
59 | 0.28667 | 0.13884
60 | 0.29244 | 0.14163
61 | 0.079693 | 0.038597
62 | 0.40812 | 0.19766
63 | 0.23623 | 0.11441
64 | 0.20412 | 0.098858
65 | 0.072869 | 0.035292
66 | 0.17364 | 0.084097
67 | 0.34628 | 0.16771
68 | 0.080754 | 0.039111
69 | 0.39785 | 0.19269
70 | 0.3521 | 0.17053
71 | 0.28905 | 0.13999
72 | 0.088416 | 0.042822
73 | 0.15007 | 0.072682
74 | 0.17063 | 0.082641
75 | 0.33421 | 0.16187
76 | 0.38279 | 0.18539
77 | 0.13441 | 0.065099
78 | 0.070625 | 0.034205
79 | 0.08891 | 0.043061
80 | 0.068589 | 0.033219
81 | 0.083112 | 0.040253
82 | 0.30943 | 0.14986

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1