## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_133_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_133_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_133_0_node_231 | 20 | n |  | TRUE
3 | bus_MV_133_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_133_0_node_160 | 20 | n |  | TRUE
5 | bus_MV_133_0_node_230 | 20 | n |  | TRUE
6 | bus_MV_133_0_node_229 | 20 | n |  | TRUE
7 | bus_MV_133_0_node_240 | 20 | n |  | TRUE
8 | bus_MV_133_0_node_173 | 20 | n |  | TRUE
9 | bus_MV_133_0_node_3 | 20 | n |  | TRUE
10 | bus_MV_133_0_node_4 | 20 | n |  | TRUE
11 | bus_MV_133_0_node_5 | 20 | n |  | TRUE
12 | bus_MV_133_0_node_6 | 20 | n |  | TRUE
13 | bus_MV_133_0_node_8 | 20 | n |  | TRUE
14 | bus_MV_133_0_node_11 | 20 | n |  | TRUE
15 | bus_MV_133_0_node_12 | 20 | n |  | TRUE
16 | bus_MV_133_0_node_13 | 20 | n |  | TRUE
17 | bus_MV_133_0_node_14 | 20 | n |  | TRUE
18 | bus_MV_133_0_node_10 | 20 | n |  | TRUE
19 | bus_MV_133_0_node_7 | 20 | n |  | TRUE
20 | bus_MV_133_0_node_9 | 20 | n |  | TRUE
21 | bus_MV_133_0_node_133 | 20 | n |  | TRUE
22 | bus_MV_133_0_node_134 | 20 | n |  | TRUE
23 | bus_MV_133_0_node_135 | 20 | n |  | TRUE
24 | bus_MV_133_0_node_121 | 20 | n |  | TRUE
25 | bus_MV_133_0_node_33 | 20 | n |  | TRUE
26 | bus_MV_133_0_node_75 | 20 | n |  | TRUE
27 | bus_MV_133_0_node_132 | 20 | n |  | TRUE
28 | bus_MV_133_0_node_212 | 20 | n |  | TRUE
29 | bus_MV_133_0_node_213 | 20 | n |  | TRUE
30 | bus_MV_133_0_node_74 | 20 | n |  | TRUE
31 | bus_MV_133_0_node_16 | 20 | n |  | TRUE
32 | bus_MV_133_0_node_15 | 20 | n |  | TRUE
33 | bus_MV_133_0_node_112 | 20 | n |  | TRUE
34 | bus_MV_133_0_node_235 | 20 | n |  | TRUE
35 | bus_MV_133_0_node_110 | 20 | n |  | TRUE
36 | bus_MV_133_0_node_111 | 20 | n |  | TRUE
37 | bus_MV_133_0_node_151 | 20 | n |  | TRUE
38 | bus_MV_133_0_node_17 | 20 | n |  | TRUE
39 | bus_MV_133_0_node_18 | 20 | n |  | TRUE
40 | bus_MV_133_0_node_19 | 20 | n |  | TRUE
41 | bus_MV_133_0_node_20 | 20 | n |  | TRUE
42 | bus_MV_133_0_node_63 | 20 | n |  | TRUE
43 | bus_MV_133_0_node_148 | 20 | n |  | TRUE
44 | bus_MV_133_0_node_149 | 20 | n |  | TRUE
45 | bus_MV_133_0_node_246 | 20 | n |  | TRUE
46 | bus_MV_133_0_node_103 | 20 | n |  | TRUE
47 | bus_MV_133_0_node_61 | 20 | n |  | TRUE
48 | bus_MV_133_0_node_104 | 20 | n |  | TRUE
49 | bus_MV_133_0_node_105 | 20 | n |  | TRUE
50 | bus_MV_133_0_node_106 | 20 | n |  | TRUE
51 | bus_MV_133_0_node_21 | 20 | n |  | TRUE
52 | bus_MV_133_0_node_241 | 20 | n |  | TRUE
53 | bus_MV_133_0_node_22 | 20 | n |  | TRUE
54 | bus_MV_133_0_node_242 | 20 | n |  | TRUE
55 | bus_MV_133_0_node_23 | 20 | n |  | TRUE
56 | bus_MV_133_0_node_99 | 20 | n |  | TRUE
57 | bus_MV_133_0_node_243 | 20 | n |  | TRUE
58 | bus_MV_133_0_node_152 | 20 | n |  | TRUE
59 | bus_MV_133_0_node_68 | 20 | n |  | TRUE
60 | bus_MV_133_0_node_69 | 20 | n |  | TRUE
61 | bus_MV_133_0_node_70 | 20 | n |  | TRUE
62 | bus_MV_133_0_node_71 | 20 | n |  | TRUE
63 | bus_MV_133_0_node_217 | 20 | n |  | TRUE
64 | bus_MV_133_0_node_97 | 20 | n |  | TRUE
65 | bus_MV_133_0_node_245 | 20 | n |  | TRUE
66 | bus_MV_133_0_node_72 | 20 | n |  | TRUE
67 | bus_MV_133_0_node_236 | 20 | n |  | TRUE
68 | bus_MV_133_0_node_94 | 20 | n |  | TRUE
69 | bus_MV_133_0_node_237 | 20 | n |  | TRUE
70 | bus_MV_133_0_node_238 | 20 | n |  | TRUE
71 | bus_MV_133_0_node_244 | 20 | n |  | TRUE
72 | bus_MV_133_0_node_107 | 20 | n |  | TRUE
73 | bus_MV_133_0_node_38 | 20 | n |  | TRUE
74 | bus_MV_133_0_node_36 | 20 | n |  | TRUE
75 | bus_MV_133_0_node_64 | 20 | n |  | TRUE
76 | bus_MV_133_0_node_65 | 20 | n |  | TRUE
77 | bus_MV_133_0_node_73 | 20 | n |  | TRUE
78 | bus_MV_133_0_node_249 | 20 | n |  | TRUE
79 | bus_MV_133_0_node_117 | 20 | n |  | TRUE
80 | bus_MV_133_0_node_40 | 20 | n |  | TRUE
81 | bus_MV_133_0_node_60 | 20 | n |  | TRUE
82 | bus_MV_133_0_node_98 | 20 | n |  | TRUE
83 | bus_MV_133_0_node_86 | 20 | n |  | TRUE
84 | bus_MV_133_0_node_24 | 20 | n |  | TRUE
85 | bus_MV_133_0_node_25 | 20 | n |  | TRUE
86 | bus_MV_133_0_node_26 | 20 | n |  | TRUE
87 | bus_MV_133_0_node_32 | 20 | n |  | TRUE
88 | bus_MV_133_0_node_27 | 20 | n |  | TRUE
89 | bus_MV_133_0_node_29 | 20 | n |  | TRUE
90 | bus_MV_133_0_node_31 | 20 | n |  | TRUE
91 | bus_MV_133_0_node_215 | 20 | n |  | TRUE
92 | bus_MV_133_0_node_30 | 20 | n |  | TRUE
93 | bus_MV_133_0_node_256 | 20 | n |  | TRUE
94 | bus_MV_133_0_node_47 | 20 | n |  | TRUE
95 | bus_MV_133_0_node_216 | 20 | n |  | TRUE
96 | bus_MV_133_0_node_248 | 20 | n |  | TRUE
97 | bus_MV_133_0_node_138 | 20 | n |  | TRUE
98 | bus_MV_133_0_node_48 | 20 | n |  | TRUE
99 | bus_MV_133_0_node_37 | 20 | n |  | TRUE
100 | bus_MV_133_0_node_35 | 20 | n |  | TRUE
101 | bus_MV_133_0_node_137 | 20 | n |  | TRUE
102 | bus_MV_133_0_node_34 | 20 | n |  | TRUE
103 | bus_MV_133_0_node_58 | 20 | n |  | TRUE
104 | bus_MV_133_0_node_76 | 20 | n |  | TRUE
105 | bus_MV_133_0_node_54 | 20 | n |  | TRUE
106 | bus_MV_133_0_node_41 | 20 | n |  | TRUE
107 | bus_MV_133_0_node_42 | 20 | n |  | TRUE
108 | bus_MV_133_0_node_43 | 20 | n |  | TRUE
109 | bus_MV_133_0_node_44 | 20 | n |  | TRUE
110 | bus_MV_133_0_node_45 | 20 | n |  | TRUE
111 | bus_MV_133_0_node_46 | 20 | n |  | TRUE
112 | bus_MV_133_0_node_247 | 20 | n |  | TRUE
113 | bus_MV_133_0_node_55 | 20 | n |  | TRUE
114 | bus_MV_133_0_node_120 | 20 | n |  | TRUE
115 | bus_MV_133_0_node_147 | 20 | n |  | TRUE
116 | bus_MV_133_0_node_67 | 20 | n |  | TRUE
117 | bus_MV_133_0_node_53 | 20 | n |  | TRUE
118 | bus_MV_133_0_node_66 | 20 | n |  | TRUE
119 | bus_MV_133_0_node_118 | 20 | n |  | TRUE
120 | bus_MV_133_0_node_56 | 20 | n |  | TRUE
121 | bus_MV_133_0_node_169 | 20 | n |  | TRUE
122 | bus_MV_133_0_node_49 | 20 | n |  | TRUE
123 | bus_MV_133_0_node_50 | 20 | n |  | TRUE
124 | bus_MV_133_0_node_51 | 20 | n |  | TRUE
125 | bus_MV_133_0_node_59 | 20 | n |  | TRUE
126 | bus_MV_133_0_node_82 | 20 | n |  | TRUE
127 | bus_MV_133_0_node_254 | 20 | n |  | TRUE
128 | bus_MV_133_0_node_255 | 20 | n |  | TRUE
129 | bus_MV_133_0_node_150 | 20 | n |  | TRUE
130 | bus_MV_133_0_node_77 | 20 | n |  | TRUE
131 | bus_MV_133_0_node_90 | 20 | n |  | TRUE
132 | bus_MV_133_0_node_91 | 20 | n |  | TRUE
133 | bus_MV_133_0_node_78 | 20 | n |  | TRUE
134 | bus_MV_133_0_node_79 | 20 | n |  | TRUE
135 | bus_MV_133_0_node_80 | 20 | n |  | TRUE
136 | bus_MV_133_0_node_113 | 20 | n |  | TRUE
137 | bus_MV_133_0_node_115 | 20 | n |  | TRUE
138 | bus_MV_133_0_node_119 | 20 | n |  | TRUE
139 | bus_MV_133_0_node_114 | 20 | n |  | TRUE
140 | bus_MV_133_0_node_136 | 20 | n |  | TRUE
141 | bus_MV_133_0_node_83 | 20 | n |  | TRUE
142 | bus_MV_133_0_node_84 | 20 | n |  | TRUE
143 | bus_MV_133_0_node_87 | 20 | n |  | TRUE
144 | bus_MV_133_0_node_122 | 20 | n |  | TRUE
145 | bus_MV_133_0_node_102 | 20 | n |  | TRUE
146 | bus_MV_133_0_node_101 | 20 | n |  | TRUE
147 | bus_MV_133_0_node_85 | 20 | n |  | TRUE
148 | bus_MV_133_0_node_88 | 20 | n |  | TRUE
149 | bus_MV_133_0_node_214 | 20 | n |  | TRUE
150 | bus_MV_133_0_node_89 | 20 | n |  | TRUE
151 | bus_MV_133_0_node_123 | 20 | n |  | TRUE
152 | bus_MV_133_0_node_93 | 20 | n |  | TRUE
153 | bus_MV_133_0_node_92 | 20 | n |  | TRUE
154 | bus_MV_133_0_node_139 | 20 | n |  | TRUE
155 | bus_MV_133_0_node_234 | 20 | n |  | TRUE
156 | bus_MV_133_0_node_116 | 20 | n |  | TRUE
157 | bus_MV_133_0_node_95 | 20 | n |  | TRUE
158 | bus_MV_133_0_node_100 | 20 | n |  | TRUE
159 | bus_MV_133_0_node_108 | 20 | n |  | TRUE
160 | bus_MV_133_0_node_109 | 20 | n |  | TRUE
161 | bus_MV_133_0_node_153 | 20 | n |  | TRUE
162 | bus_MV_133_0_node_154 | 20 | n |  | TRUE
163 | bus_MV_133_0_node_170 | 20 | n |  | TRUE
164 | bus_MV_133_0_node_155 | 20 | n |  | TRUE
165 | bus_MV_133_0_node_171 | 20 | n |  | TRUE
166 | bus_MV_133_0_node_157 | 20 | n |  | TRUE
167 | bus_MV_133_0_node_232 | 20 | n |  | TRUE
168 | bus_MV_133_0_node_156 | 20 | n |  | TRUE
169 | bus_MV_133_0_node_172 | 20 | n |  | TRUE
170 | bus_MV_133_0_node_158 | 20 | n |  | TRUE
171 | bus_MV_133_0_node_159 | 20 | n |  | TRUE
172 | bus_MV_133_0_node_163 | 20 | n |  | TRUE
173 | bus_MV_133_0_node_164 | 20 | n |  | TRUE
174 | bus_MV_133_0_node_161 | 20 | n |  | TRUE
175 | bus_MV_133_0_node_250 | 20 | n |  | TRUE
176 | bus_MV_133_0_node_162 | 20 | n |  | TRUE
177 | bus_MV_133_0_node_165 | 20 | n |  | TRUE
178 | bus_MV_133_0_node_253 | 20 | n |  | TRUE
179 | bus_MV_133_0_node_167 | 20 | n |  | TRUE
180 | bus_MV_133_0_node_166 | 20 | n |  | TRUE
181 | bus_MV_133_0_node_218 | 20 | n |  | TRUE
182 | bus_MV_133_0_node_168 | 20 | n |  | TRUE
183 | bus_HV_133_0_node_147 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_133_0_load_0 | 0 | 0.12683 | 0.061427 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_133_0_load_231 | 2 | 0.097374 | 0.04716 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_133_0_load_229 | 6 | 0.15747 | 0.076265 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_133_0_load_240 | 7 | 0.10436 | 0.050544 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_133_0_load_3 | 9 | 0.16034 | 0.077656 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_133_0_load_13 | 16 | 0.1257 | 0.060879 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_133_0_load_133 | 21 | 0.13392 | 0.064862 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_133_0_load_134 | 22 | 0.12586 | 0.060958 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_133_0_load_135 | 23 | 0.079522 | 0.038514 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_133_0_load_121 | 24 | 0.15032 | 0.072805 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_133_0_load_33 | 25 | 0.10618 | 0.051425 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_133_0_load_132 | 27 | 0.094372 | 0.045707 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_133_0_load_212 | 28 | 0.12204 | 0.059108 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_133_0_load_74 | 30 | 0.086651 | 0.041967 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_133_0_load_235 | 34 | 0.1037 | 0.050223 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_133_0_load_151 | 37 | 0.13287 | 0.064354 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_133_0_load_17 | 38 | 0.15406 | 0.074615 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_133_0_load_148 | 43 | 0.084312 | 0.040834 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_133_0_load_149 | 44 | 0.15483 | 0.074989 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_133_0_load_246 | 45 | 0.15204 | 0.073636 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_133_0_load_103 | 46 | 0.10348 | 0.050118 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_133_0_load_241 | 52 | 0.16306 | 0.078974 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_133_0_load_242 | 54 | 0.081076 | 0.039267 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_133_0_load_243 | 57 | 0.056246 | 0.027241 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_133_0_load_152 | 58 | 0.14067 | 0.068128 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_133_0_load_69 | 60 | 0.16161 | 0.078271 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_133_0_load_217 | 63 | 0.11804 | 0.057167 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_133_0_load_245 | 65 | 0.1094 | 0.052983 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_133_0_load_236 | 67 | 0.15472 | 0.074937 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_133_0_load_94 | 68 | 0.094831 | 0.045929 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_133_0_load_244 | 71 | 0.14906 | 0.072193 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_133_0_load_107 | 72 | 0.12981 | 0.06287 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_133_0_load_64 | 75 | 0.14495 | 0.070201 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_133_0_load_73 | 77 | 0.099924 | 0.048396 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_133_0_load_249 | 78 | 0.11211 | 0.054299 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_133_0_load_117 | 79 | 0.11313 | 0.054792 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_133_0_load_60 | 81 | 0.092668 | 0.044881 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_133_0_load_98 | 82 | 0.16162 | 0.078274 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_133_0_load_24 | 84 | 0.14888 | 0.072107 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_133_0_load_26 | 86 | 0.11378 | 0.055105 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_133_0_load_32 | 87 | 0.093193 | 0.045135 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_133_0_load_215 | 91 | 0.20616 | 0.099846 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_133_0_load_256 | 93 | 0.11187 | 0.054182 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_133_0_load_47 | 94 | 0.14193 | 0.068742 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_133_0_load_216 | 95 | 0.10781 | 0.052214 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_133_0_load_248 | 96 | 0.14961 | 0.072458 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_133_0_load_34 | 102 | 0.12309 | 0.059616 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_133_0_load_76 | 104 | 0.076536 | 0.037068 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_133_0_load_41 | 106 | 0.13954 | 0.067583 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_133_0_load_46 | 111 | 0.063116 | 0.030569 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_133_0_load_247 | 112 | 0.16179 | 0.078359 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_133_0_load_120 | 114 | 0.15831 | 0.076675 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_133_0_load_147 | 115 | 0.10476 | 0.050737 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_133_0_load_53 | 117 | 0.090115 | 0.043644 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_133_0_load_118 | 119 | 0.096858 | 0.046911 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_133_0_load_59 | 125 | 0.09349 | 0.045279 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_133_0_load_82 | 126 | 0.10227 | 0.049534 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_133_0_load_254 | 127 | 0.09869 | 0.047798 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_133_0_load_255 | 128 | 0.10076 | 0.048802 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_133_0_load_150 | 129 | 0.080334 | 0.038908 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_133_0_load_77 | 130 | 0.11379 | 0.055111 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_133_0_load_90 | 131 | 0.10553 | 0.051111 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_133_0_load_113 | 136 | 0.10015 | 0.048505 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_133_0_load_119 | 138 | 0.14677 | 0.071085 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_133_0_load_114 | 139 | 0.074884 | 0.036268 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_133_0_load_136 | 140 | 0.066491 | 0.032203 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_133_0_load_83 | 141 | 0.13739 | 0.066539 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_133_0_load_122 | 144 | 0.15204 | 0.073636 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_133_0_load_102 | 145 | 0.10497 | 0.05084 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_133_0_load_214 | 149 | 0.094658 | 0.045845 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_133_0_load_89 | 150 | 0.1435 | 0.069501 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_133_0_load_123 | 151 | 0.15068 | 0.072979 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_133_0_load_139 | 154 | 0.11482 | 0.055612 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_133_0_load_234 | 155 | 0.13365 | 0.064731 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_133_0_load_108 | 159 | 0.073552 | 0.035623 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_133_0_load_109 | 160 | 0.11958 | 0.057917 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_133_0_load_153 | 161 | 0.074227 | 0.03595 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_133_0_load_170 | 163 | 0.15536 | 0.075244 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_133_0_load_171 | 165 | 0.08852 | 0.042872 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_133_0_load_232 | 167 | 0.14187 | 0.068712 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_133_0_load_156 | 168 | 0.12268 | 0.059419 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_133_0_load_172 | 169 | 0.054881 | 0.02658 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_133_0_load_158 | 170 | 0.16437 | 0.07961 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_133_0_load_250 | 175 | 0.1632 | 0.079043 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_133_0_load_165 | 177 | 0.12266 | 0.059408 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_133_0_load_166 | 180 | 0.10881 | 0.0527 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_133_0_load_218 | 181 | 0.28224 | 0.13669 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_133_0_load_168 | 182 | 0.11934 | 0.057801 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 115 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_133_0_line_0 |  | 0 | 1 | 0.034833 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_133_0_line_1 |  | 0 | 2 | 3.0904 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_133_0_line_2 |  | 1 | 3 | 0.13361 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_133_0_line_3 |  | 2 | 4 | 0.18447 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_133_0_line_4 |  | 3 | 5 | 0.14947 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_133_0_line_5 |  | 3 | 6 | 0.076229 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_133_0_line_6 |  | 4 | 171 | 0.37889 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_133_0_line_7 |  | 5 | 7 | 0.021518 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_133_0_line_8 |  | 6 | 8 | 3.3275 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_133_0_line_9 |  | 8 | 169 | 0.085987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_133_0_line_10 |  | 9 | 10 | 0.012382 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_133_0_line_11 |  | 9 | 11 | 0.020086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_133_0_line_12 |  | 9 | 12 | 0.10739 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_133_0_line_13 |  | 10 | 13 | 0.40009 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_133_0_line_14 |  | 11 | 14 | 0.10832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_133_0_line_15 |  | 12 | 15 | 0.056364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_133_0_line_16 |  | 13 | 22 | 0.033481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_133_0_line_17 |  | 14 | 25 | 0.030589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_133_0_line_18 |  | 14 | 26 | 0.031455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_133_0_line_19 |  | 14 | 16 | 0.19181 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_133_0_line_20 |  | 15 | 27 | 0.029229 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_133_0_line_21 |  | 16 | 17 | 0.013578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_133_0_line_22 |  | 16 | 18 | 0.3681 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_133_0_line_23 |  | 17 | 32 | 0.026594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_133_0_line_24 |  | 18 | 24 | 0.11623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_133_0_line_25 |  | 19 | 20 | 0.059904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_133_0_line_26 |  | 19 | 21 | 0.049461 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_133_0_line_27 |  | 20 | 23 | 0.028926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_133_0_line_28 |  | 21 | 28 | 0.3176 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_133_0_line_29 |  | 25 | 31 | 0.1662 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_133_0_line_30 |  | 26 | 30 | 0.006135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_133_0_line_31 |  | 28 | 29 | 0.2058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_133_0_line_32 |  | 28 | 30 | 0.1834 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_133_0_line_33 |  | 29 | 97 | 0.050972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_133_0_line_34 |  | 31 | 37 | 0.10497 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_133_0_line_35 |  | 32 | 34 | 0.016134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_133_0_line_36 |  | 33 | 34 | 0.093941 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_133_0_line_37 |  | 33 | 35 | 0.17855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_133_0_line_38 |  | 33 | 36 | 0.11039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_133_0_line_39 |  | 35 | 160 | 0.05445 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_133_0_line_40 |  | 36 | 91 | 0.047296 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_133_0_line_41 |  | 38 | 39 | 0.012369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_133_0_line_42 |  | 38 | 40 | 0.012924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_133_0_line_43 |  | 39 | 41 | 0.10908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_133_0_line_44 |  | 39 | 42 | 0.1069 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_133_0_line_45 |  | 40 | 43 | 0.10407 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_133_0_line_46 |  | 41 | 44 | 0.089799 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_133_0_line_47 |  | 41 | 45 | 0.1305 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_133_0_line_48 |  | 42 | 46 | 0.021853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_133_0_line_49 |  | 42 | 47 | 0.078668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_133_0_line_50 |  | 43 | 66 | 0.096478 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_133_0_line_51 |  | 45 | 73 | 0.038665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_133_0_line_52 |  | 46 | 48 | 0.019397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_133_0_line_53 |  | 47 | 51 | 0.08641 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_133_0_line_54 |  | 47 | 81 | 0.053858 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_133_0_line_55 |  | 48 | 49 | 0.040335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_133_0_line_56 |  | 48 | 50 | 0.16857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_133_0_line_57 |  | 49 | 72 | 0.037801 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_133_0_line_58 |  | 50 | 159 | 0.05316 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_133_0_line_59 |  | 51 | 52 | 0.051288 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_133_0_line_60 |  | 53 | 54 | 0.02124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_133_0_line_61 |  | 53 | 55 | 0.18348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_133_0_line_62 |  | 53 | 56 | 0.051219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_133_0_line_63 |  | 55 | 57 | 0.018819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_133_0_line_64 |  | 55 | 58 | 0.08313 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_133_0_line_65 |  | 56 | 82 | 0.057283 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_133_0_line_66 |  | 57 | 83 | 0.17072 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_133_0_line_67 |  | 59 | 60 | 0.015114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_133_0_line_68 |  | 59 | 61 | 0.046223 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_133_0_line_69 |  | 59 | 62 | 0.094855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_133_0_line_70 |  | 61 | 77 | 0.007183 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_133_0_line_71 |  | 61 | 75 | 0.052322 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_133_0_line_72 |  | 62 | 63 | 0.040969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_133_0_line_73 |  | 62 | 64 | 0.077448 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_133_0_line_74 |  | 63 | 67 | 0.07398 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_133_0_line_75 |  | 63 | 68 | 0.14955 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_133_0_line_76 |  | 64 | 65 | 0.030349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_133_0_line_77 |  | 66 | 78 | 0.088591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_133_0_line_78 |  | 67 | 69 | 0.015799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_133_0_line_79 |  | 68 | 157 | 0.013828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_133_0_line_80 |  | 69 | 70 | 0.006234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_133_0_line_81 |  | 70 | 71 | 0.040026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_133_0_line_82 |  | 73 | 74 | 0.05065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_133_0_line_83 |  | 74 | 80 | 0.13753 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
84 | MV_133_0_line_84 |  | 74 | 102 | 0.018157 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
85 | MV_133_0_line_85 |  | 75 | 76 | 0.025537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_133_0_line_86 |  | 76 | 118 | 0.033899 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
87 | MV_133_0_line_87 |  | 76 | 116 | 0.1259 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_133_0_line_88 |  | 79 | 80 | 0.028354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_133_0_line_89 |  | 80 | 103 | 0.036329 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
90 | MV_133_0_line_90 |  | 82 | 158 | 0.060765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_133_0_line_91 |  | 83 | 147 | 0.28987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_133_0_line_92 |  | 84 | 85 | 0.030135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_133_0_line_93 |  | 85 | 86 | 0.14496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_133_0_line_94 |  | 86 | 87 | 0.0094216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_133_0_line_95 |  | 87 | 97 | 0.066429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_133_0_line_96 |  | 88 | 89 | 0.096964 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_133_0_line_97 |  | 88 | 90 | 0.18852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_133_0_line_98 |  | 88 | 91 | 0.047137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_133_0_line_99 |  | 89 | 92 | 0.17842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_133_0_line_100 |  | 89 | 93 | 0.014297 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_133_0_line_101 |  | 90 | 95 | 0.059307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_133_0_line_102 |  | 90 | 96 | 0.097044 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
103 | MV_133_0_line_103 |  | 92 | 94 | 0.020011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_133_0_line_104 |  | 94 | 98 | 0.04584 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_133_0_line_105 |  | 96 | 99 | 0.005479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_133_0_line_106 |  | 97 | 101 | 0.18304 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_133_0_line_107 |  | 98 | 122 | 0.16886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_133_0_line_108 |  | 98 | 123 | 0.28224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_133_0_line_109 |  | 98 | 124 | 0.23345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_133_0_line_110 |  | 99 | 100 | 0.20059 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_133_0_line_111 |  | 100 | 102 | 0.011258 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_133_0_line_112 |  | 101 | 140 | 0.13344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_133_0_line_113 |  | 103 | 104 | 0.03096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_133_0_line_114 |  | 103 | 105 | 0.13392 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
115 | MV_133_0_line_115 |  | 105 | 120 | 0.022568 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
116 | MV_133_0_line_116 |  | 105 | 117 | 0.020399 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_133_0_line_117 |  | 106 | 107 | 0.017955 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_133_0_line_118 |  | 106 | 108 | 0.041813 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_133_0_line_119 |  | 107 | 109 | 0.00587 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_133_0_line_120 |  | 108 | 110 | 0.13066 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_133_0_line_121 |  | 109 | 111 | 0.11639 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
122 | MV_133_0_line_122 |  | 110 | 113 | 0.14523 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
123 | MV_133_0_line_123 |  | 110 | 114 | 0.06316 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
124 | MV_133_0_line_124 |  | 111 | 112 | 0.053728 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
125 | MV_133_0_line_125 |  | 113 | 115 | 0.041039 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
126 | MV_133_0_line_126 |  | 114 | 116 | 0.0048177 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
127 | MV_133_0_line_127 |  | 115 | 121 | 1.134 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
128 | MV_133_0_line_128 |  | 118 | 119 | 0.023313 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
129 | MV_133_0_line_129 |  | 119 | 120 | 0.037045 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
130 | MV_133_0_line_130 |  | 121 | 182 | 0.092013 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_133_0_line_131 |  | 122 | 125 | 0.042397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_133_0_line_132 |  | 123 | 126 | 0.01519 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_133_0_line_133 |  | 123 | 127 | 0.1579 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
134 | MV_133_0_line_134 |  | 123 | 128 | 0.12993 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
135 | MV_133_0_line_135 |  | 124 | 129 | 0.053731 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_133_0_line_136 |  | 125 | 130 | 0.22793 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_133_0_line_137 |  | 130 | 133 | 0.13503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_133_0_line_138 |  | 131 | 132 | 0.094756 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
139 | MV_133_0_line_139 |  | 132 | 152 | 0.28222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_133_0_line_140 |  | 133 | 134 | 0.20558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_133_0_line_141 |  | 134 | 135 | 0.091107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_133_0_line_142 |  | 134 | 136 | 0.008231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_133_0_line_143 |  | 135 | 137 | 0.19197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_133_0_line_144 |  | 135 | 138 | 0.023405 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_133_0_line_145 |  | 137 | 139 | 0.056238 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_133_0_line_146 |  | 139 | 156 | 0.008257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_133_0_line_147 |  | 141 | 142 | 0.063511 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_133_0_line_148 |  | 142 | 143 | 0.52698 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_133_0_line_149 |  | 142 | 144 | 0.067604 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
150 | MV_133_0_line_150 |  | 143 | 148 | 0.23274 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_133_0_line_151 |  | 144 | 151 | 0.11731 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
152 | MV_133_0_line_152 |  | 145 | 146 | 0.21173 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
153 | MV_133_0_line_153 |  | 146 | 158 | 0.25984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_133_0_line_154 |  | 147 | 148 | 0.22306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_133_0_line_155 |  | 147 | 149 | 0.087432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_133_0_line_156 |  | 148 | 150 | 0.063081 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
157 | MV_133_0_line_157 |  | 152 | 155 | 0.004708 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_133_0_line_158 |  | 152 | 156 | 0.017404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_133_0_line_159 |  | 152 | 153 | 0.34839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_133_0_line_160 |  | 153 | 154 | 0.027461 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
161 | MV_133_0_line_161 |  | 157 | 158 | 0.16135 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
162 | MV_133_0_line_162 |  | 161 | 162 | 0.023198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_133_0_line_163 |  | 161 | 163 | 0.4765 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
164 | MV_133_0_line_164 |  | 162 | 164 | 0.15416 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_133_0_line_165 |  | 163 | 165 | 0.020993 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_133_0_line_166 |  | 164 | 166 | 0.61219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_133_0_line_167 |  | 164 | 167 | 0.054683 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
168 | MV_133_0_line_168 |  | 166 | 168 | 0.061946 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_133_0_line_169 |  | 167 | 169 | 3.2118 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
170 | MV_133_0_line_170 |  | 170 | 171 | 0.030798 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
171 | MV_133_0_line_171 |  | 171 | 172 | 0.35538 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_133_0_line_172 |  | 171 | 173 | 0.44611 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_133_0_line_173 |  | 172 | 179 | 0.10851 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_133_0_line_174 |  | 172 | 180 | 0.065666 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_133_0_line_175 |  | 173 | 181 | 0.010409 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_133_0_line_176 |  | 173 | 174 | 0.19645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_133_0_line_177 |  | 174 | 175 | 0.059001 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
178 | MV_133_0_line_178 |  | 175 | 178 | 0.080124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_133_0_line_179 |  | 176 | 177 | 0.007797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_133_0_line_180 |  | 176 | 178 | 0.094799 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
181 | MV_133_0_line_181 |  | 179 | 182 | 0.013867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_133_0_trafo_147 | 25 MVA 110/20 kV | 183 | 115 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2689942.8414 | 1200525.3883
1 | 2689942.3609 | 1200490.5584
2 | 2689529.2801 | 1203587.9836
3 | 2690036.3457 | 1200471.7835
4 | 2689568.6961 | 1203768.1922
5 | 2689961.957 | 1200367.8181
6 | 2690108.4235 | 1200496.597
7 | 2689980.6718 | 1200357.204
8 | 2693426.5885 | 1200248.0469
9 | 2688669.1105 | 1206385.4942
10 | 2688663.7874 | 1206396.678
11 | 2688689.0703 | 1206387.97
12 | 2688578.4147 | 1206330.1784
13 | 2688583.733 | 1206577.5418
14 | 2688791.5944 | 1206354.1604
15 | 2688572.1705 | 1206305.036
16 | 2688787.7999 | 1206162.3892
17 | 2688794.1625 | 1206150.3871
18 | 2688557.318 | 1206449.3993
19 | 2688917.9521 | 1206701.4911
20 | 2688945.8192 | 1206746.4135
21 | 2688871.155 | 1206685.0836
22 | 2688615.7445 | 1206567.9216
23 | 2688958.161 | 1206772.5812
24 | 2688448.9276 | 1206488.1737
25 | 2688820.2936 | 1206343.3579
26 | 2688803.6436 | 1206383.2253
27 | 2688544.8368 | 1206315.5931
28 | 2688990.694 | 1206390.8384
29 | 2689190.9559 | 1206438.2009
30 | 2688807.3125 | 1206388.1498
31 | 2688975.2822 | 1206283.3482
32 | 2688806.2292 | 1206126.6843
33 | 2688898.1536 | 1206070.5041
34 | 2688814.1967 | 1206112.6491
35 | 2688888.3522 | 1205941.0733
36 | 2688966.2857 | 1206102.6288
37 | 2688955.1171 | 1206180.3356
38 | 2688570.01 | 1205758.28
39 | 2688579.9407 | 1205765.6533
40 | 2688559.6334 | 1205750.5756
41 | 2688648.8824 | 1205779.9858
42 | 2688544.2222 | 1205866.4118
43 | 2688599.4304 | 1205654.4141
44 | 2688711.6132 | 1205715.7308
45 | 2688779.146 | 1205772.1158
46 | 2688562.7159 | 1205878.0545
47 | 2688478.2059 | 1205823.6275
48 | 2688579.1307 | 1205888.3884
49 | 2688613.3848 | 1205909.844
50 | 2688508.6807 | 1206025.5781
51 | 2688416.3356 | 1205763.305
52 | 2688467.6175 | 1205762.5418
53 | 2688287.7814 | 1205694.736
54 | 2688300.9002 | 1205711.4075
55 | 2688262.7193 | 1205799.9788
56 | 2688247.8599 | 1205706.0533
57 | 2688247.635 | 1205811.2855
58 | 2688319.0331 | 1205861.1292
59 | 2688677.4925 | 1205484.5504
60 | 2688666.989 | 1205473.654
61 | 2688720.718 | 1205488.5839
62 | 2688601.6773 | 1205527.153
63 | 2688568.8084 | 1205551.609
64 | 2688570.9493 | 1205456.0618
65 | 2688556.7636 | 1205439.5295
66 | 2688681.4961 | 1205603.6879
67 | 2688498.1031 | 1205529.8412
68 | 2688422.932 | 1205584.5524
69 | 2688487.3358 | 1205518.2519
70 | 2688491.9024 | 1205513.9945
71 | 2688464.1226 | 1205485.1307
72 | 2688645.4909 | 1205929.9448
73 | 2688805.2973 | 1205743.5748
74 | 2688849.0351 | 1205718.6868
75 | 2688732.1513 | 1205437.5262
76 | 2688754.527 | 1205426.5346
77 | 2688727.7956 | 1205489.9233
78 | 2688696.068 | 1205676.5965
79 | 2688777.4093 | 1205592.7836
80 | 2688801.7577 | 1205607.2328
81 | 2688444.8395 | 1205865.9054
82 | 2688212.9984 | 1205667.3685
83 | 2688111.4583 | 1205914.2531
84 | 2689089.7198 | 1206237.9431
85 | 2689117.2312 | 1206225.7494
86 | 2689194.5953 | 1206348.342
87 | 2689199.6235 | 1206356.3098
88 | 2689045.6131 | 1206059.3495
89 | 2689115.839 | 1206045.9661
90 | 2689038.8735 | 1205940.5821
91 | 2689004.0504 | 1206074.1549
92 | 2689241.9441 | 1205970.989
93 | 2689103.4297 | 1206050.2393
94 | 2689253.4509 | 1205954.8504
95 | 2688992.2327 | 1205972.7996
96 | 2688997.1642 | 1205852.9584
97 | 2689235.0755 | 1206412.4876
98 | 2689282.7721 | 1205930.1169
99 | 2689001.1007 | 1205849.1368
100 | 2688876.2029 | 1205707.228
101 | 2689358.7679 | 1206539.8546
102 | 2688865.7705 | 1205711.5312
103 | 2688823.6708 | 1205580.3522
104 | 2688836.7863 | 1205608.4101
105 | 2688802.7217 | 1205489.281
106 | 2688949.1505 | 1205551.2897
107 | 2688954.7321 | 1205568.2729
108 | 2688923.3341 | 1205518.4504
109 | 2688955.1393 | 1205574.1272
110 | 2688880.0505 | 1205451.9402
111 | 2689053.5932 | 1205636.2019
112 | 2689022.1724 | 1205679.7843
113 | 2688978.3761 | 1205349.8264
114 | 2688837.5151 | 1205405.2502
115 | 2689011.3686 | 1205325.9246
116 | 2688840.8211 | 1205401.7459
117 | 2688811.784 | 1205479.4315
118 | 2688782.7689 | 1205428.3555
119 | 2688788.5339 | 1205450.9449
120 | 2688781.5659 | 1205482.6288
121 | 2689620.1917 | 1204369.1579
122 | 2689342.0255 | 1206050.2265
123 | 2689476.4026 | 1205834.6746
124 | 2689172.4918 | 1205809.8345
125 | 2689344.0161 | 1206092.5508
126 | 2689471.8406 | 1205820.1854
127 | 2689618.2639 | 1205904.0141
128 | 2689572.6273 | 1205921.9857
129 | 2689119.9149 | 1205820.9125
130 | 2689571.8561 | 1206086.0066
131 | 2689977.2103 | 1206240.1778
132 | 2689948.0728 | 1206330.3427
133 | 2689573.3109 | 1206141.9851
134 | 2689494.921 | 1206276.7317
135 | 2689542.2816 | 1206331.7335
136 | 2689489.6688 | 1206283.0794
137 | 2689675.8118 | 1206415.5704
138 | 2689560.7743 | 1206345.7737
139 | 2689722.942 | 1206446.2541
140 | 2689429.3099 | 1206650.7059
141 | 2687309.1697 | 1206277.8508
142 | 2687372.0043 | 1206267.4853
143 | 2687683.2478 | 1206163.6908
144 | 2687387.8445 | 1206201.7631
145 | 2687948.9684 | 1205649.6627
146 | 2688160.5255 | 1205641.0765
147 | 2687890.4809 | 1206060.5923
148 | 2687863.1882 | 1206205.2741
149 | 2687812.4409 | 1206099.0643
150 | 2687800.151 | 1206202.9342
151 | 2687491.6282 | 1206147.0804
152 | 2689728.5181 | 1206466.9404
153 | 2689984.1026 | 1206634.5417
154 | 2690006.5213 | 1206650.4012
155 | 2689732.1533 | 1206463.9375
156 | 2689718.3662 | 1206453.1344
157 | 2688411.648 | 1205576.5134
158 | 2688260.7741 | 1205633.6969
159 | 2688462.2727 | 1205999.4288
160 | 2688925.2258 | 1205981.1375
161 | 2693416.2015 | 1203693.0603
162 | 2693437.5067 | 1203683.9541
163 | 2693359.5841 | 1204166.1869
164 | 2693391.1895 | 1203539.7564
165 | 2693364.6338 | 1204186.5633
166 | 2693087.5266 | 1203562.921
167 | 2693412.1234 | 1203489.2391
168 | 2693088.0741 | 1203623.9478
169 | 2693478.2981 | 1200278.0862
170 | 2689622.5985 | 1204141.4449
171 | 2689621.3485 | 1204110.6727
172 | 2689740.8721 | 1204231.1127
173 | 2689758.832 | 1203969.3
174 | 2689886.7672 | 1203970.2577
175 | 2689944.0822 | 1203984.263
176 | 2689931.7936 | 1204057.9818
177 | 2689932.628 | 1204065.7328
178 | 2690015.0887 | 1204012.7179
179 | 2689704.0279 | 1204330.4688
180 | 2689794.6738 | 1204227.0412
181 | 2689759.6296 | 1203979.0072
182 | 2689701.7376 | 1204344.1434
183 | 2689011.3686 | 1205325.9246

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98878 | -0.11114 | 0.12683 | 0.061427
1 | 0.98872 | -0.11164 | 0 | 0
2 | 0.99491 | -0.061678 | 0.097374 | 0.04716
3 | 0.98857 | -0.11047 | 0 | 0
4 | 0.99531 | -0.058495 | 0 | 0
5 | 0.98855 | -0.1103 | 0 | 0
6 | 0.98845 | -0.11142 | 0.15747 | 0.076265
7 | 0.98855 | -0.11027 | 0.10436 | 0.050544
8 | 0.98436 | -0.14599 | 0 | 0
9 | 0.99372 | -0.023585 | 0.16034 | 0.077656
10 | 0.99372 | -0.023575 | 0 | 0
11 | 0.99373 | -0.023658 | 0 | 0
12 | 0.9937 | -0.023485 | 0 | 0
13 | 0.99365 | -0.023107 | 0 | 0
14 | 0.99378 | -0.02404 | 0 | 0
15 | 0.9937 | -0.023426 | 0 | 0
16 | 0.99432 | -0.019888 | 0.1257 | 0.060879
17 | 0.99435 | -0.020133 | 0 | 0
18 | 0.99421 | -0.020658 | 0 | 0
19 | 0.99334 | -0.026666 | 0 | 0
20 | 0.99333 | -0.026613 | 0 | 0
21 | 0.99334 | -0.026705 | 0.13392 | 0.064862
22 | 0.99365 | -0.023057 | 0.12586 | 0.060958
23 | 0.99333 | -0.026586 | 0.079522 | 0.038514
24 | 0.99419 | -0.020457 | 0.15032 | 0.072805
25 | 0.99377 | -0.023953 | 0.10618 | 0.051425
26 | 0.99375 | -0.023766 | 0 | 0
27 | 0.99369 | -0.023393 | 0.094372 | 0.045707
28 | 0.99347 | -0.02578 | 0.12204 | 0.059108
29 | 0.99336 | -0.024953 | 0 | 0
30 | 0.99374 | -0.023713 | 0.086651 | 0.041967
31 | 0.99373 | -0.024226 | 0 | 0
32 | 0.99441 | -0.020613 | 0 | 0
33 | 0.99478 | -0.018398 | 0 | 0
34 | 0.99444 | -0.020903 | 0.1037 | 0.050223
35 | 0.99475 | -0.018165 | 0 | 0
36 | 0.99505 | -0.020639 | 0 | 0
37 | 0.9937 | -0.024397 | 0.13287 | 0.064354
38 | 0.99748 | -0.031782 | 0.15406 | 0.074615
39 | 0.99748 | -0.031832 | 0 | 0
40 | 0.99748 | -0.031754 | 0 | 0
41 | 0.99761 | -0.032928 | 0 | 0
42 | 0.99737 | -0.032656 | 0 | 0
43 | 0.99744 | -0.032022 | 0.084312 | 0.040834
44 | 0.99758 | -0.033097 | 0.15483 | 0.074989
45 | 0.99788 | -0.031057 | 0.15204 | 0.073636
46 | 0.99736 | -0.032587 | 0.10348 | 0.050118
47 | 0.99734 | -0.03242 | 0 | 0
48 | 0.99735 | -0.032548 | 0 | 0
49 | 0.99735 | -0.032489 | 0 | 0
50 | 0.99734 | -0.032435 | 0 | 0
51 | 0.99732 | -0.032592 | 0 | 0
52 | 0.9973 | -0.032694 | 0.16306 | 0.078974
53 | 0.99711 | -0.025632 | 0 | 0
54 | 0.99711 | -0.025612 | 0.081076 | 0.039267
55 | 0.99691 | -0.024133 | 0 | 0
56 | 0.99717 | -0.026089 | 0 | 0
57 | 0.99689 | -0.024008 | 0.056246 | 0.027241
58 | 0.99688 | -0.024276 | 0.14067 | 0.068128
59 | 0.99841 | -0.02376 | 0 | 0
60 | 0.99841 | -0.023731 | 0.16161 | 0.078271
61 | 0.99853 | -0.024707 | 0 | 0
62 | 0.99819 | -0.021988 | 0 | 0
63 | 0.9981 | -0.02127 | 0.11804 | 0.057167
64 | 0.99817 | -0.022096 | 0 | 0
65 | 0.99817 | -0.022057 | 0.1094 | 0.052983
66 | 0.99741 | -0.032171 | 0 | 0
67 | 0.99806 | -0.021552 | 0.15472 | 0.074937
68 | 0.99772 | -0.024313 | 0.094831 | 0.045929
69 | 0.99805 | -0.021525 | 0 | 0
70 | 0.99805 | -0.021514 | 0 | 0
71 | 0.99804 | -0.021444 | 0.14906 | 0.072193
72 | 0.99734 | -0.032431 | 0.12981 | 0.06287
73 | 0.99794 | -0.031583 | 0 | 0
74 | 0.99802 | -0.032268 | 0 | 0
75 | 0.99874 | -0.023108 | 0.14495 | 0.070201
76 | 0.99881 | -0.023704 | 0 | 0
77 | 0.99853 | -0.024699 | 0.099924 | 0.048396
78 | 0.9974 | -0.032058 | 0.11211 | 0.054299
79 | 0.99825 | -0.031072 | 0.11313 | 0.054792
80 | 0.99825 | -0.03111 | 0 | 0
81 | 0.99733 | -0.032481 | 0.092668 | 0.044881
82 | 0.99724 | -0.026596 | 0.16162 | 0.078274
83 | 0.99667 | -0.025918 | 0 | 0
84 | 0.99327 | -0.024153 | 0.14888 | 0.072107
85 | 0.99327 | -0.024206 | 0 | 0
86 | 0.9933 | -0.024445 | 0.11378 | 0.055105
87 | 0.9933 | -0.024473 | 0.093193 | 0.045135
88 | 0.9953 | -0.022658 | 0 | 0
89 | 0.99511 | -0.021233 | 0 | 0
90 | 0.99618 | -0.029634 | 0 | 0
91 | 0.99517 | -0.021594 | 0.20616 | 0.099846
92 | 0.9948 | -0.018808 | 0 | 0
93 | 0.99511 | -0.021213 | 0.11187 | 0.054182
94 | 0.99476 | -0.018532 | 0.14193 | 0.068742
95 | 0.99617 | -0.02956 | 0.10781 | 0.052214
96 | 0.99689 | -0.024128 | 0.14961 | 0.072458
97 | 0.99333 | -0.024737 | 0 | 0
98 | 0.99469 | -0.017979 | 0 | 0
99 | 0.99692 | -0.024346 | 0 | 0
100 | 0.99792 | -0.032294 | 0 | 0
101 | 0.99332 | -0.024653 | 0 | 0
102 | 0.99798 | -0.032738 | 0.12309 | 0.059616
103 | 0.99832 | -0.030796 | 0 | 0
104 | 0.99831 | -0.030768 | 0.076536 | 0.037068
105 | 0.99856 | -0.029614 | 0 | 0
106 | 0.99941 | -0.0017928 | 0.13954 | 0.067583
107 | 0.9994 | -0.001745 | 0 | 0
108 | 0.99943 | -0.0019719 | 0 | 0
109 | 0.9994 | -0.0017293 | 0 | 0
110 | 0.99949 | -0.0025146 | 0 | 0
111 | 0.99935 | -0.0020474 | 0.063116 | 0.030569
112 | 0.99934 | -0.0021527 | 0.16179 | 0.078359
113 | 0.99989 | -0.00055655 | 0 | 0
114 | 0.99915 | -0.022039 | 0.15831 | 0.076675
115 | 1 | 0 | -10.5937 | -4.8013
116 | 0.99914 | -0.022101 | 0 | 0
117 | 0.99855 | -0.029593 | 0.090115 | 0.043644
118 | 0.99875 | -0.024015 | 0 | 0
119 | 0.99866 | -0.029077 | 0.096858 | 0.046911
120 | 0.9986 | -0.029411 | 0 | 0
121 | 0.99724 | -0.073141 | 0 | 0
122 | 0.9945 | -0.01655 | 0 | 0
123 | 0.99458 | -0.017022 | 0 | 0
124 | 0.99466 | -0.017794 | 0 | 0
125 | 0.99445 | -0.016184 | 0.09349 | 0.045279
126 | 0.99458 | -0.017003 | 0.10227 | 0.049534
127 | 0.99455 | -0.017214 | 0.09869 | 0.047798
128 | 0.99455 | -0.017183 | 0.10076 | 0.048802
129 | 0.99465 | -0.017847 | 0.080334 | 0.038908
130 | 0.99411 | -0.019001 | 0.11379 | 0.055111
131 | 0.99353 | -0.015643 | 0.10553 | 0.051111
132 | 0.99355 | -0.01552 | 0 | 0
133 | 0.99399 | -0.018155 | 0 | 0
134 | 0.99381 | -0.016812 | 0 | 0
135 | 0.99375 | -0.016306 | 0 | 0
136 | 0.99381 | -0.016802 | 0.10015 | 0.048505
137 | 0.99364 | -0.015532 | 0 | 0
138 | 0.99374 | -0.016264 | 0.14677 | 0.071085
139 | 0.9936 | -0.015903 | 0.074884 | 0.036268
140 | 0.99331 | -0.024559 | 0.066491 | 0.032203
141 | 0.99582 | -0.019259 | 0.13739 | 0.066539
142 | 0.99583 | -0.019362 | 0 | 0
143 | 0.99613 | -0.021889 | 0 | 0
144 | 0.99579 | -0.019612 | 0.15204 | 0.073636
145 | 0.99725 | -0.027246 | 0.10497 | 0.05084
146 | 0.99729 | -0.026974 | 0 | 0
147 | 0.99642 | -0.024118 | 0 | 0
148 | 0.99626 | -0.022871 | 0 | 0
149 | 0.99641 | -0.024024 | 0.094658 | 0.045845
150 | 0.99624 | -0.022981 | 0.1435 | 0.069501
151 | 0.99576 | -0.019828 | 0.15068 | 0.072979
152 | 0.99359 | -0.015819 | 0 | 0
153 | 0.99353 | -0.015427 | 0 | 0
154 | 0.99353 | -0.015466 | 0.11482 | 0.055612
155 | 0.99358 | -0.015811 | 0.13365 | 0.064731
156 | 0.99359 | -0.015876 | 0 | 0
157 | 0.9977 | -0.024154 | 0 | 0
158 | 0.99733 | -0.027246 | 0 | 0
159 | 0.99733 | -0.03239 | 0.073552 | 0.035623
160 | 0.99474 | -0.018244 | 0.11958 | 0.057917
161 | 0.98054 | -0.17499 | 0.074227 | 0.03595
162 | 0.98055 | -0.17508 | 0 | 0
163 | 0.98031 | -0.17648 | 0.15536 | 0.075244
164 | 0.98061 | -0.17565 | 0 | 0
165 | 0.98031 | -0.17646 | 0.08852 | 0.042872
166 | 0.98052 | -0.17506 | 0 | 0
167 | 0.98066 | -0.17525 | 0.14187 | 0.068712
168 | 0.98051 | -0.17497 | 0.12268 | 0.059419
169 | 0.98429 | -0.14546 | 0.054881 | 0.02658
170 | 0.99584 | -0.06267 | 0.16437 | 0.07961
171 | 0.99585 | -0.062608 | 0 | 0
172 | 0.99669 | -0.068994 | 0 | 0
173 | 0.99553 | -0.059906 | 0 | 0
174 | 0.99546 | -0.059286 | 0 | 0
175 | 0.99543 | -0.059503 | 0.1632 | 0.079043
176 | 0.99539 | -0.059535 | 0 | 0
177 | 0.99539 | -0.059523 | 0.12266 | 0.059408
178 | 0.99542 | -0.059391 | 0 | 0
179 | 0.99697 | -0.071035 | 0 | 0
180 | 0.99668 | -0.068912 | 0.10881 | 0.0527
181 | 0.99553 | -0.059871 | 0.28224 | 0.13669
182 | 0.997 | -0.071295 | 0.11934 | 0.057801
183 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.90433 | 0.40118 | -0.90428 | -0.40119 | 5.1776e-05 | -8.223e-06 | 0.028883 | 0.028884 | 0.028884 | 0.98878 | -0.11114 | 0.98872 | -0.11164 | 13.7542
1 | -1.0312 | -0.46261 | 1.0372 | 0.46273 | 0.0059868 | 0.00012048 | 0.032996 | 0.032952 | 0.032996 | 0.98878 | -0.11114 | 0.99491 | -0.061678 | 15.7122
2 | 0.90428 | 0.40119 | -0.90413 | -0.40427 | 0.00014899 | -0.0030738 | 0.028884 | 0.028921 | 0.028921 | 0.98872 | -0.11164 | 0.98857 | -0.11047 | 13.1459
3 | -1.1345 | -0.50989 | 1.135 | 0.50994 | 0.00042806 | 5.0054e-05 | 0.03609 | 0.036088 | 0.03609 | 0.99491 | -0.061678 | 0.99531 | -0.058495 | 17.1859
4 | 0.10436 | 0.046555 | -0.10436 | -0.050042 | 2.2503e-06 | -0.003487 | 0.003337 | 0.0033798 | 0.0033798 | 0.98857 | -0.11047 | 0.98855 | -0.1103 | 1.5363
5 | 0.79977 | 0.35771 | -0.79968 | -0.35774 | 8.8901e-05 | -3.3239e-05 | 0.025584 | 0.025585 | 0.025585 | 0.98857 | -0.11047 | 0.98845 | -0.11142 | 12.1833
6 | -1.135 | -0.50994 | 1.1356 | 0.50117 | 0.0006568 | -0.0087718 | 0.036088 | 0.035982 | 0.036088 | 0.99531 | -0.058495 | 0.99585 | -0.062608 | 16.4035
7 | 0.10436 | 0.050042 | -0.10436 | -0.050544 | 3.2875e-07 | -0.00050197 | 0.0033798 | 0.0033862 | 0.0033862 | 0.98855 | -0.1103 | 0.98855 | -0.11027 | 1.5392
8 | 0.64221 | 0.28148 | -0.63972 | -0.28378 | 0.0024917 | -0.0023044 | 0.020478 | 0.020524 | 0.020524 | 0.98845 | -0.11142 | 0.98436 | -0.14599 | 9.7732
9 | 0.63972 | 0.28378 | -0.63967 | -0.28576 | 4.8409e-05 | -0.0019748 | 0.020524 | 0.020547 | 0.020547 | 0.98436 | -0.14599 | 0.98429 | -0.14546 | 9.3398
10 | 0.12587 | 0.050448 | -0.12587 | -0.05074 | 2.5673e-07 | -0.00029185 | 0.0039393 | 0.0039425 | 0.0039425 | 0.99372 | -0.023585 | 0.99372 | -0.023575 | 1.7921
11 | -0.38059 | -0.16926 | 0.38059 | 0.16879 | 3.9243e-06 | -0.00047241 | 0.0121 | 0.012095 | 0.0121 | 0.99372 | -0.023585 | 0.99373 | -0.023658 | 5.5001
12 | 0.094375 | 0.041157 | -0.094373 | -0.043689 | 1.2953e-06 | -0.0025315 | 0.002991 | 0.0030211 | 0.0030211 | 0.99372 | -0.023585 | 0.9937 | -0.023485 | 1.3732
13 | 0.12587 | 0.05074 | -0.12586 | -0.060169 | 8.5278e-06 | -0.0094297 | 0.0039425 | 0.0040529 | 0.0040529 | 0.99372 | -0.023575 | 0.99365 | -0.023107 | 1.8422
14 | -0.38059 | -0.16879 | 0.38061 | 0.16624 | 2.11e-05 | -0.0025478 | 0.012095 | 0.012065 | 0.012095 | 0.99373 | -0.023658 | 0.99378 | -0.02404 | 5.4975
15 | 0.094373 | 0.043689 | -0.094373 | -0.045018 | 6.9049e-07 | -0.0013286 | 0.0030211 | 0.0030375 | 0.0030375 | 0.9937 | -0.023485 | 0.9937 | -0.023426 | 1.3807
16 | 0.12586 | 0.060169 | -0.12586 | -0.060958 | 7.36e-07 | -0.00078906 | 0.0040529 | 0.0040629 | 0.0040629 | 0.99365 | -0.023107 | 0.99365 | -0.023057 | 1.8468
17 | 0.23906 | 0.11474 | -0.23906 | -0.11546 | 2.4258e-06 | -0.00072056 | 0.0077029 | 0.007712 | 0.007712 | 0.99378 | -0.02404 | 0.99377 | -0.023953 | 3.5054
18 | 0.84482 | 0.38502 | -0.84479 | -0.38575 | 3.0552e-05 | -0.00073262 | 0.026969 | 0.026978 | 0.026978 | 0.99378 | -0.02404 | 0.99375 | -0.023766 | 12.2626
19 | -1.4645 | -0.66601 | 1.4652 | 0.66625 | 0.00074633 | 0.00024121 | 0.046733 | 0.046731 | 0.046733 | 0.99378 | -0.02404 | 0.99432 | -0.019888 | 22.254
20 | 0.094373 | 0.045018 | -0.094372 | -0.045707 | 3.6105e-07 | -0.000689 | 0.0030375 | 0.0030462 | 0.0030462 | 0.9937 | -0.023426 | 0.99369 | -0.023393 | 1.3846
21 | -1.7413 | -0.79676 | 1.7413 | 0.79646 | 5.6021e-05 | -0.00030391 | 0.055595 | 0.055591 | 0.055595 | 0.99432 | -0.019888 | 0.99435 | -0.020133 | 25.2703
22 | 0.15034 | 0.069638 | -0.15033 | -0.070063 | 1.5192e-05 | -0.0004249 | 0.0048103 | 0.0048156 | 0.0048156 | 0.99432 | -0.019888 | 0.99421 | -0.020658 | 2.2931
23 | -1.7413 | -0.79646 | 1.7414 | 0.79586 | 0.0001097 | -0.0005953 | 0.055591 | 0.055583 | 0.055591 | 0.99435 | -0.020133 | 0.99441 | -0.020613 | 25.2685
24 | 0.15033 | 0.070063 | -0.15032 | -0.072805 | 3.6236e-06 | -0.0027419 | 0.0048156 | 0.0048498 | 0.0048498 | 0.99421 | -0.020658 | 0.99419 | -0.020457 | 2.2044
25 | 0.079523 | 0.036422 | -0.079522 | -0.037833 | 5.2021e-07 | -0.0014111 | 0.0025419 | 0.0025592 | 0.0025592 | 0.99334 | -0.026666 | 0.99333 | -0.026613 | 1.1633
26 | -0.079523 | -0.036422 | 0.079523 | 0.035257 | 4.2428e-07 | -0.0011651 | 0.0025419 | 0.002528 | 0.0025419 | 0.99334 | -0.026666 | 0.99334 | -0.026705 | 1.1554
27 | 0.079522 | 0.037833 | -0.079522 | -0.038514 | 2.5377e-07 | -0.00068138 | 0.0025592 | 0.0025678 | 0.0025678 | 0.99333 | -0.026613 | 0.99333 | -0.026586 | 1.1672
28 | -0.21345 | -0.10012 | 0.21347 | 0.099761 | 2.6545e-05 | -0.00035754 | 0.0068514 | 0.0068468 | 0.0068514 | 0.99334 | -0.026705 | 0.99347 | -0.02578 | 3.2626
29 | 0.13288 | 0.06404 | -0.13288 | -0.064233 | 5.4401e-06 | -0.00019253 | 0.0042849 | 0.0042874 | 0.0042874 | 0.99377 | -0.023953 | 0.99373 | -0.024226 | 2.0416
30 | 0.84479 | 0.38575 | -0.84478 | -0.3859 | 5.9613e-06 | -0.00014288 | 0.026978 | 0.02698 | 0.02698 | 0.99375 | -0.023766 | 0.99374 | -0.023713 | 12.2634
31 | 0.42243 | 0.18516 | -0.42238 | -0.18999 | 4.9556e-05 | -0.0048346 | 0.013402 | 0.013459 | 0.013459 | 0.99347 | -0.02578 | 0.99336 | -0.024953 | 6.1177
32 | -0.75794 | -0.34403 | 0.75813 | 0.34393 | 0.00019113 | -9.6438e-05 | 0.024186 | 0.024184 | 0.024186 | 0.99347 | -0.02578 | 0.99374 | -0.023713 | 11.5172
33 | 0.42238 | 0.18999 | -0.42236 | -0.19119 | 1.234e-05 | -0.0011972 | 0.013459 | 0.013473 | 0.013473 | 0.99336 | -0.024953 | 0.99333 | -0.024737 | 6.1243
34 | 0.13288 | 0.064233 | -0.13287 | -0.064354 | 3.4391e-06 | -0.00012159 | 0.0042874 | 0.004289 | 0.004289 | 0.99373 | -0.024226 | 0.9937 | -0.024397 | 2.0424
35 | -1.7414 | -0.79586 | 1.7415 | 0.7955 | 6.6539e-05 | -0.0003612 | 0.055583 | 0.055579 | 0.055583 | 0.99441 | -0.020613 | 0.99444 | -0.020903 | 25.2651
36 | 1.8458 | 0.84598 | -1.8452 | -0.84573 | 0.00058109 | 0.00025303 | 0.058921 | 0.058923 | 0.058923 | 0.99478 | -0.018398 | 0.99444 | -0.020903 | 28.0583
37 | 0.11959 | 0.053636 | -0.11958 | -0.057853 | 3.4943e-06 | -0.0042174 | 0.0038034 | 0.0038551 | 0.0038551 | 0.99478 | -0.018398 | 0.99475 | -0.018165 | 1.7523
38 | -1.9654 | -0.89962 | 1.966 | 0.89718 | 0.00057951 | -0.002437 | 0.062724 | 0.062693 | 0.062724 | 0.99478 | -0.018398 | 0.99505 | -0.020639 | 28.5111
39 | 0.11958 | 0.057853 | -0.11958 | -0.057917 | 1.4421e-06 | -6.3418e-05 | 0.0038551 | 0.0038559 | 0.0038559 | 0.99475 | -0.018165 | 0.99474 | -0.018244 | 1.8362
40 | -1.966 | -0.89718 | 1.9662 | 0.89613 | 0.00024812 | -0.0010446 | 0.062693 | 0.06268 | 0.062693 | 0.99505 | -0.020639 | 0.99517 | -0.021594 | 28.4968
41 | -0.3505 | -0.16711 | 0.3505 | 0.16681 | 2.0845e-06 | -0.00029321 | 0.011237 | 0.011234 | 0.011237 | 0.99748 | -0.031782 | 0.99748 | -0.031832 | 5.1079
42 | 0.19644 | 0.09249 | -0.19644 | -0.092797 | 6.8165e-07 | -0.00030682 | 0.0062836 | 0.0062874 | 0.0062874 | 0.99748 | -0.031782 | 0.99748 | -0.031754 | 2.8579
43 | -0.91316 | -0.429 | 0.91328 | 0.42645 | 0.00012401 | -0.0025549 | 0.029198 | 0.029166 | 0.029198 | 0.99748 | -0.031832 | 0.99761 | -0.032928 | 13.2719
44 | 0.56266 | 0.26219 | -0.56259 | -0.26228 | 6.1474e-05 | -8.8459e-05 | 0.017965 | 0.017966 | 0.017966 | 0.99748 | -0.031832 | 0.99737 | -0.032656 | 8.5553
45 | 0.19644 | 0.092797 | -0.19643 | -0.092916 | 7.3319e-06 | -0.00011902 | 0.0062874 | 0.0062889 | 0.0062889 | 0.99748 | -0.031754 | 0.99744 | -0.032022 | 2.9947
46 | 0.15484 | 0.074885 | -0.15483 | -0.074989 | 3.9641e-06 | -0.0001042 | 0.0049769 | 0.0049783 | 0.0049783 | 0.99761 | -0.032928 | 0.99758 | -0.033097 | 2.3706
47 | -1.0681 | -0.50133 | 1.0684 | 0.50135 | 0.00027104 | 1.4677e-05 | 0.034143 | 0.034141 | 0.034143 | 0.99761 | -0.032928 | 0.99788 | -0.031057 | 16.2585
48 | 0.30685 | 0.14051 | -0.30685 | -0.14103 | 2.7856e-06 | -0.0005182 | 0.0097683 | 0.0097746 | 0.0097746 | 0.99737 | -0.032656 | 0.99736 | -0.032587 | 4.443
49 | 0.25574 | 0.12177 | -0.25574 | -0.12363 | 7.0789e-06 | -0.0018663 | 0.0081983 | 0.0082217 | 0.0082217 | 0.99737 | -0.032656 | 0.99734 | -0.03242 | 3.7372
50 | 0.11212 | 0.052082 | -0.11212 | -0.052195 | 2.2013e-06 | -0.0001132 | 0.0035779 | 0.0035793 | 0.0035793 | 0.99744 | -0.032022 | 0.99741 | -0.032171 | 1.7044
51 | -1.2204 | -0.57498 | 1.2205 | 0.57409 | 7.8599e-05 | -0.000896 | 0.039028 | 0.039016 | 0.039028 | 0.99788 | -0.031057 | 0.99794 | -0.031583 | 17.7399
52 | 0.20337 | 0.090912 | -0.20337 | -0.091373 | 1.0774e-06 | -0.00046035 | 0.0064477 | 0.0064531 | 0.0064531 | 0.99736 | -0.032587 | 0.99735 | -0.032548 | 2.9332
53 | 0.16307 | 0.078815 | -0.16306 | -0.078915 | 4.232e-06 | -9.9956e-05 | 0.0052423 | 0.0052436 | 0.0052436 | 0.99734 | -0.03242 | 0.99732 | -0.032592 | 2.4969
54 | 0.092668 | 0.044818 | -0.092668 | -0.044881 | 8.5208e-07 | -6.3421e-05 | 0.0029795 | 0.0029803 | 0.0029803 | 0.99734 | -0.03242 | 0.99733 | -0.032481 | 1.4192
55 | 0.12981 | 0.061015 | -0.12981 | -0.061973 | 9.3078e-07 | -0.00095767 | 0.0041517 | 0.0041635 | 0.0041635 | 0.99735 | -0.032548 | 0.99735 | -0.032489 | 1.8925
56 | 0.073554 | 0.030358 | -0.073553 | -0.034361 | 1.2174e-06 | -0.0040031 | 0.0023031 | 0.0023498 | 0.0023498 | 0.99735 | -0.032548 | 0.99734 | -0.032435 | 1.0681
57 | 0.12981 | 0.061973 | -0.12981 | -0.06287 | 8.7716e-07 | -0.00089749 | 0.0041635 | 0.0041748 | 0.0041748 | 0.99735 | -0.032489 | 0.99734 | -0.032431 | 1.8976
58 | 0.073553 | 0.034361 | -0.073552 | -0.035623 | 3.9446e-07 | -0.0012624 | 0.0023498 | 0.0023655 | 0.0023655 | 0.99734 | -0.032435 | 0.99733 | -0.03239 | 1.0752
59 | 0.16306 | 0.078915 | -0.16306 | -0.078974 | 2.5128e-06 | -5.9324e-05 | 0.0052436 | 0.0052443 | 0.0052443 | 0.99732 | -0.032592 | 0.9973 | -0.032694 | 2.4973
60 | 0.081076 | 0.038763 | -0.081076 | -0.039267 | 1.9239e-07 | -0.00050414 | 0.0026017 | 0.002608 | 0.002608 | 0.99711 | -0.025632 | 0.99711 | -0.025612 | 1.1855
61 | 0.87603 | 0.38504 | -0.87584 | -0.38934 | 0.00018834 | -0.0042988 | 0.027704 | 0.027755 | 0.027755 | 0.99711 | -0.025632 | 0.99691 | -0.024133 | 12.6158
62 | -0.9571 | -0.42381 | 0.95717 | 0.42261 | 6.2764e-05 | -0.0011973 | 0.030304 | 0.03029 | 0.030304 | 0.99711 | -0.025632 | 0.99717 | -0.026089 | 13.7747
63 | 0.73517 | 0.32131 | -0.73515 | -0.32175 | 1.3564e-05 | -0.00044252 | 0.023233 | 0.023238 | 0.023238 | 0.99691 | -0.024133 | 0.99689 | -0.024008 | 10.5627
64 | 0.14067 | 0.068031 | -0.14067 | -0.068128 | 3.0332e-06 | -9.6726e-05 | 0.0045248 | 0.004526 | 0.004526 | 0.99691 | -0.024133 | 0.99688 | -0.024276 | 2.1552
65 | -0.95717 | -0.42261 | 0.95724 | 0.42127 | 7.0126e-05 | -0.0013393 | 0.03029 | 0.030274 | 0.03029 | 0.99717 | -0.026089 | 0.99724 | -0.026596 | 13.7682
66 | 0.67891 | 0.29451 | -0.67877 | -0.29463 | 0.0001397 | -0.00011499 | 0.02143 | 0.021432 | 0.021432 | 0.99689 | -0.024008 | 0.99667 | -0.025918 | 10.2057
67 | 0.16161 | 0.077911 | -0.16161 | -0.078271 | 5.4341e-07 | -0.00035956 | 0.0051874 | 0.0051919 | 0.0051919 | 0.99841 | -0.02376 | 0.99841 | -0.023731 | 2.3599
68 | -2.0131 | -0.91813 | 2.0134 | 0.9171 | 0.0002525 | -0.0010253 | 0.063974 | 0.063961 | 0.063974 | 0.99841 | -0.02376 | 0.99853 | -0.024707 | 29.0793
69 | 1.8515 | 0.84021 | -1.8511 | -0.84234 | 0.00043785 | -0.0021272 | 0.058788 | 0.058815 | 0.058815 | 0.99841 | -0.02376 | 0.99819 | -0.021988 | 26.7342
70 | 0.099925 | 0.048225 | -0.099924 | -0.048396 | 9.8733e-08 | -0.00017097 | 0.0032076 | 0.0032098 | 0.0032098 | 0.99853 | -0.024707 | 0.99853 | -0.024699 | 1.459
71 | -2.1133 | -0.96533 | 2.1137 | 0.96553 | 0.00042057 | 0.00020114 | 0.067168 | 0.067167 | 0.067168 | 0.99853 | -0.024707 | 0.99874 | -0.023108 | 31.9848
72 | 1.7417 | 0.79017 | -1.7415 | -0.7911 | 0.00016736 | -0.00092491 | 0.055311 | 0.055322 | 0.055322 | 0.99819 | -0.021988 | 0.9981 | -0.02127 | 25.1465
73 | 0.1094 | 0.05217 | -0.1094 | -0.052261 | 1.6959e-06 | -9.1059e-05 | 0.0035051 | 0.0035063 | 0.0035063 | 0.99819 | -0.021988 | 0.99817 | -0.022096 | 1.6697
74 | 0.3038 | 0.14557 | -0.30379 | -0.14565 | 1.2514e-05 | -8.014e-05 | 0.0097433 | 0.0097444 | 0.0097444 | 0.9981 | -0.02127 | 0.99806 | -0.021552 | 4.6402
75 | 1.3197 | 0.58836 | -1.3192 | -0.58824 | 0.00046536 | 0.0001137 | 0.04179 | 0.041792 | 0.041792 | 0.9981 | -0.02127 | 0.99772 | -0.024313 | 19.9011
76 | 0.1094 | 0.052261 | -0.1094 | -0.052983 | 4.9939e-07 | -0.00072182 | 0.0035063 | 0.0035153 | 0.0035153 | 0.99817 | -0.022096 | 0.99817 | -0.022057 | 1.5979
77 | 0.11212 | 0.052195 | -0.11211 | -0.054299 | 1.5262e-06 | -0.0021038 | 0.0035793 | 0.0036054 | 0.0036054 | 0.99741 | -0.032171 | 0.9974 | -0.032058 | 1.6388
78 | 0.14906 | 0.070718 | -0.14906 | -0.071093 | 4.8078e-07 | -0.00037561 | 0.004772 | 0.0047767 | 0.0047767 | 0.99806 | -0.021552 | 0.99805 | -0.021525 | 2.1712
79 | 1.2244 | 0.54231 | -1.2244 | -0.54263 | 2.7715e-05 | -0.00032043 | 0.038745 | 0.038749 | 0.038749 | 0.99772 | -0.024313 | 0.9977 | -0.024154 | 17.6132
80 | 0.14906 | 0.071093 | -0.14906 | -0.071242 | 1.8996e-07 | -0.00014821 | 0.0047767 | 0.0047785 | 0.0047785 | 0.99805 | -0.021525 | 0.99805 | -0.021514 | 2.1721
81 | 0.14906 | 0.071242 | -0.14906 | -0.072193 | 1.2232e-06 | -0.00095158 | 0.0047785 | 0.0047905 | 0.0047905 | 0.99805 | -0.021514 | 0.99804 | -0.021444 | 2.1775
82 | -1.2205 | -0.57409 | 1.2206 | 0.57291 | 0.00010289 | -0.0011739 | 0.039016 | 0.039002 | 0.039016 | 0.99794 | -0.031583 | 0.99802 | -0.032268 | 17.7347
83 | -5.3053 | -2.4229 | 5.3065 | 2.415 | 0.0012087 | -0.0079285 | 0.1687 | 0.1686 | 0.1687 | 0.99802 | -0.032268 | 0.99825 | -0.03111 | 26.4421
84 | 4.0847 | 1.85 | -4.0845 | -1.8505 | 0.00014754 | -0.00051319 | 0.1297 | 0.12971 | 0.12971 | 0.99802 | -0.032268 | 0.99798 | -0.032738 | 35.8313
85 | -2.2587 | -1.0357 | 2.2589 | 1.0352 | 0.00017584 | -0.00055608 | 0.071821 | 0.071814 | 0.071821 | 0.99874 | -0.023108 | 0.99881 | -0.023704 | 32.646
86 | 5.6859 | 2.5811 | -5.6856 | -2.583 | 0.00034121 | -0.0019326 | 0.18047 | 0.1805 | 0.1805 | 0.99881 | -0.023704 | 0.99875 | -0.024015 | 28.2912
87 | -7.9448 | -3.6163 | 7.9473 | 3.6098 | 0.0024752 | -0.0065006 | 0.25229 | 0.25219 | 0.25229 | 0.99881 | -0.023704 | 0.99914 | -0.022101 | 39.5433
88 | -0.11313 | -0.054792 | 0.11313 | 0.054118 | 4.9901e-07 | -0.00067447 | 0.0036351 | 0.0036266 | 0.0036351 | 0.99825 | -0.031072 | 0.99825 | -0.03111 | 1.6523
89 | -5.4196 | -2.4691 | 5.42 | 2.467 | 0.00033291 | -0.0020873 | 0.17222 | 0.1722 | 0.17222 | 0.99825 | -0.03111 | 0.99832 | -0.030796 | 26.9942
90 | -1.1189 | -0.49955 | 1.119 | 0.49813 | 0.00010201 | -0.0014127 | 0.035469 | 0.035452 | 0.035469 | 0.99724 | -0.026596 | 0.99733 | -0.027246 | 16.1224
91 | 0.67877 | 0.29463 | -0.67859 | -0.30145 | 0.00017841 | -0.0068203 | 0.021432 | 0.021512 | 0.021512 | 0.99667 | -0.025918 | 0.99642 | -0.024118 | 9.7782
92 | -0.14888 | -0.072107 | 0.14888 | 0.071397 | 9.2816e-07 | -0.00070958 | 0.0048077 | 0.0047988 | 0.0048077 | 0.99327 | -0.024153 | 0.99327 | -0.024206 | 2.1853
93 | -0.14888 | -0.071397 | 0.14889 | 0.067984 | 4.4172e-06 | -0.0034135 | 0.0047988 | 0.0047567 | 0.0047988 | 0.99327 | -0.024206 | 0.9933 | -0.024445 | 2.1813
94 | -0.26266 | -0.12309 | 0.26267 | 0.12287 | 8.9359e-07 | -0.00022168 | 0.0084302 | 0.0084275 | 0.0084302 | 0.9933 | -0.024445 | 0.9933 | -0.024473 | 3.8319
95 | -0.35586 | -0.168 | 0.35587 | 0.16644 | 1.158e-05 | -0.0015615 | 0.011437 | 0.011417 | 0.011437 | 0.9933 | -0.024473 | 0.99333 | -0.024737 | 5.1985
96 | 1.5208 | 0.67844 | -1.5204 | -0.68064 | 0.00030213 | -0.0022034 | 0.048298 | 0.048325 | 0.048325 | 0.9953 | -0.022658 | 0.99511 | -0.021233 | 21.9659
97 | -3.6934 | -1.6734 | 3.6969 | 1.67 | 0.0034794 | -0.0034308 | 0.11761 | 0.11755 | 0.11761 | 0.9953 | -0.022658 | 0.99618 | -0.029634 | 53.457
98 | 2.1727 | 0.99495 | -2.1724 | -0.99598 | 0.00030235 | -0.0010251 | 0.069309 | 0.069322 | 0.069322 | 0.9953 | -0.022658 | 0.99517 | -0.021594 | 31.5102
99 | 1.4086 | 0.6268 | -1.4081 | -0.63088 | 0.00047698 | -0.0040755 | 0.044725 | 0.044775 | 0.044775 | 0.99511 | -0.021233 | 0.9948 | -0.018808 | 20.3521
100 | 0.11187 | 0.053844 | -0.11187 | -0.054182 | 2.4789e-07 | -0.00033795 | 0.0036017 | 0.0036059 | 0.0036059 | 0.99511 | -0.021233 | 0.99511 | -0.021213 | 1.6391
101 | 0.10781 | 0.050809 | -0.10781 | -0.052214 | 9.4918e-07 | -0.0014049 | 0.0034537 | 0.0034712 | 0.0034712 | 0.99618 | -0.029634 | 0.99617 | -0.02956 | 1.5778
102 | -3.8047 | -1.7208 | 3.8072 | 1.7222 | 0.0025317 | 0.0014707 | 0.12101 | 0.121 | 0.12101 | 0.99618 | -0.029634 | 0.99689 | -0.024128 | 57.6216
103 | 1.4081 | 0.63088 | -1.408 | -0.63133 | 5.3564e-05 | -0.00045692 | 0.044775 | 0.04478 | 0.04478 | 0.9948 | -0.018808 | 0.99476 | -0.018532 | 20.3547
104 | 1.2661 | 0.56259 | -1.266 | -0.56364 | 9.8957e-05 | -0.0010536 | 0.040206 | 0.040219 | 0.040219 | 0.99476 | -0.018532 | 0.99469 | -0.017979 | 18.2813
105 | -3.9568 | -1.7947 | 3.957 | 1.7946 | 0.00011578 | -9.5663e-05 | 0.12582 | 0.12581 | 0.12582 | 0.99689 | -0.024128 | 0.99692 | -0.024346 | 57.1891
106 | 0.066493 | 0.024748 | -0.066492 | -0.02906 | 1.0618e-06 | -0.0043118 | 0.0020619 | 0.0021089 | 0.0021089 | 0.99333 | -0.024737 | 0.99332 | -0.024653 | 0.95858
107 | 0.88391 | 0.39153 | -0.88373 | -0.39547 | 0.00017775 | -0.0039355 | 0.028057 | 0.028104 | 0.028104 | 0.99469 | -0.017979 | 0.9945 | -0.01655 | 12.7744
108 | 0.30177 | 0.13878 | -0.30173 | -0.14544 | 3.5309e-05 | -0.0066561 | 0.0096396 | 0.0097221 | 0.0097221 | 0.99469 | -0.017979 | 0.99458 | -0.017022 | 4.4191
109 | 0.080337 | 0.03333 | -0.080335 | -0.038845 | 2.036e-06 | -0.0055141 | 0.0025242 | 0.0025898 | 0.0025898 | 0.99469 | -0.017979 | 0.99466 | -0.017794 | 1.1772
110 | -3.957 | -1.7946 | 3.9612 | 1.7911 | 0.0042369 | -0.0035077 | 0.12581 | 0.12576 | 0.12581 | 0.99692 | -0.024346 | 0.99792 | -0.032294 | 57.1884
111 | -3.9612 | -1.7911 | 3.9614 | 1.7909 | 0.00023768 | -0.00019719 | 0.12576 | 0.12575 | 0.12576 | 0.99792 | -0.032294 | 0.99798 | -0.032738 | 57.1625
112 | 0.066492 | 0.02906 | -0.066491 | -0.032203 | 8.0636e-07 | -0.0031433 | 0.0021089 | 0.0021471 | 0.0021471 | 0.99332 | -0.024653 | 0.99331 | -0.024559 | 0.97595
113 | 0.076536 | 0.036331 | -0.076536 | -0.037068 | 2.4899e-07 | -0.00073664 | 0.0024498 | 0.002459 | 0.002459 | 0.99832 | -0.030796 | 0.99831 | -0.030768 | 1.1177
114 | -5.4965 | -2.5034 | 5.4978 | 2.4957 | 0.0012615 | -0.0076779 | 0.17465 | 0.17455 | 0.17465 | 0.99832 | -0.030796 | 0.99856 | -0.029614 | 27.3739
115 | -5.5879 | -2.5388 | 5.5881 | 2.5375 | 0.00021952 | -0.0012903 | 0.17743 | 0.17742 | 0.17743 | 0.99856 | -0.029614 | 0.9986 | -0.029411 | 27.8108
116 | 0.090115 | 0.043159 | -0.090115 | -0.043644 | 2.2769e-07 | -0.00048557 | 0.0028885 | 0.0028946 | 0.0028946 | 0.99856 | -0.029614 | 0.99855 | -0.029593 | 1.3157
117 | 0.22492 | 0.10817 | -0.22492 | -0.10859 | 1.2466e-06 | -0.00042782 | 0.007209 | 0.0072144 | 0.0072144 | 0.99941 | -0.0017928 | 0.9994 | -0.001745 | 3.2793
118 | -0.36446 | -0.17575 | 0.36447 | 0.17475 | 7.6167e-06 | -0.00099491 | 0.011687 | 0.011675 | 0.011687 | 0.99941 | -0.0017928 | 0.99943 | -0.0019719 | 5.3125
119 | 0.22492 | 0.10859 | -0.22492 | -0.10873 | 4.0797e-07 | -0.00013986 | 0.0072144 | 0.0072161 | 0.0072161 | 0.9994 | -0.001745 | 0.9994 | -0.0017293 | 3.2801
120 | -0.36447 | -0.17475 | 0.3645 | 0.17164 | 2.3697e-05 | -0.0031092 | 0.011675 | 0.011636 | 0.011675 | 0.99943 | -0.0019719 | 0.99949 | -0.0025146 | 5.3068
121 | 0.22492 | 0.10873 | -0.22491 | -0.10887 | 1.0801e-05 | -0.00013201 | 0.0072161 | 0.0072179 | 0.0072179 | 0.9994 | -0.0017293 | 0.99935 | -0.0020474 | 3.4371
122 | -8.4716 | -3.8618 | 8.4749 | 3.8545 | 0.0032437 | -0.007293 | 0.2689 | 0.26879 | 0.2689 | 0.99949 | -0.0025146 | 0.99989 | -0.00055655 | 42.1478
123 | 8.1072 | 3.6901 | -8.1057 | -3.6862 | 0.0014924 | 0.003926 | 0.25727 | 0.25727 | 0.25727 | 0.99949 | -0.0025146 | 0.99915 | -0.022039 | 39.8866
124 | 0.16179 | 0.078296 | -0.16179 | -0.078359 | 2.581e-06 | -6.244e-05 | 0.0051921 | 0.0051929 | 0.0051929 | 0.99935 | -0.0020474 | 0.99934 | -0.0021527 | 2.4728
125 | -8.4749 | -3.8545 | 8.4758 | 3.8524 | 0.0009161 | -0.0020624 | 0.26879 | 0.26876 | 0.26879 | 0.99989 | -0.00055655 | 1 | 0 | 42.1307
126 | 7.9473 | 3.6095 | -7.9473 | -3.6098 | 9.4679e-05 | -0.00024887 | 0.25219 | 0.25219 | 0.25219 | 0.99915 | -0.022039 | 0.99914 | -0.022101 | 39.5285
127 | 2.1039 | 0.93837 | -2.0993 | -0.93453 | 0.0046053 | 0.0038464 | 0.066503 | 0.066519 | 0.066519 | 1 | 0 | 0.99724 | -0.073141 | 19.0055
128 | 5.6856 | 2.583 | -5.6853 | -2.5823 | 0.00027116 | 0.00069702 | 0.1805 | 0.1805 | 0.1805 | 0.99875 | -0.024015 | 0.99866 | -0.029077 | 27.9842
129 | 5.5885 | 2.5354 | -5.5881 | -2.5375 | 0.00036025 | -0.0021184 | 0.17739 | 0.17742 | 0.17742 | 0.99866 | -0.029077 | 0.9986 | -0.029411 | 27.8082
130 | 2.0993 | 0.93453 | -2.0988 | -0.93655 | 0.00054374 | -0.002023 | 0.066519 | 0.066545 | 0.066545 | 0.99724 | -0.073141 | 0.997 | -0.071295 | 30.2477
131 | 0.88373 | 0.39547 | -0.88369 | -0.39646 | 4.4722e-05 | -0.00098785 | 0.028104 | 0.028116 | 0.028116 | 0.9945 | -0.01655 | 0.99445 | -0.016184 | 12.7798
132 | 0.10227 | 0.049175 | -0.10227 | -0.049534 | 2.2031e-07 | -0.0003587 | 0.0032938 | 0.0032983 | 0.0032983 | 0.99458 | -0.017022 | 0.99458 | -0.017003 | 1.4992
133 | 0.098692 | 0.047613 | -0.09869 | -0.047798 | 2.8479e-06 | -0.00018467 | 0.0031805 | 0.0031828 | 0.0031828 | 0.99458 | -0.017022 | 0.99455 | -0.017214 | 1.5156
134 | 0.10077 | 0.04865 | -0.10076 | -0.048802 | 2.4433e-06 | -0.0001519 | 0.0032478 | 0.0032497 | 0.0032497 | 0.99458 | -0.017022 | 0.99455 | -0.017183 | 1.5475
135 | 0.080335 | 0.038845 | -0.080334 | -0.038908 | 6.4227e-07 | -6.3059e-05 | 0.0025898 | 0.0025906 | 0.0025906 | 0.99466 | -0.017794 | 0.99465 | -0.017847 | 1.2336
136 | 0.7902 | 0.35118 | -0.78994 | -0.35128 | 0.00025592 | -0.00010871 | 0.025102 | 0.025105 | 0.025105 | 0.99445 | -0.016184 | 0.99411 | -0.019001 | 11.9546
137 | 0.67615 | 0.29617 | -0.67607 | -0.29933 | 8.2972e-05 | -0.0031611 | 0.021436 | 0.021473 | 0.021473 | 0.99411 | -0.019001 | 0.99399 | -0.018155 | 9.7604
138 | -0.10553 | -0.051111 | 0.10553 | 0.051 | 1.9588e-06 | -0.00011044 | 0.0034069 | 0.0034055 | 0.0034069 | 0.99353 | -0.015643 | 0.99355 | -0.01552 | 1.6224
139 | -0.10553 | -0.051 | 0.10554 | 0.04435 | 4.2653e-06 | -0.0066507 | 0.0034055 | 0.003326 | 0.0034055 | 0.99355 | -0.01552 | 0.99359 | -0.015819 | 1.548
140 | 0.67607 | 0.29933 | -0.67594 | -0.30415 | 0.00012688 | -0.0048112 | 0.021473 | 0.02153 | 0.02153 | 0.99399 | -0.018155 | 0.99381 | -0.016812 | 9.7865
141 | 0.57579 | 0.25584 | -0.57575 | -0.25797 | 4.0796e-05 | -0.0021362 | 0.018302 | 0.018327 | 0.018327 | 0.99381 | -0.016812 | 0.99375 | -0.016306 | 8.3305
142 | 0.10015 | 0.048311 | -0.10015 | -0.048505 | 1.1472e-07 | -0.00019407 | 0.0032298 | 0.0032323 | 0.0032323 | 0.99381 | -0.016812 | 0.99381 | -0.016802 | 1.4692
143 | 0.42898 | 0.18744 | -0.42893 | -0.19195 | 4.7579e-05 | -0.0045118 | 0.013599 | 0.013652 | 0.013652 | 0.99375 | -0.016306 | 0.99364 | -0.015532 | 6.2055
144 | 0.14677 | 0.070534 | -0.14677 | -0.071085 | 7.0021e-07 | -0.00055164 | 0.0047304 | 0.0047374 | 0.0047374 | 0.99375 | -0.016306 | 0.99374 | -0.016264 | 2.1534
145 | 0.42893 | 0.19195 | -0.42891 | -0.192 | 1.8676e-05 | -5.4585e-05 | 0.013652 | 0.013653 | 0.013653 | 0.99364 | -0.015532 | 0.9936 | -0.015903 | 6.5014
146 | 0.35402 | 0.15574 | -0.35402 | -0.15593 | 1.3921e-06 | -0.00019421 | 0.011237 | 0.011239 | 0.011239 | 0.9936 | -0.015903 | 0.99359 | -0.015876 | 5.1087
147 | -0.13739 | -0.066539 | 0.13739 | 0.065036 | 1.6532e-06 | -0.0015033 | 0.0044251 | 0.0044063 | 0.0044251 | 0.99582 | -0.019259 | 0.99583 | -0.019362 | 2.0114
148 | -0.44012 | -0.21144 | 0.44026 | 0.199 | 0.00013941 | -0.01244 | 0.014154 | 0.014002 | 0.014154 | 0.99583 | -0.019362 | 0.99613 | -0.021889 | 6.4338
149 | 0.30274 | 0.14641 | -0.30273 | -0.14648 | 1.1447e-05 | -7.2862e-05 | 0.0097482 | 0.0097492 | 0.0097492 | 0.99583 | -0.019362 | 0.99579 | -0.019612 | 4.6425
150 | -0.44026 | -0.199 | 0.44032 | 0.1935 | 6.0627e-05 | -0.0054966 | 0.014002 | 0.013937 | 0.014002 | 0.99613 | -0.021889 | 0.99626 | -0.022871 | 6.3643
151 | 0.15069 | 0.072843 | -0.15068 | -0.072979 | 4.9221e-06 | -0.00013578 | 0.004852 | 0.0048537 | 0.0048537 | 0.99579 | -0.019612 | 0.99576 | -0.019828 | 2.3113
152 | -0.10497 | -0.05084 | 0.10498 | 0.050591 | 4.2962e-06 | -0.0002487 | 0.0033763 | 0.0033731 | 0.0033763 | 0.99725 | -0.027246 | 0.99729 | -0.026974 | 1.6077
153 | -0.10498 | -0.050591 | 0.10498 | 0.044422 | 3.8588e-06 | -0.0061694 | 0.0033731 | 0.0032995 | 0.0033731 | 0.99729 | -0.026974 | 0.99733 | -0.027246 | 1.5332
154 | 0.58393 | 0.25768 | -0.58383 | -0.26293 | 0.00010216 | -0.0052566 | 0.018491 | 0.018553 | 0.018553 | 0.99642 | -0.024118 | 0.99626 | -0.022871 | 8.4334
155 | 0.094659 | 0.043773 | -0.094658 | -0.045845 | 1.0745e-06 | -0.0020723 | 0.0030214 | 0.0030471 | 0.0030471 | 0.99642 | -0.024118 | 0.99641 | -0.024024 | 1.385
156 | 0.1435 | 0.069428 | -0.1435 | -0.069501 | 2.3986e-06 | -7.324e-05 | 0.0046192 | 0.0046202 | 0.0046202 | 0.99626 | -0.022871 | 0.99624 | -0.022981 | 2.2001
157 | 0.13365 | 0.06462 | -0.13365 | -0.064731 | 1.1699e-07 | -0.00011094 | 0.0043132 | 0.0043146 | 0.0043146 | 0.99359 | -0.015819 | 0.99358 | -0.015811 | 1.9612
158 | -0.35402 | -0.15634 | 0.35402 | 0.15593 | 2.9361e-06 | -0.00040935 | 0.011244 | 0.011239 | 0.011244 | 0.99359 | -0.015819 | 0.99359 | -0.015876 | 5.1109
159 | 0.11483 | 0.04737 | -0.11483 | -0.05558 | 6.2174e-06 | -0.0082096 | 0.003609 | 0.0037066 | 0.0037066 | 0.99359 | -0.015819 | 0.99353 | -0.015427 | 1.6848
160 | 0.11483 | 0.05558 | -0.11482 | -0.055612 | 6.7228e-07 | -3.194e-05 | 0.0037066 | 0.003707 | 0.003707 | 0.99353 | -0.015427 | 0.99353 | -0.015466 | 1.7652
161 | 1.2244 | 0.54263 | -1.2239 | -0.54255 | 0.00043166 | 7.8718e-05 | 0.038749 | 0.038751 | 0.038751 | 0.9977 | -0.024154 | 0.99733 | -0.027246 | 18.453
162 | -0.31816 | -0.15307 | 0.31816 | 0.15254 | 3.3439e-06 | -0.00053154 | 0.010394 | 0.010388 | 0.010394 | 0.98054 | -0.17499 | 0.98055 | -0.17508 | 4.7247
163 | 0.24393 | 0.11712 | -0.24388 | -0.11763 | 5.3926e-05 | -0.00051302 | 0.0079664 | 0.0079733 | 0.0079733 | 0.98054 | -0.17499 | 0.98031 | -0.17648 | 3.7968
164 | -0.31816 | -0.15254 | 0.31819 | 0.14901 | 2.2111e-05 | -0.0035326 | 0.010388 | 0.010343 | 0.010388 | 0.98055 | -0.17508 | 0.98061 | -0.17565 | 4.7217
165 | 0.08852 | 0.042391 | -0.08852 | -0.042872 | 2.346e-07 | -0.00048161 | 0.0028902 | 0.0028963 | 0.0028963 | 0.98031 | -0.17648 | 0.98031 | -0.17646 | 1.3165
166 | 0.1227 | 0.043947 | -0.12269 | -0.057997 | 1.2503e-05 | -0.01405 | 0.0038367 | 0.0039952 | 0.0039952 | 0.98061 | -0.17565 | 0.98052 | -0.17506 | 1.816
167 | -0.44088 | -0.19295 | 0.4409 | 0.1929 | 1.9554e-05 | -5.0529e-05 | 0.014167 | 0.014167 | 0.014167 | 0.98061 | -0.17565 | 0.98066 | -0.17525 | 6.7464
168 | 0.12269 | 0.057997 | -0.12268 | -0.059419 | 1.326e-06 | -0.0014216 | 0.0039952 | 0.0040133 | 0.0040133 | 0.98052 | -0.17506 | 0.98051 | -0.17497 | 1.8242
169 | -0.58277 | -0.26161 | 0.58479 | 0.25918 | 0.0020187 | -0.0024366 | 0.018804 | 0.01876 | 0.018804 | 0.98066 | -0.17525 | 0.98429 | -0.14546 | 8.9544
170 | -0.16437 | -0.07961 | 0.16437 | 0.079574 | 1.5379e-06 | -3.5498e-05 | 0.0052943 | 0.0052938 | 0.0052943 | 0.99584 | -0.06267 | 0.99585 | -0.062608 | 2.5211
171 | -1.8683 | -0.83825 | 1.87 | 0.83032 | 0.0016689 | -0.0079268 | 0.05936 | 0.05926 | 0.05936 | 0.99585 | -0.062608 | 0.99669 | -0.068994 | 26.9816
172 | 0.56834 | 0.2575 | -0.56814 | -0.268 | 0.0001962 | -0.010502 | 0.018087 | 0.018215 | 0.018215 | 0.99585 | -0.062608 | 0.99553 | -0.059906 | 8.2797
173 | -1.9788 | -0.88146 | 1.9794 | 0.87906 | 0.00056997 | -0.0024053 | 0.062742 | 0.062711 | 0.062742 | 0.99669 | -0.068994 | 0.99697 | -0.071035 | 28.519
174 | 0.10881 | 0.051143 | -0.10881 | -0.0527 | 1.069e-06 | -0.0015572 | 0.0034823 | 0.0035017 | 0.0035017 | 0.99669 | -0.068994 | 0.99668 | -0.068912 | 1.5917
175 | 0.28224 | 0.13645 | -0.28224 | -0.13669 | 1.1487e-06 | -0.00024597 | 0.0090904 | 0.0090935 | 0.0090935 | 0.99553 | -0.059906 | 0.99553 | -0.059871 | 4.1334
176 | 0.2859 | 0.13156 | -0.28588 | -0.1362 | 2.1977e-05 | -0.0046417 | 0.0091259 | 0.009183 | 0.009183 | 0.99553 | -0.059906 | 0.99546 | -0.059286 | 4.1741
177 | 0.28588 | 0.1362 | -0.28587 | -0.13626 | 8.8656e-06 | -6.4243e-05 | 0.009183 | 0.0091839 | 0.0091839 | 0.99546 | -0.059286 | 0.99543 | -0.059503 | 4.3733
178 | 0.12267 | 0.057218 | -0.12266 | -0.059113 | 1.658e-06 | -0.0018951 | 0.0039253 | 0.0039489 | 0.0039489 | 0.99543 | -0.059503 | 0.99542 | -0.059391 | 1.7949
179 | 0.12266 | 0.059223 | -0.12266 | -0.059408 | 1.6253e-07 | -0.0001844 | 0.0039503 | 0.0039526 | 0.0039526 | 0.99539 | -0.059535 | 0.99539 | -0.059523 | 1.7966
180 | -0.12266 | -0.059223 | 0.12266 | 0.059113 | 2.6347e-06 | -0.00011048 | 0.0039503 | 0.0039489 | 0.0039503 | 0.99539 | -0.059535 | 0.99542 | -0.059391 | 1.8811
181 | -1.9794 | -0.87906 | 1.9794 | 0.87875 | 7.28e-05 | -0.0003075 | 0.062711 | 0.062708 | 0.062711 | 0.99697 | -0.071035 | 0.997 | -0.071295 | 28.5052

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 10.6985 | 4.852

## res_load
| p_mw | q_mvar
0 | 0.12683 | 0.061427
1 | 0.097374 | 0.04716
2 | 0.15747 | 0.076265
3 | 0.10436 | 0.050544
4 | 0.16034 | 0.077656
5 | 0.1257 | 0.060879
6 | 0.13392 | 0.064862
7 | 0.12586 | 0.060958
8 | 0.079522 | 0.038514
9 | 0.15032 | 0.072805
10 | 0.10618 | 0.051425
11 | 0.094372 | 0.045707
12 | 0.12204 | 0.059108
13 | 0.086651 | 0.041967
14 | 0.1037 | 0.050223
15 | 0.13287 | 0.064354
16 | 0.15406 | 0.074615
17 | 0.084312 | 0.040834
18 | 0.15483 | 0.074989
19 | 0.15204 | 0.073636
20 | 0.10348 | 0.050118
21 | 0.16306 | 0.078974
22 | 0.081076 | 0.039267
23 | 0.056246 | 0.027241
24 | 0.14067 | 0.068128
25 | 0.16161 | 0.078271
26 | 0.11804 | 0.057167
27 | 0.1094 | 0.052983
28 | 0.15472 | 0.074937
29 | 0.094831 | 0.045929
30 | 0.14906 | 0.072193
31 | 0.12981 | 0.06287
32 | 0.14495 | 0.070201
33 | 0.099924 | 0.048396
34 | 0.11211 | 0.054299
35 | 0.11313 | 0.054792
36 | 0.092668 | 0.044881
37 | 0.16162 | 0.078274
38 | 0.14888 | 0.072107
39 | 0.11378 | 0.055105
40 | 0.093193 | 0.045135
41 | 0.20616 | 0.099846
42 | 0.11187 | 0.054182
43 | 0.14193 | 0.068742
44 | 0.10781 | 0.052214
45 | 0.14961 | 0.072458
46 | 0.12309 | 0.059616
47 | 0.076536 | 0.037068
48 | 0.13954 | 0.067583
49 | 0.063116 | 0.030569
50 | 0.16179 | 0.078359
51 | 0.15831 | 0.076675
52 | 0.10476 | 0.050737
53 | 0.090115 | 0.043644
54 | 0.096858 | 0.046911
55 | 0.09349 | 0.045279
56 | 0.10227 | 0.049534
57 | 0.09869 | 0.047798
58 | 0.10076 | 0.048802
59 | 0.080334 | 0.038908
60 | 0.11379 | 0.055111
61 | 0.10553 | 0.051111
62 | 0.10015 | 0.048505
63 | 0.14677 | 0.071085
64 | 0.074884 | 0.036268
65 | 0.066491 | 0.032203
66 | 0.13739 | 0.066539
67 | 0.15204 | 0.073636
68 | 0.10497 | 0.05084
69 | 0.094658 | 0.045845
70 | 0.1435 | 0.069501
71 | 0.15068 | 0.072979
72 | 0.11482 | 0.055612
73 | 0.13365 | 0.064731
74 | 0.073552 | 0.035623
75 | 0.11958 | 0.057917
76 | 0.074227 | 0.03595
77 | 0.15536 | 0.075244
78 | 0.08852 | 0.042872
79 | 0.14187 | 0.068712
80 | 0.12268 | 0.059419
81 | 0.054881 | 0.02658
82 | 0.16437 | 0.07961
83 | 0.1632 | 0.079043
84 | 0.12266 | 0.059408
85 | 0.10881 | 0.0527
86 | 0.28224 | 0.13669
87 | 0.11934 | 0.057801

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1