## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_142_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_142_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_142_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_142_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_142_0_node_296 | 20 | n |  | TRUE
5 | bus_MV_142_0_node_42 | 20 | n |  | TRUE
6 | bus_MV_142_0_node_58 | 20 | n |  | TRUE
7 | bus_MV_142_0_node_4 | 20 | n |  | TRUE
8 | bus_MV_142_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_142_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_142_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_142_0_node_8 | 20 | n |  | TRUE
12 | bus_MV_142_0_node_10 | 20 | n |  | TRUE
13 | bus_MV_142_0_node_297 | 20 | n |  | TRUE
14 | bus_MV_142_0_node_51 | 20 | n |  | TRUE
15 | bus_MV_142_0_node_9 | 20 | n |  | TRUE
16 | bus_MV_142_0_node_20 | 20 | n |  | TRUE
17 | bus_MV_142_0_node_13 | 20 | n |  | TRUE
18 | bus_MV_142_0_node_59 | 20 | n |  | TRUE
19 | bus_MV_142_0_node_308 | 20 | n |  | TRUE
20 | bus_MV_142_0_node_11 | 20 | n |  | TRUE
21 | bus_MV_142_0_node_12 | 20 | n |  | TRUE
22 | bus_MV_142_0_node_14 | 20 | n |  | TRUE
23 | bus_MV_142_0_node_305 | 20 | n |  | TRUE
24 | bus_MV_142_0_node_15 | 20 | n |  | TRUE
25 | bus_MV_142_0_node_16 | 20 | n |  | TRUE
26 | bus_MV_142_0_node_22 | 20 | n |  | TRUE
27 | bus_MV_142_0_node_17 | 20 | n |  | TRUE
28 | bus_MV_142_0_node_304 | 20 | n |  | TRUE
29 | bus_MV_142_0_node_18 | 20 | n |  | TRUE
30 | bus_MV_142_0_node_19 | 20 | n |  | TRUE
31 | bus_MV_142_0_node_44 | 20 | n |  | TRUE
32 | bus_MV_142_0_node_24 | 20 | n |  | TRUE
33 | bus_MV_142_0_node_57 | 20 | n |  | TRUE
34 | bus_MV_142_0_node_25 | 20 | n |  | TRUE
35 | bus_MV_142_0_node_27 | 20 | n |  | TRUE
36 | bus_MV_142_0_node_30 | 20 | n |  | TRUE
37 | bus_MV_142_0_node_295 | 20 | n |  | TRUE
38 | bus_MV_142_0_node_31 | 20 | n |  | TRUE
39 | bus_MV_142_0_node_33 | 20 | n |  | TRUE
40 | bus_MV_142_0_node_36 | 20 | n |  | TRUE
41 | bus_MV_142_0_node_34 | 20 | n |  | TRUE
42 | bus_MV_142_0_node_35 | 20 | n |  | TRUE
43 | bus_MV_142_0_node_38 | 20 | n |  | TRUE
44 | bus_MV_142_0_node_37 | 20 | n |  | TRUE
45 | bus_MV_142_0_node_52 | 20 | n |  | TRUE
46 | bus_MV_142_0_node_46 | 20 | n |  | TRUE
47 | bus_MV_142_0_node_45 | 20 | n |  | TRUE
48 | bus_MV_142_0_node_39 | 20 | n |  | TRUE
49 | bus_MV_142_0_node_40 | 20 | n |  | TRUE
50 | bus_MV_142_0_node_41 | 20 | n |  | TRUE
51 | bus_MV_142_0_node_43 | 20 | n |  | TRUE
52 | bus_MV_142_0_node_47 | 20 | n |  | TRUE
53 | bus_MV_142_0_node_49 | 20 | n |  | TRUE
54 | bus_MV_142_0_node_48 | 20 | n |  | TRUE
55 | bus_MV_142_0_node_50 | 20 | n |  | TRUE
56 | bus_MV_142_0_node_53 | 20 | n |  | TRUE
57 | bus_MV_142_0_node_54 | 20 | n |  | TRUE
58 | bus_MV_142_0_node_55 | 20 | n |  | TRUE
59 | bus_MV_142_0_node_56 | 20 | n |  | TRUE
60 | bus_MV_142_0_node_300 | 20 | n |  | TRUE
61 | bus_MV_142_0_node_140 | 20 | n |  | TRUE
62 | bus_MV_142_0_node_141 | 20 | n |  | TRUE
63 | bus_MV_142_0_node_142 | 20 | n |  | TRUE
64 | bus_MV_142_0_node_155 | 20 | n |  | TRUE
65 | bus_MV_142_0_node_143 | 20 | n |  | TRUE
66 | bus_MV_142_0_node_145 | 20 | n |  | TRUE
67 | bus_MV_142_0_node_144 | 20 | n |  | TRUE
68 | bus_MV_142_0_node_146 | 20 | n |  | TRUE
69 | bus_MV_142_0_node_158 | 20 | n |  | TRUE
70 | bus_MV_142_0_node_147 | 20 | n |  | TRUE
71 | bus_MV_142_0_node_148 | 20 | n |  | TRUE
72 | bus_MV_142_0_node_150 | 20 | n |  | TRUE
73 | bus_MV_142_0_node_152 | 20 | n |  | TRUE
74 | bus_MV_142_0_node_149 | 20 | n |  | TRUE
75 | bus_MV_142_0_node_151 | 20 | n |  | TRUE
76 | bus_MV_142_0_node_157 | 20 | n |  | TRUE
77 | bus_MV_142_0_node_156 | 20 | n |  | TRUE
78 | bus_MV_142_0_node_160 | 20 | n |  | TRUE
79 | bus_MV_142_0_node_159 | 20 | n |  | TRUE
80 | bus_MV_142_0_node_153 | 20 | n |  | TRUE
81 | bus_MV_142_0_node_154 | 20 | n |  | TRUE
82 | bus_MV_142_0_node_299 | 20 | n |  | TRUE
83 | bus_HV_142_0_node_51 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_142_0_load_0 | 0 | 0.13899 | 0.067317 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_142_0_load_296 | 4 | 0.14011 | 0.067857 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_142_0_load_42 | 5 | 0.11555 | 0.055962 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_142_0_load_58 | 6 | 0.090185 | 0.043679 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_142_0_load_4 | 7 | 0.11313 | 0.054789 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_142_0_load_297 | 13 | 0.073994 | 0.035837 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_142_0_load_51 | 14 | 0.099536 | 0.048208 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_142_0_load_13 | 17 | 0.10444 | 0.050582 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_142_0_load_59 | 18 | 0.10148 | 0.049147 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_142_0_load_308 | 19 | 0.14543 | 0.070435 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_142_0_load_11 | 20 | 0.11568 | 0.056026 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_142_0_load_305 | 23 | 0.10238 | 0.049586 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_142_0_load_15 | 24 | 0.12639 | 0.061215 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_142_0_load_304 | 28 | 0.11928 | 0.05777 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_142_0_load_18 | 29 | 0.1563 | 0.075701 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_142_0_load_44 | 31 | 0.14744 | 0.07141 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_142_0_load_57 | 33 | 0.12447 | 0.060282 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_142_0_load_25 | 34 | 0.15125 | 0.073254 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_142_0_load_295 | 37 | 0.11726 | 0.056791 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_142_0_load_31 | 38 | 0.11398 | 0.055205 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_142_0_load_38 | 43 | 0.13236 | 0.064103 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_142_0_load_52 | 45 | 0.11134 | 0.053926 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_142_0_load_46 | 46 | 0.12017 | 0.0582 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_142_0_load_45 | 47 | 0.13465 | 0.065215 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_142_0_load_39 | 48 | 0.13138 | 0.06363 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_142_0_load_50 | 55 | 0.1351 | 0.06543 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_142_0_load_53 | 56 | 0.16046 | 0.077713 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_142_0_load_56 | 59 | 0.086825 | 0.042051 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_142_0_load_300 | 60 | 0.10382 | 0.050283 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_142_0_load_140 | 61 | 0.10634 | 0.051501 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_142_0_load_155 | 64 | 0.075234 | 0.036438 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_142_0_load_143 | 65 | 0.14275 | 0.069139 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_142_0_load_145 | 66 | 0.10035 | 0.0486 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_142_0_load_158 | 69 | 0.073876 | 0.03578 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_142_0_load_147 | 70 | 0.16422 | 0.079537 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_142_0_load_156 | 77 | 0.1566 | 0.075845 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_142_0_load_159 | 79 | 0.10464 | 0.050677 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_142_0_load_153 | 80 | 0.14398 | 0.069732 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_142_0_load_154 | 81 | 0.15928 | 0.077145 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_142_0_load_299 | 82 | 0.1252 | 0.060635 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_142_0_line_0 |  | 0 | 1 | 0.068745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_142_0_line_1 |  | 1 | 2 | 0.13929 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_142_0_line_2 |  | 1 | 3 | 0.26752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_142_0_line_3 |  | 2 | 4 | 0.019841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_142_0_line_4 |  | 3 | 5 | 0.0297 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_142_0_line_5 |  | 3 | 6 | 0.06549 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_142_0_line_6 |  | 4 | 47 | 0.14614 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_142_0_line_7 |  | 5 | 51 | 0.066849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_142_0_line_8 |  | 7 | 8 | 0.069813 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_142_0_line_9 |  | 8 | 9 | 0.032457 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_142_0_line_10 |  | 8 | 10 | 0.11136 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
11 | MV_142_0_line_11 |  | 8 | 11 | 0.8152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_142_0_line_12 |  | 8 | 12 | 1.249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_142_0_line_13 |  | 9 | 13 | 0.10705 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_142_0_line_14 |  | 10 | 14 | 0.070979 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
15 | MV_142_0_line_15 |  | 11 | 15 | 0.37074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_142_0_line_16 |  | 11 | 16 | 0.085735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_142_0_line_17 |  | 11 | 17 | 0.061797 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_142_0_line_18 |  | 12 | 19 | 0.043615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_142_0_line_19 |  | 13 | 59 | 2.5145 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_142_0_line_20 |  | 15 | 18 | 0.025232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_142_0_line_21 |  | 16 | 29 | 0.02311 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_142_0_line_22 |  | 17 | 20 | 0.051876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_142_0_line_23 |  | 20 | 21 | 0.015906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_142_0_line_24 |  | 21 | 22 | 0.052097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_142_0_line_25 |  | 22 | 23 | 0.006908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_142_0_line_26 |  | 23 | 32 | 0.14224 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_142_0_line_27 |  | 24 | 25 | 0.038971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_142_0_line_28 |  | 24 | 26 | 0.11543 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_142_0_line_29 |  | 25 | 27 | 0.053468 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_142_0_line_30 |  | 26 | 31 | 0.063306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_142_0_line_31 |  | 26 | 30 | 0.12228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_142_0_line_32 |  | 27 | 28 | 0.082601 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_142_0_line_33 |  | 28 | 58 | 0.017631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_142_0_line_34 |  | 29 | 30 | 0.078737 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_142_0_line_35 |  | 31 | 51 | 0.060932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_142_0_line_36 |  | 32 | 33 | 0.10995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_142_0_line_37 |  | 34 | 35 | 0.01355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_142_0_line_38 |  | 35 | 36 | 0.22918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_142_0_line_39 |  | 36 | 37 | 0.050575 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_142_0_line_40 |  | 37 | 41 | 0.10345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_142_0_line_41 |  | 38 | 39 | 0.12357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_142_0_line_42 |  | 39 | 40 | 0.16104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_142_0_line_43 |  | 40 | 44 | 0.13804 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_142_0_line_44 |  | 40 | 45 | 0.03276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_142_0_line_45 |  | 41 | 42 | 0.066359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_142_0_line_46 |  | 42 | 43 | 0.12572 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_142_0_line_47 |  | 43 | 47 | 0.12632 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_142_0_line_48 |  | 44 | 46 | 0.099843 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_142_0_line_49 |  | 45 | 50 | 0.054319 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_142_0_line_50 |  | 46 | 52 | 0.030784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_142_0_line_51 |  | 48 | 49 | 0.084588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_142_0_line_52 |  | 49 | 50 | 0.061692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_142_0_line_53 |  | 52 | 53 | 0.23646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_142_0_line_54 |  | 53 | 56 | 0.15674 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_142_0_line_55 |  | 53 | 54 | 0.37901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_142_0_line_56 |  | 54 | 55 | 0.060749 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_142_0_line_57 |  | 56 | 57 | 0.028074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_142_0_line_58 |  | 57 | 58 | 0.11566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_142_0_line_59 |  | 59 | 60 | 2.4138 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_142_0_line_60 |  | 60 | 65 | 1.0954 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_142_0_line_61 |  | 61 | 62 | 0.008325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_142_0_line_62 |  | 62 | 63 | 0.10162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_142_0_line_63 |  | 63 | 64 | 0.13638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_142_0_line_64 |  | 64 | 74 | 0.12729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_142_0_line_65 |  | 65 | 66 | 0.1116 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_142_0_line_66 |  | 65 | 67 | 0.099804 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_142_0_line_67 |  | 67 | 68 | 0.088904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_142_0_line_68 |  | 68 | 69 | 0.05534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_142_0_line_69 |  | 69 | 76 | 0.074774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_142_0_line_70 |  | 70 | 71 | 0.018507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_142_0_line_71 |  | 71 | 72 | 0.20165 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_142_0_line_72 |  | 71 | 73 | 0.47382 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_142_0_line_73 |  | 72 | 76 | 0.13982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_142_0_line_74 |  | 72 | 77 | 0.086158 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_142_0_line_75 |  | 72 | 74 | 0.2274 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_142_0_line_76 |  | 73 | 80 | 0.046697 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_142_0_line_77 |  | 74 | 75 | 0.0456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_142_0_line_78 |  | 75 | 78 | 0.34006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_142_0_line_79 |  | 75 | 79 | 0.02706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_142_0_line_80 |  | 78 | 82 | 0.063147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_142_0_line_81 |  | 80 | 81 | 0.22593 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_142_0_trafo_51 | 25 MVA 110/20 kV | 83 | 14 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2678309.3791 | 1202506.7415
1 | 2678301.6628 | 1202567.0336
2 | 2678260.8106 | 1202639.4993
3 | 2678533.4171 | 1202559.8706
4 | 2678241.6095 | 1202644.7067
5 | 2678561.8234 | 1202550.9384
6 | 2678509.2468 | 1202499.0038
7 | 2679485.0973 | 1201809.2611
8 | 2679549.6311 | 1201799.3691
9 | 2679567.4087 | 1201772.1887
10 | 2679590.9675 | 1201811.5494
11 | 2678926.8855 | 1202223.1884
12 | 2680026.6564 | 1201782.7054
13 | 2679667.8665 | 1201735.1928
14 | 2679580.4339 | 1201881.742
15 | 2678992.199 | 1201923.7528
16 | 2678872.2791 | 1202288.6417
17 | 2678865.0937 | 1202222.4054
18 | 2679012.2752 | 1201909.0011
19 | 2680070.3505 | 1201784.7475
20 | 2678834.8703 | 1202180.8806
21 | 2678830.6736 | 1202165.5378
22 | 2678821.0751 | 1202116.5806
23 | 2678821.3641 | 1202109.6801
24 | 2678690.1377 | 1202346.5878
25 | 2678655.3131 | 1202364.2737
26 | 2678726.2217 | 1202456.2317
27 | 2678622.9581 | 1202339.499
28 | 2678556.676 | 1202290.2076
29 | 2678853.8906 | 1202302.4966
30 | 2678806.7606 | 1202365.5699
31 | 2678675.3995 | 1202494.1639
32 | 2678726.8409 | 1202003.3897
33 | 2678635.0299 | 1201981.0558
34 | 2677448.8567 | 1202727.6973
35 | 2677462.3608 | 1202729.2066
36 | 2677690.5209 | 1202750.8267
37 | 2677740.9599 | 1202754.5295
38 | 2677801.3881 | 1202632.8956
39 | 2677828.0017 | 1202514.9686
40 | 2677777.4917 | 1202366.9629
41 | 2677842.9249 | 1202735.7564
42 | 2677846.8732 | 1202670.4893
43 | 2677969.1734 | 1202641.3657
44 | 2677907.7047 | 1202331.4815
45 | 2677745.7751 | 1202375.311
46 | 2677991.4066 | 1202277.0519
47 | 2678095.4703 | 1202643.6831
48 | 2677570.2983 | 1202472.6468
49 | 2677643.7277 | 1202430.4185
50 | 2677698.4093 | 1202401.9004
51 | 2678624.7899 | 1202528.1301
52 | 2678016.6889 | 1202259.5585
53 | 2678241.9987 | 1202290.8683
54 | 2678258.4047 | 1202050.0772
55 | 2678197.9332 | 1202055.8781
56 | 2678398.6426 | 1202296.4916
57 | 2678426.5071 | 1202300.4931
58 | 2678539.139 | 1202287.9868
59 | 2678867.8445 | 1199351.3171
60 | 2681195.2484 | 1199991.386
61 | 2681872.0778 | 1201438.6079
62 | 2681874.2281 | 1201430.5656
63 | 2681797.4621 | 1201390.8782
64 | 2681713.0031 | 1201308.6153
65 | 2681342.2336 | 1201076.8337
66 | 2681336.4607 | 1201171.4925
67 | 2681440.5701 | 1201059.7843
68 | 2681522.2082 | 1201068.714
69 | 2681575.9893 | 1201082.2564
70 | 2681947.8847 | 1201141.9929
71 | 2681952.6331 | 1201159.8804
72 | 2681778.3779 | 1201153.5005
73 | 2682300.1123 | 1201200.4698
74 | 2681648.3472 | 1201244.8804
75 | 2681619.6533 | 1201245.0774
76 | 2681648.2811 | 1201102.145
77 | 2681762.5537 | 1201068.8084
78 | 2681412.8276 | 1201359.2729
79 | 2681603.2838 | 1201223.5514
80 | 2682341.1611 | 1201222.9494
81 | 2682456.9713 | 1201416.9355
82 | 2681443.0605 | 1201407.5041
83 | 2679580.4339 | 1201881.742

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99476 | 0.016909 | 0.13899 | 0.067317
1 | 0.99477 | 0.016797 | 0 | 0
2 | 0.99465 | 0.017825 | 0 | 0
3 | 0.99505 | 0.014487 | 0 | 0
4 | 0.99463 | 0.017973 | 0.14011 | 0.067857
5 | 0.99508 | 0.014205 | 0.11555 | 0.055962
6 | 0.99504 | 0.014415 | 0.090185 | 0.043679
7 | 0.99931 | -0.01391 | 0.11313 | 0.054789
8 | 0.99932 | -0.014001 | 0 | 0
9 | 0.99925 | -0.013481 | 0 | 0
10 | 0.99961 | -0.010493 | 0 | 0
11 | 0.99633 | 0.0093205 | 0 | 0
12 | 0.9991 | -0.013094 | 0 | 0
13 | 0.99892 | -0.016128 | 0.073994 | 0.035837
14 | 1 | 0 | -4.8221 | -2.1386
15 | 0.99629 | 0.0096551 | 0 | 0
16 | 0.99608 | 0.011357 | 0 | 0
17 | 0.99628 | 0.0089534 | 0.10444 | 0.050582
18 | 0.99628 | 0.0096855 | 0.10148 | 0.049147
19 | 0.99909 | -0.01302 | 0.14543 | 0.070435
20 | 0.99626 | 0.0091504 | 0.11568 | 0.056026
21 | 0.99625 | 0.0091894 | 0 | 0
22 | 0.99624 | 0.00932 | 0 | 0
23 | 0.99624 | 0.0093376 | 0.10238 | 0.049586
24 | 0.99512 | 0.010229 | 0.12639 | 0.061215
25 | 0.99507 | 0.010555 | 0 | 0
26 | 0.99534 | 0.012044 | 0 | 0
27 | 0.99501 | 0.011005 | 0 | 0
28 | 0.99487 | 0.0098494 | 0.11928 | 0.05777
29 | 0.99601 | 0.011908 | 0.1563 | 0.075701
30 | 0.99568 | 0.0093435 | 0 | 0
31 | 0.99525 | 0.012829 | 0.14744 | 0.07141
32 | 0.9962 | 0.0090892 | 0 | 0
33 | 0.99619 | 0.009245 | 0.12447 | 0.060282
34 | 0.9942 | 0.01639 | 0.15125 | 0.073254
35 | 0.9942 | 0.016365 | 0 | 0
36 | 0.99425 | 0.01599 | 0 | 0
37 | 0.99426 | 0.016109 | 0.11726 | 0.056791
38 | 0.99422 | 0.011746 | 0.11398 | 0.055205
39 | 0.99424 | 0.011587 | 0 | 0
40 | 0.99426 | 0.011415 | 0 | 0
41 | 0.9943 | 0.015819 | 0 | 0
42 | 0.99432 | 0.015642 | 0 | 0
43 | 0.99439 | 0.016162 | 0.13236 | 0.064103
44 | 0.99433 | 0.010931 | 0 | 0
45 | 0.99425 | 0.011503 | 0.11134 | 0.053926
46 | 0.99437 | 0.0106 | 0.12017 | 0.0582
47 | 0.99448 | 0.016889 | 0.13465 | 0.065215
48 | 0.99422 | 0.011615 | 0.13138 | 0.06363
49 | 0.99423 | 0.011486 | 0 | 0
50 | 0.99424 | 0.011399 | 0 | 0
51 | 0.99517 | 0.013482 | 0 | 0
52 | 0.99439 | 0.010456 | 0 | 0
53 | 0.99453 | 0.0093985 | 0 | 0
54 | 0.99447 | 0.0099069 | 0 | 0
55 | 0.99445 | 0.0098064 | 0.1351 | 0.06543
56 | 0.99471 | 0.011003 | 0.16046 | 0.077713
57 | 0.99474 | 0.010799 | 0 | 0
58 | 0.99486 | 0.0099735 | 0 | 0
59 | 0.99141 | -0.076184 | 0.086825 | 0.042051
60 | 0.9846 | -0.13147 | 0.10382 | 0.050283
61 | 0.98085 | -0.15204 | 0.10634 | 0.051501
62 | 0.98085 | -0.15205 | 0 | 0
63 | 0.98087 | -0.15217 | 0 | 0
64 | 0.98088 | -0.15232 | 0.075234 | 0.036438
65 | 0.98174 | -0.15519 | 0.14275 | 0.069139
66 | 0.98172 | -0.15506 | 0.10035 | 0.0486
67 | 0.98152 | -0.15702 | 0 | 0
68 | 0.9814 | -0.15609 | 0 | 0
69 | 0.98132 | -0.1555 | 0.073876 | 0.03578
70 | 0.98091 | -0.15236 | 0.16422 | 0.079537
71 | 0.98091 | -0.1524 | 0 | 0
72 | 0.98103 | -0.15337 | 0 | 0
73 | 0.98073 | -0.15083 | 0 | 0
74 | 0.98091 | -0.15254 | 0 | 0
75 | 0.9809 | -0.15244 | 0 | 0
76 | 0.98122 | -0.15477 | 0 | 0
77 | 0.98101 | -0.15354 | 0.1566 | 0.075845
78 | 0.98085 | -0.15204 | 0 | 0
79 | 0.9809 | -0.15241 | 0.10464 | 0.050677
80 | 0.98071 | -0.15065 | 0.14398 | 0.069732
81 | 0.98064 | -0.15111 | 0.15928 | 0.077145
82 | 0.98084 | -0.15194 | 0.1252 | 0.060635
83 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13899 | -0.067317 | 0.13899 | 0.065693 | 1.8349e-06 | -0.0016237 | 0.0044817 | 0.0044613 | 0.0044817 | 0.99476 | 0.016909 | 0.99477 | 0.016797 | 2.0371
1 | 0.67588 | 0.31331 | -0.67579 | -0.31658 | 8.7068e-05 | -0.0032648 | 0.021618 | 0.021659 | 0.021659 | 0.99477 | 0.016797 | 0.99465 | 0.017825 | 9.8449
2 | -0.81488 | -0.37901 | 0.81512 | 0.37276 | 0.00024219 | -0.0062505 | 0.02608 | 0.026003 | 0.02608 | 0.99477 | 0.016797 | 0.99505 | 0.014487 | 11.8544
3 | 0.67579 | 0.31658 | -0.67578 | -0.31704 | 1.2429e-05 | -0.00046498 | 0.021659 | 0.021665 | 0.021665 | 0.99465 | 0.017825 | 0.99463 | 0.017973 | 9.8475
4 | -0.9053 | -0.41636 | 0.90534 | 0.41567 | 3.3125e-05 | -0.00069231 | 0.028908 | 0.0289 | 0.028908 | 0.99505 | 0.014487 | 0.99508 | 0.014205 | 13.1402
5 | 0.090186 | 0.043602 | -0.090185 | -0.043679 | 9.8581e-07 | -7.6792e-05 | 0.0029062 | 0.0029071 | 0.0029071 | 0.99505 | 0.014487 | 0.99504 | 0.014415 | 1.3843
6 | 0.53567 | 0.24919 | -0.5356 | -0.24931 | 7.6565e-05 | -0.00012461 | 0.017147 | 0.017149 | 0.017149 | 0.99463 | 0.017973 | 0.99448 | 0.016889 | 8.1662
7 | -1.0209 | -0.47163 | 1.021 | 0.47008 | 9.4926e-05 | -0.0015524 | 0.032624 | 0.032604 | 0.032624 | 0.99508 | 0.014205 | 0.99517 | 0.013482 | 14.829
8 | -0.11313 | -0.054789 | 0.11313 | 0.053125 | 1.2217e-06 | -0.0016642 | 0.003631 | 0.0036103 | 0.003631 | 0.99931 | -0.01391 | 0.99932 | -0.014001 | 1.6505
9 | 1.643 | 0.73812 | -1.6429 | -0.73886 | 0.00011732 | -0.00073904 | 0.05203 | 0.052039 | 0.052039 | 0.99932 | -0.014001 | 0.99925 | -0.013481 | 23.6543
10 | -4.8054 | -2.1294 | 4.8066 | 2.1265 | 0.0012396 | -0.0029155 | 0.15183 | 0.15179 | 0.15183 | 0.99932 | -0.014001 | 0.99961 | -0.010493 | 41.9426
11 | 2.9038 | 1.2985 | -2.8946 | -1.3152 | 0.0092119 | -0.016647 | 0.091888 | 0.092118 | 0.092118 | 0.99932 | -0.014001 | 0.99633 | 0.0093205 | 41.872
12 | 0.14547 | 0.039633 | -0.14543 | -0.069396 | 3.3578e-05 | -0.029763 | 0.0043553 | 0.0046559 | 0.0046559 | 0.99932 | -0.014001 | 0.9991 | -0.013094 | 2.1163
13 | 1.6429 | 0.73886 | -1.6423 | -0.73866 | 0.00051655 | 0.00019598 | 0.052039 | 0.052041 | 0.052041 | 0.99925 | -0.013481 | 0.99892 | -0.016128 | 24.7814
14 | -4.8066 | -2.1265 | 4.8081 | 2.1281 | 0.0015012 | 0.0016279 | 0.15179 | 0.15179 | 0.15179 | 0.99961 | -0.010493 | 1 | 0 | 43.3679
15 | 0.10148 | 0.039764 | -0.10148 | -0.04855 | 5.0891e-06 | -0.0087851 | 0.003158 | 0.0032595 | 0.0032595 | 0.99633 | 0.0093205 | 0.99629 | 0.0096551 | 1.4816
16 | 2.3461 | 1.0647 | -2.3455 | -1.0666 | 0.00063801 | -0.0018423 | 0.074649 | 0.074673 | 0.074673 | 0.99633 | 0.0093205 | 0.99608 | 0.011357 | 33.9423
17 | 0.44701 | 0.21065 | -0.44699 | -0.2107 | 2.2571e-05 | -5.9091e-05 | 0.014317 | 0.014318 | 0.014318 | 0.99633 | 0.0093205 | 0.99628 | 0.0089534 | 6.8183
18 | 0.14543 | 0.069396 | -0.14543 | -0.070435 | 1.2657e-06 | -0.0010391 | 0.0046559 | 0.004669 | 0.004669 | 0.9991 | -0.013094 | 0.99909 | -0.01302 | 2.1223
19 | 1.5683 | 0.70282 | -1.5573 | -0.69887 | 0.011059 | 0.0039541 | 0.049666 | 0.049701 | 0.049701 | 0.99892 | -0.016128 | 0.99141 | -0.076184 | 23.6673
20 | 0.10148 | 0.04855 | -0.10148 | -0.049147 | 3.587e-07 | -0.00059787 | 0.0032595 | 0.003267 | 0.003267 | 0.99629 | 0.0096551 | 0.99628 | 0.0096855 | 1.485
21 | 2.3455 | 1.0666 | -2.3453 | -1.0671 | 0.00017205 | -0.00049639 | 0.074673 | 0.07468 | 0.07468 | 0.99608 | 0.011357 | 0.99601 | 0.011908 | 33.9453
22 | 0.34255 | 0.16012 | -0.34254 | -0.16135 | 8.3248e-06 | -0.0012269 | 0.010956 | 0.010971 | 0.010971 | 0.99628 | 0.0089534 | 0.99626 | 0.0091504 | 4.987
23 | 0.22686 | 0.10532 | -0.22686 | -0.1057 | 1.116e-06 | -0.0003766 | 0.0072474 | 0.007252 | 0.007252 | 0.99626 | 0.0091504 | 0.99625 | 0.0091894 | 3.2964
24 | 0.22686 | 0.1057 | -0.22686 | -0.10693 | 3.6654e-06 | -0.0012335 | 0.007252 | 0.0072672 | 0.0072672 | 0.99625 | 0.0091894 | 0.99624 | 0.00932 | 3.3033
25 | 0.22686 | 0.10693 | -0.22686 | -0.1071 | 4.8717e-07 | -0.00016355 | 0.0072672 | 0.0072692 | 0.0072692 | 0.99624 | 0.00932 | 0.99624 | 0.0093376 | 3.3042
26 | 0.12447 | 0.057512 | -0.12447 | -0.057678 | 4.0028e-06 | -0.00016602 | 0.0039732 | 0.0039752 | 0.0039752 | 0.99624 | 0.0093376 | 0.9962 | 0.0090892 | 1.893
27 | 0.89231 | 0.39389 | -0.89226 | -0.3948 | 4.1668e-05 | -0.00090901 | 0.028295 | 0.028306 | 0.028306 | 0.99512 | 0.010229 | 0.99507 | 0.010555 | 12.8662
28 | -1.0187 | -0.45511 | 1.0189 | 0.4551 | 0.00021544 | -1.545e-06 | 0.032367 | 0.032365 | 0.032367 | 0.99512 | 0.010229 | 0.99534 | 0.012044 | 15.4127
29 | 0.89226 | 0.3948 | -0.89221 | -0.39605 | 5.722e-05 | -0.001247 | 0.028306 | 0.028321 | 0.028321 | 0.99507 | 0.010555 | 0.99501 | 0.011005 | 12.873
30 | 1.1686 | 0.53861 | -1.1685 | -0.54007 | 0.00011777 | -0.0014624 | 0.03732 | 0.037338 | 0.037338 | 0.99534 | 0.012044 | 0.99525 | 0.012829 | 16.9718
31 | -2.1875 | -0.99371 | 2.1883 | 0.99105 | 0.00079226 | -0.0026583 | 0.069684 | 0.069649 | 0.069684 | 0.99534 | 0.012044 | 0.99568 | 0.0093435 | 31.6743
32 | 0.89221 | 0.39605 | -0.89209 | -0.39607 | 0.00011804 | -2.3676e-05 | 0.028321 | 0.028322 | 0.028322 | 0.99501 | 0.011005 | 0.99487 | 0.0098494 | 13.4865
33 | 0.77281 | 0.3383 | -0.77279 | -0.33871 | 1.4106e-05 | -0.00041246 | 0.024478 | 0.024483 | 0.024483 | 0.99487 | 0.0098494 | 0.99486 | 0.0099735 | 11.1288
34 | 2.189 | 0.99139 | -2.1883 | -0.99105 | 0.00068051 | 0.00033303 | 0.069648 | 0.069649 | 0.069649 | 0.99601 | 0.011908 | 0.99568 | 0.0093435 | 33.1661
35 | 1.0211 | 0.46866 | -1.021 | -0.47008 | 8.6427e-05 | -0.0014153 | 0.032587 | 0.032604 | 0.032604 | 0.99525 | 0.012829 | 0.99517 | 0.013482 | 14.8202
36 | 0.12447 | 0.057678 | -0.12447 | -0.060282 | 2.3382e-06 | -0.0026045 | 0.0039752 | 0.0040076 | 0.0040076 | 0.9962 | 0.0090892 | 0.99619 | 0.009245 | 1.8216
37 | -0.15125 | -0.073254 | 0.15125 | 0.072934 | 4.3037e-07 | -0.00031965 | 0.0048797 | 0.0048756 | 0.0048797 | 0.9942 | 0.01639 | 0.9942 | 0.016365 | 2.218
38 | -0.15125 | -0.072934 | 0.15126 | 0.067527 | 7.1732e-06 | -0.0054068 | 0.0048756 | 0.0048095 | 0.0048756 | 0.9942 | 0.016365 | 0.99425 | 0.01599 | 2.2162
39 | -0.15126 | -0.067527 | 0.15126 | 0.067469 | 2.084e-06 | -5.8379e-05 | 0.0048095 | 0.0048088 | 0.0048095 | 0.99425 | 0.01599 | 0.99426 | 0.016109 | 2.2902
40 | -0.26852 | -0.12426 | 0.26853 | 0.12182 | 1.0157e-05 | -0.0024389 | 0.0085905 | 0.008561 | 0.0085905 | 0.99426 | 0.016109 | 0.9943 | 0.015819 | 3.9048
41 | -0.11398 | -0.055205 | 0.11399 | 0.052289 | 2.2086e-06 | -0.0029157 | 0.0036773 | 0.0036412 | 0.0036773 | 0.99422 | 0.011746 | 0.99424 | 0.011587 | 1.6715
42 | -0.11399 | -0.052289 | 0.11399 | 0.048489 | 2.815e-06 | -0.0038001 | 0.0036412 | 0.0035965 | 0.0036412 | 0.99424 | 0.011587 | 0.99426 | 0.011415 | 1.6551
43 | -0.35672 | -0.16176 | 0.35674 | 0.15851 | 2.3751e-05 | -0.0032513 | 0.011372 | 0.011333 | 0.011372 | 0.99426 | 0.011415 | 0.99433 | 0.010931 | 5.1692
44 | 0.24273 | 0.11327 | -0.24273 | -0.11404 | 2.6484e-06 | -0.00077244 | 0.0077771 | 0.0077866 | 0.0077866 | 0.99426 | 0.011415 | 0.99425 | 0.011503 | 3.5394
45 | -0.26853 | -0.12182 | 0.26854 | 0.12026 | 6.4785e-06 | -0.0015645 | 0.008561 | 0.0085423 | 0.008561 | 0.9943 | 0.015819 | 0.99432 | 0.015642 | 3.8914
46 | -0.26854 | -0.12026 | 0.26855 | 0.12012 | 1.6342e-05 | -0.00013816 | 0.0085423 | 0.0085406 | 0.0085423 | 0.99432 | 0.015642 | 0.99439 | 0.016162 | 4.0678
47 | -0.40091 | -0.18422 | 0.40094 | 0.1841 | 3.6918e-05 | -0.000126 | 0.012808 | 0.012807 | 0.012808 | 0.99439 | 0.016162 | 0.99448 | 0.016889 | 6.0993
48 | -0.35674 | -0.15851 | 0.35676 | 0.15616 | 1.7079e-05 | -0.0023519 | 0.011333 | 0.011306 | 0.011333 | 0.99433 | 0.010931 | 0.99437 | 0.0106 | 5.1516
49 | 0.13139 | 0.060116 | -0.13138 | -0.060179 | 1.7035e-06 | -6.3035e-05 | 0.0041951 | 0.0041958 | 0.0041958 | 0.99425 | 0.011503 | 0.99424 | 0.011399 | 1.998
50 | -0.47693 | -0.21436 | 0.47694 | 0.21363 | 9.4644e-06 | -0.00072396 | 0.01518 | 0.015171 | 0.01518 | 0.99437 | 0.0106 | 0.99439 | 0.010456 | 6.8999
51 | -0.13138 | -0.06363 | 0.13138 | 0.061635 | 2.0167e-06 | -0.0019958 | 0.0042385 | 0.0042136 | 0.0042385 | 0.99422 | 0.011615 | 0.99423 | 0.011486 | 1.9266
52 | -0.13138 | -0.061635 | 0.13138 | 0.060179 | 1.456e-06 | -0.0014556 | 0.0042136 | 0.0041958 | 0.0042136 | 0.99423 | 0.011486 | 0.99424 | 0.011399 | 1.9153
53 | -0.47694 | -0.21363 | 0.47701 | 0.20807 | 7.2343e-05 | -0.005562 | 0.015171 | 0.015106 | 0.015171 | 0.99439 | 0.010456 | 0.99453 | 0.0093985 | 6.896
54 | -0.61212 | -0.26448 | 0.61222 | 0.26436 | 0.00010461 | -0.00011959 | 0.019355 | 0.019353 | 0.019355 | 0.99453 | 0.0093985 | 0.99471 | 0.011003 | 9.2167
55 | 0.13511 | 0.056412 | -0.1351 | -0.065359 | 9.3619e-06 | -0.0089472 | 0.0042498 | 0.0043565 | 0.0043565 | 0.99453 | 0.0093985 | 0.99447 | 0.0099069 | 1.9802
56 | 0.1351 | 0.065359 | -0.1351 | -0.06543 | 2.0546e-06 | -7.0434e-05 | 0.0043565 | 0.0043574 | 0.0043574 | 0.99447 | 0.0099069 | 0.99445 | 0.0098064 | 2.0749
57 | -0.77268 | -0.34207 | 0.7727 | 0.34142 | 2.2532e-05 | -0.00065657 | 0.024523 | 0.024515 | 0.024523 | 0.99471 | 0.011003 | 0.99474 | 0.010799 | 11.1468
58 | -0.7727 | -0.34142 | 0.77279 | 0.33871 | 9.2679e-05 | -0.0027054 | 0.024515 | 0.024483 | 0.024515 | 0.99474 | 0.010799 | 0.99486 | 0.0099735 | 11.1433
59 | 1.4705 | 0.65682 | -1.461 | -0.6537 | 0.009464 | 0.003115 | 0.046894 | 0.046927 | 0.046927 | 0.99141 | -0.076184 | 0.9846 | -0.13147 | 22.3462
60 | 1.3572 | 0.60342 | -1.3535 | -0.60236 | 0.0037021 | 0.0010549 | 0.043547 | 0.043562 | 0.043562 | 0.9846 | -0.13147 | 0.98174 | -0.15519 | 20.7437
61 | -0.10634 | -0.051501 | 0.10634 | 0.05131 | 1.343e-07 | -0.00019119 | 0.0034773 | 0.0034749 | 0.0034773 | 0.98085 | -0.15204 | 0.98085 | -0.15205 | 1.5806
62 | -0.10634 | -0.05131 | 0.10634 | 0.048976 | 1.6241e-06 | -0.0023337 | 0.0034749 | 0.0034456 | 0.0034749 | 0.98085 | -0.15205 | 0.98087 | -0.15217 | 1.5795
63 | -0.10634 | -0.048976 | 0.10634 | 0.045844 | 2.1377e-06 | -0.0031323 | 0.0034456 | 0.003408 | 0.0034456 | 0.98087 | -0.15217 | 0.98088 | -0.15232 | 1.5662
64 | -0.18157 | -0.082282 | 0.18158 | 0.079359 | 5.8137e-06 | -0.0029224 | 0.0058668 | 0.0058318 | 0.0058668 | 0.98088 | -0.15232 | 0.98091 | -0.15254 | 2.6667
65 | 0.10035 | 0.046032 | -0.10035 | -0.0486 | 1.5856e-06 | -0.0025677 | 0.0032463 | 0.0032785 | 0.0032785 | 0.98174 | -0.15519 | 0.98172 | -0.15506 | 1.4902
66 | 1.1104 | 0.48719 | -1.1101 | -0.48717 | 0.00022606 | 2.6789e-05 | 0.035655 | 0.035656 | 0.035656 | 0.98174 | -0.15519 | 0.98152 | -0.15702 | 16.979
67 | 1.1101 | 0.48717 | -1.11 | -0.48917 | 0.00015099 | -0.0019999 | 0.035656 | 0.03568 | 0.03568 | 0.98152 | -0.15702 | 0.9814 | -0.15609 | 16.2182
68 | 1.11 | 0.48917 | -1.1099 | -0.49041 | 9.4093e-05 | -0.0012446 | 0.03568 | 0.035695 | 0.035695 | 0.9814 | -0.15609 | 0.98132 | -0.1555 | 16.2251
69 | 1.036 | 0.45463 | -1.0359 | -0.45632 | 0.00011064 | -0.0016862 | 0.033282 | 0.033302 | 0.033302 | 0.98132 | -0.1555 | 0.98122 | -0.15477 | 15.1375
70 | -0.16422 | -0.079537 | 0.16422 | 0.079112 | 7.1174e-07 | -0.00042495 | 0.00537 | 0.0053645 | 0.00537 | 0.98091 | -0.15236 | 0.98091 | -0.1524 | 2.4409
71 | -0.46756 | -0.2138 | 0.46763 | 0.20919 | 6.1399e-05 | -0.0046149 | 0.01513 | 0.015074 | 0.01513 | 0.98091 | -0.1524 | 0.98103 | -0.15337 | 6.8775
72 | 0.30334 | 0.13469 | -0.30328 | -0.14555 | 6.1168e-05 | -0.010865 | 0.0097675 | 0.0099019 | 0.0099019 | 0.98091 | -0.1524 | 0.98073 | -0.15083 | 4.5008
73 | -1.0357 | -0.45947 | 1.0359 | 0.45632 | 0.00020725 | -0.003152 | 0.033341 | 0.033302 | 0.033341 | 0.98103 | -0.15337 | 0.98122 | -0.15477 | 15.1549
74 | 0.1566 | 0.075748 | -0.1566 | -0.075845 | 4.0234e-06 | -9.6468e-05 | 0.0051189 | 0.0051202 | 0.0051202 | 0.98103 | -0.15337 | 0.98101 | -0.15354 | 2.4382
75 | 0.41148 | 0.17454 | -0.41142 | -0.17974 | 5.2754e-05 | -0.005209 | 0.013152 | 0.013213 | 0.013213 | 0.98103 | -0.15337 | 0.98091 | -0.15254 | 6.0059
76 | 0.30328 | 0.14555 | -0.30327 | -0.14662 | 6.1207e-06 | -0.0010705 | 0.0099019 | 0.0099156 | 0.0099156 | 0.98073 | -0.15083 | 0.98071 | -0.15065 | 4.5071
77 | 0.22984 | 0.10038 | -0.22984 | -0.10143 | 3.3222e-06 | -0.0010466 | 0.0073811 | 0.0073935 | 0.0073935 | 0.98091 | -0.15254 | 0.9809 | -0.15244 | 3.3607
78 | 0.1252 | 0.051376 | -0.1252 | -0.059185 | 7.3654e-06 | -0.0078095 | 0.0039829 | 0.0040757 | 0.0040757 | 0.9809 | -0.15244 | 0.98085 | -0.15204 | 1.8526
79 | 0.10464 | 0.050056 | -0.10464 | -0.050677 | 4.2194e-07 | -0.00062152 | 0.0034136 | 0.0034216 | 0.0034216 | 0.9809 | -0.15244 | 0.9809 | -0.15241 | 1.5553
80 | 0.1252 | 0.059185 | -0.1252 | -0.060635 | 1.4067e-06 | -0.0014501 | 0.0040757 | 0.0040941 | 0.0040941 | 0.98085 | -0.15204 | 0.98084 | -0.15194 | 1.861
81 | 0.1593 | 0.076892 | -0.15928 | -0.077145 | 1.0919e-05 | -0.00025255 | 0.0052066 | 0.0052099 | 0.0052099 | 0.98071 | -0.15065 | 0.98064 | -0.15111 | 2.4809

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 4.9217 | 2.1868

## res_load
| p_mw | q_mvar
0 | 0.13899 | 0.067317
1 | 0.14011 | 0.067857
2 | 0.11555 | 0.055962
3 | 0.090185 | 0.043679
4 | 0.11313 | 0.054789
5 | 0.073994 | 0.035837
6 | 0.099536 | 0.048208
7 | 0.10444 | 0.050582
8 | 0.10148 | 0.049147
9 | 0.14543 | 0.070435
10 | 0.11568 | 0.056026
11 | 0.10238 | 0.049586
12 | 0.12639 | 0.061215
13 | 0.11928 | 0.05777
14 | 0.1563 | 0.075701
15 | 0.14744 | 0.07141
16 | 0.12447 | 0.060282
17 | 0.15125 | 0.073254
18 | 0.11726 | 0.056791
19 | 0.11398 | 0.055205
20 | 0.13236 | 0.064103
21 | 0.11134 | 0.053926
22 | 0.12017 | 0.0582
23 | 0.13465 | 0.065215
24 | 0.13138 | 0.06363
25 | 0.1351 | 0.06543
26 | 0.16046 | 0.077713
27 | 0.086825 | 0.042051
28 | 0.10382 | 0.050283
29 | 0.10634 | 0.051501
30 | 0.075234 | 0.036438
31 | 0.14275 | 0.069139
32 | 0.10035 | 0.0486
33 | 0.073876 | 0.03578
34 | 0.16422 | 0.079537
35 | 0.1566 | 0.075845
36 | 0.10464 | 0.050677
37 | 0.14398 | 0.069732
38 | 0.15928 | 0.077145
39 | 0.1252 | 0.060635

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1