## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_143_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_143_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_143_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_143_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_143_0_node_7 | 20 | n |  | TRUE
5 | bus_MV_143_0_node_9 | 20 | n |  | TRUE
6 | bus_MV_143_0_node_140 | 20 | n |  | TRUE
7 | bus_MV_143_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_143_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_143_0_node_118 | 20 | n |  | TRUE
10 | bus_MV_143_0_node_6 | 20 | n |  | TRUE
11 | bus_MV_143_0_node_11 | 20 | n |  | TRUE
12 | bus_MV_143_0_node_16 | 20 | n |  | TRUE
13 | bus_MV_143_0_node_158 | 20 | n |  | TRUE
14 | bus_MV_143_0_node_159 | 20 | n |  | TRUE
15 | bus_MV_143_0_node_8 | 20 | n |  | TRUE
16 | bus_MV_143_0_node_12 | 20 | n |  | TRUE
17 | bus_MV_143_0_node_10 | 20 | n |  | TRUE
18 | bus_MV_143_0_node_15 | 20 | n |  | TRUE
19 | bus_MV_143_0_node_13 | 20 | n |  | TRUE
20 | bus_MV_143_0_node_51 | 20 | n |  | TRUE
21 | bus_MV_143_0_node_52 | 20 | n |  | TRUE
22 | bus_MV_143_0_node_14 | 20 | n |  | TRUE
23 | bus_MV_143_0_node_53 | 20 | n |  | TRUE
24 | bus_MV_143_0_node_17 | 20 | n |  | TRUE
25 | bus_MV_143_0_node_18 | 20 | n |  | TRUE
26 | bus_MV_143_0_node_63 | 20 | n |  | TRUE
27 | bus_MV_143_0_node_19 | 20 | n |  | TRUE
28 | bus_MV_143_0_node_64 | 20 | n |  | TRUE
29 | bus_MV_143_0_node_61 | 20 | n |  | TRUE
30 | bus_MV_143_0_node_168 | 20 | n |  | TRUE
31 | bus_MV_143_0_node_20 | 20 | n |  | TRUE
32 | bus_MV_143_0_node_50 | 20 | n |  | TRUE
33 | bus_MV_143_0_node_22 | 20 | n |  | TRUE
34 | bus_MV_143_0_node_49 | 20 | n |  | TRUE
35 | bus_MV_143_0_node_23 | 20 | n |  | TRUE
36 | bus_MV_143_0_node_130 | 20 | n |  | TRUE
37 | bus_MV_143_0_node_59 | 20 | n |  | TRUE
38 | bus_MV_143_0_node_24 | 20 | n |  | TRUE
39 | bus_MV_143_0_node_66 | 20 | n |  | TRUE
40 | bus_MV_143_0_node_65 | 20 | n |  | TRUE
41 | bus_MV_143_0_node_46 | 20 | n |  | TRUE
42 | bus_MV_143_0_node_57 | 20 | n |  | TRUE
43 | bus_MV_143_0_node_139 | 20 | n |  | TRUE
44 | bus_MV_143_0_node_56 | 20 | n |  | TRUE
45 | bus_MV_143_0_node_67 | 20 | n |  | TRUE
46 | bus_MV_143_0_node_47 | 20 | n |  | TRUE
47 | bus_MV_143_0_node_25 | 20 | n |  | TRUE
48 | bus_MV_143_0_node_27 | 20 | n |  | TRUE
49 | bus_MV_143_0_node_31 | 20 | n |  | TRUE
50 | bus_MV_143_0_node_33 | 20 | n |  | TRUE
51 | bus_MV_143_0_node_34 | 20 | n |  | TRUE
52 | bus_MV_143_0_node_26 | 20 | n |  | TRUE
53 | bus_MV_143_0_node_29 | 20 | n |  | TRUE
54 | bus_MV_143_0_node_30 | 20 | n |  | TRUE
55 | bus_MV_143_0_node_28 | 20 | n |  | TRUE
56 | bus_MV_143_0_node_133 | 20 | n |  | TRUE
57 | bus_MV_143_0_node_132 | 20 | n |  | TRUE
58 | bus_MV_143_0_node_120 | 20 | n |  | TRUE
59 | bus_MV_143_0_node_119 | 20 | n |  | TRUE
60 | bus_MV_143_0_node_166 | 20 | n |  | TRUE
61 | bus_MV_143_0_node_121 | 20 | n |  | TRUE
62 | bus_MV_143_0_node_146 | 20 | n |  | TRUE
63 | bus_MV_143_0_node_35 | 20 | n |  | TRUE
64 | bus_MV_143_0_node_36 | 20 | n |  | TRUE
65 | bus_MV_143_0_node_122 | 20 | n |  | TRUE
66 | bus_MV_143_0_node_154 | 20 | n |  | TRUE
67 | bus_MV_143_0_node_155 | 20 | n |  | TRUE
68 | bus_MV_143_0_node_42 | 20 | n |  | TRUE
69 | bus_MV_143_0_node_127 | 20 | n |  | TRUE
70 | bus_MV_143_0_node_131 | 20 | n |  | TRUE
71 | bus_MV_143_0_node_126 | 20 | n |  | TRUE
72 | bus_MV_143_0_node_153 | 20 | n |  | TRUE
73 | bus_MV_143_0_node_129 | 20 | n |  | TRUE
74 | bus_MV_143_0_node_37 | 20 | n |  | TRUE
75 | bus_MV_143_0_node_38 | 20 | n |  | TRUE
76 | bus_MV_143_0_node_39 | 20 | n |  | TRUE
77 | bus_MV_143_0_node_41 | 20 | n |  | TRUE
78 | bus_MV_143_0_node_58 | 20 | n |  | TRUE
79 | bus_MV_143_0_node_165 | 20 | n |  | TRUE
80 | bus_MV_143_0_node_40 | 20 | n |  | TRUE
81 | bus_MV_143_0_node_141 | 20 | n |  | TRUE
82 | bus_MV_143_0_node_145 | 20 | n |  | TRUE
83 | bus_MV_143_0_node_48 | 20 | n |  | TRUE
84 | bus_MV_143_0_node_151 | 20 | n |  | TRUE
85 | bus_MV_143_0_node_45 | 20 | n |  | TRUE
86 | bus_MV_143_0_node_43 | 20 | n |  | TRUE
87 | bus_MV_143_0_node_44 | 20 | n |  | TRUE
88 | bus_MV_143_0_node_55 | 20 | n |  | TRUE
89 | bus_MV_143_0_node_54 | 20 | n |  | TRUE
90 | bus_MV_143_0_node_167 | 20 | n |  | TRUE
91 | bus_MV_143_0_node_164 | 20 | n |  | TRUE
92 | bus_MV_143_0_node_60 | 20 | n |  | TRUE
93 | bus_MV_143_0_node_62 | 20 | n |  | TRUE
94 | bus_MV_143_0_node_147 | 20 | n |  | TRUE
95 | bus_MV_143_0_node_148 | 20 | n |  | TRUE
96 | bus_MV_143_0_node_149 | 20 | n |  | TRUE
97 | bus_MV_143_0_node_150 | 20 | n |  | TRUE
98 | bus_MV_143_0_node_68 | 20 | n |  | TRUE
99 | bus_MV_143_0_node_69 | 20 | n |  | TRUE
100 | bus_MV_143_0_node_70 | 20 | n |  | TRUE
101 | bus_MV_143_0_node_156 | 20 | n |  | TRUE
102 | bus_MV_143_0_node_73 | 20 | n |  | TRUE
103 | bus_MV_143_0_node_71 | 20 | n |  | TRUE
104 | bus_MV_143_0_node_77 | 20 | n |  | TRUE
105 | bus_MV_143_0_node_79 | 20 | n |  | TRUE
106 | bus_MV_143_0_node_72 | 20 | n |  | TRUE
107 | bus_MV_143_0_node_109 | 20 | n |  | TRUE
108 | bus_MV_143_0_node_78 | 20 | n |  | TRUE
109 | bus_MV_143_0_node_81 | 20 | n |  | TRUE
110 | bus_MV_143_0_node_74 | 20 | n |  | TRUE
111 | bus_MV_143_0_node_76 | 20 | n |  | TRUE
112 | bus_MV_143_0_node_92 | 20 | n |  | TRUE
113 | bus_MV_143_0_node_161 | 20 | n |  | TRUE
114 | bus_MV_143_0_node_75 | 20 | n |  | TRUE
115 | bus_MV_143_0_node_162 | 20 | n |  | TRUE
116 | bus_MV_143_0_node_160 | 20 | n |  | TRUE
117 | bus_MV_143_0_node_110 | 20 | n |  | TRUE
118 | bus_MV_143_0_node_82 | 20 | n |  | TRUE
119 | bus_MV_143_0_node_88 | 20 | n |  | TRUE
120 | bus_MV_143_0_node_93 | 20 | n |  | TRUE
121 | bus_MV_143_0_node_91 | 20 | n |  | TRUE
122 | bus_MV_143_0_node_89 | 20 | n |  | TRUE
123 | bus_MV_143_0_node_94 | 20 | n |  | TRUE
124 | bus_MV_143_0_node_83 | 20 | n |  | TRUE
125 | bus_MV_143_0_node_84 | 20 | n |  | TRUE
126 | bus_MV_143_0_node_85 | 20 | n |  | TRUE
127 | bus_MV_143_0_node_86 | 20 | n |  | TRUE
128 | bus_MV_143_0_node_87 | 20 | n |  | TRUE
129 | bus_MV_143_0_node_136 | 20 | n |  | TRUE
130 | bus_MV_143_0_node_134 | 20 | n |  | TRUE
131 | bus_MV_143_0_node_152 | 20 | n |  | TRUE
132 | bus_MV_143_0_node_128 | 20 | n |  | TRUE
133 | bus_MV_143_0_node_137 | 20 | n |  | TRUE
134 | bus_MV_143_0_node_108 | 20 | n |  | TRUE
135 | bus_MV_143_0_node_125 | 20 | n |  | TRUE
136 | bus_MV_143_0_node_90 | 20 | n |  | TRUE
137 | bus_MV_143_0_node_144 | 20 | n |  | TRUE
138 | bus_MV_143_0_node_143 | 20 | n |  | TRUE
139 | bus_MV_143_0_node_142 | 20 | n |  | TRUE
140 | bus_MV_143_0_node_98 | 20 | n |  | TRUE
141 | bus_MV_143_0_node_135 | 20 | n |  | TRUE
142 | bus_MV_143_0_node_95 | 20 | n |  | TRUE
143 | bus_MV_143_0_node_96 | 20 | n |  | TRUE
144 | bus_MV_143_0_node_99 | 20 | n |  | TRUE
145 | bus_MV_143_0_node_101 | 20 | n |  | TRUE
146 | bus_MV_143_0_node_102 | 20 | n |  | TRUE
147 | bus_MV_143_0_node_100 | 20 | n |  | TRUE
148 | bus_MV_143_0_node_103 | 20 | n |  | TRUE
149 | bus_MV_143_0_node_104 | 20 | n |  | TRUE
150 | bus_MV_143_0_node_107 | 20 | n |  | TRUE
151 | bus_MV_143_0_node_138 | 20 | n |  | TRUE
152 | bus_MV_143_0_node_105 | 20 | n |  | TRUE
153 | bus_MV_143_0_node_117 | 20 | n |  | TRUE
154 | bus_MV_143_0_node_106 | 20 | n |  | TRUE
155 | bus_MV_143_0_node_157 | 20 | n |  | TRUE
156 | bus_MV_143_0_node_114 | 20 | n |  | TRUE
157 | bus_MV_143_0_node_111 | 20 | n |  | TRUE
158 | bus_MV_143_0_node_112 | 20 | n |  | TRUE
159 | bus_MV_143_0_node_124 | 20 | n |  | TRUE
160 | bus_MV_143_0_node_113 | 20 | n |  | TRUE
161 | bus_MV_143_0_node_115 | 20 | n |  | TRUE
162 | bus_MV_143_0_node_116 | 20 | n |  | TRUE
163 | bus_MV_143_0_node_123 | 20 | n |  | TRUE
164 | bus_MV_143_0_node_163 | 20 | n |  | TRUE
165 | bus_HV_143_0_node_166 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_143_0_load_0 | 0 | 0.093829 | 0.045443 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_143_0_load_140 | 6 | 0.12009 | 0.058162 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_143_0_load_5 | 8 | 0.16029 | 0.077632 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_143_0_load_118 | 9 | 0.098119 | 0.047521 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_143_0_load_6 | 10 | 0.1524 | 0.073809 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_143_0_load_16 | 12 | 0.077081 | 0.037332 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_143_0_load_159 | 14 | 0.11334 | 0.054891 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_143_0_load_8 | 15 | 0.11786 | 0.057084 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_143_0_load_10 | 17 | 0.13959 | 0.067605 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_143_0_load_51 | 20 | 0.12649 | 0.061261 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_143_0_load_52 | 21 | 0.1331 | 0.064462 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_143_0_load_14 | 22 | 0.12101 | 0.058607 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_143_0_load_17 | 24 | 0.32663 | 0.15819 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_143_0_load_64 | 28 | 0.32226 | 0.15608 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_143_0_load_168 | 30 | 0.41167 | 0.19938 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_143_0_load_50 | 32 | 0.086895 | 0.042085 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_143_0_load_49 | 34 | 0.34227 | 0.16577 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_143_0_load_130 | 36 | 0.085793 | 0.041552 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_143_0_load_59 | 37 | 0.37841 | 0.18327 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_143_0_load_65 | 40 | 0.27965 | 0.13544 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_143_0_load_57 | 42 | 0.24603 | 0.11916 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_143_0_load_139 | 43 | 0.073873 | 0.035778 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_143_0_load_67 | 45 | 0.39874 | 0.19312 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_143_0_load_25 | 47 | 0.33894 | 0.16416 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_143_0_load_133 | 56 | 0.079145 | 0.038332 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_143_0_load_120 | 58 | 0.10503 | 0.050867 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_143_0_load_119 | 59 | 0.24543 | 0.11887 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_143_0_load_166 | 60 | 0.33103 | 0.16033 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_143_0_load_121 | 61 | 0.13938 | 0.067506 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_143_0_load_146 | 62 | 0.17868 | 0.086538 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_143_0_load_122 | 65 | 0.33399 | 0.16176 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_143_0_load_155 | 67 | 0.13347 | 0.06464 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_143_0_load_42 | 68 | 0.25643 | 0.1242 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_143_0_load_131 | 70 | 0.10818 | 0.052395 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_143_0_load_153 | 72 | 0.41286 | 0.19996 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_143_0_load_129 | 73 | 0.11942 | 0.05784 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_143_0_load_37 | 74 | 0.3881 | 0.18797 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_143_0_load_165 | 79 | 0.5819 | 0.28183 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_143_0_load_141 | 81 | 0.35332 | 0.17112 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_143_0_load_145 | 82 | 0.38072 | 0.18439 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_143_0_load_151 | 84 | 0.23989 | 0.11618 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_143_0_load_43 | 86 | 0.24414 | 0.11824 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_143_0_load_167 | 90 | 0.26224 | 0.12701 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_143_0_load_164 | 91 | 0.35544 | 0.17215 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_143_0_load_60 | 92 | 0.35137 | 0.17018 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_143_0_load_148 | 95 | 0.086027 | 0.041665 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_143_0_load_149 | 96 | 0.088421 | 0.042824 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_143_0_load_68 | 98 | 0.36193 | 0.17529 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_143_0_load_156 | 101 | 0.38245 | 0.18523 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_143_0_load_79 | 105 | 0.24726 | 0.11976 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_143_0_load_109 | 107 | 0.33487 | 0.16219 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_143_0_load_81 | 109 | 0.25728 | 0.12461 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_143_0_load_161 | 113 | 0.21993 | 0.10652 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_143_0_load_162 | 115 | 0.12526 | 0.060667 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_143_0_load_160 | 116 | 0.29637 | 0.14354 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_143_0_load_110 | 117 | 0.27242 | 0.13194 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_143_0_load_82 | 118 | 0.33754 | 0.16348 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_143_0_load_88 | 119 | 0.2691 | 0.13033 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_143_0_load_91 | 121 | 0.31086 | 0.15056 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_143_0_load_94 | 123 | 0.18222 | 0.088252 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_143_0_load_83 | 124 | 0.26731 | 0.12947 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_143_0_load_134 | 130 | 0.34397 | 0.16659 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_143_0_load_152 | 131 | 0.34662 | 0.16788 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_143_0_load_128 | 132 | 0.079122 | 0.038321 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_143_0_load_137 | 133 | 0.26952 | 0.13053 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_143_0_load_144 | 137 | 0.10501 | 0.050857 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_143_0_load_142 | 139 | 0.062749 | 0.030391 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_143_0_load_98 | 140 | 0.16524 | 0.080031 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_143_0_load_135 | 141 | 0.099104 | 0.047998 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_143_0_load_95 | 142 | 0.11237 | 0.054424 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_143_0_load_99 | 144 | 0.35419 | 0.17154 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_143_0_load_101 | 145 | 0.52071 | 0.25219 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_143_0_load_100 | 147 | 0.22501 | 0.10898 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_143_0_load_104 | 149 | 0.18527 | 0.08973 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_143_0_load_138 | 151 | 0.077234 | 0.037406 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_143_0_load_117 | 153 | 0.1846 | 0.089407 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_143_0_load_157 | 155 | 0.12614 | 0.061094 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_143_0_load_114 | 156 | 0.18275 | 0.088509 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_143_0_load_111 | 157 | 0.10582 | 0.051253 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_143_0_load_112 | 158 | 0.08943 | 0.043313 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_143_0_load_113 | 160 | 0.29151 | 0.14118 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_143_0_load_115 | 161 | 0.10879 | 0.052691 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_143_0_load_116 | 162 | 0.15048 | 0.072879 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_143_0_load_123 | 163 | 0.1006 | 0.048722 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_143_0_load_163 | 164 | 0.17999 | 0.087172 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_143_0_line_0 |  | 0 | 1 | 0.050951 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_143_0_line_1 |  | 1 | 2 | 0.24695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_143_0_line_2 |  | 1 | 3 | 0.83117 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_143_0_line_3 |  | 2 | 4 | 0.3499 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_143_0_line_4 |  | 2 | 5 | 0.61316 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_143_0_line_5 |  | 2 | 6 | 0.088943 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_143_0_line_6 |  | 3 | 9 | 0.1145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_143_0_line_7 |  | 3 | 7 | 0.44212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_143_0_line_8 |  | 4 | 10 | 0.045588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_143_0_line_9 |  | 5 | 11 | 0.15129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_143_0_line_10 |  | 5 | 12 | 0.065526 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_143_0_line_11 |  | 7 | 8 | 0.081912 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_143_0_line_12 |  | 8 | 13 | 2.3318 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_143_0_line_13 |  | 10 | 15 | 0.094342 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_143_0_line_14 |  | 11 | 16 | 0.37141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_143_0_line_15 |  | 11 | 17 | 0.10384 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_143_0_line_16 |  | 13 | 14 | 0.085981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_143_0_line_17 |  | 16 | 18 | 0.17658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_143_0_line_18 |  | 16 | 19 | 0.5414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_143_0_line_19 |  | 18 | 21 | 0.073918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_143_0_line_20 |  | 18 | 22 | 0.24028 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_143_0_line_21 |  | 19 | 20 | 0.052192 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_143_0_line_22 |  | 21 | 23 | 0.020559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_143_0_line_23 |  | 23 | 88 | 0.77953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_143_0_line_24 |  | 24 | 25 | 0.043027 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
25 | MV_143_0_line_25 |  | 24 | 26 | 0.21824 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
26 | MV_143_0_line_26 |  | 25 | 27 | 0.17679 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_143_0_line_27 |  | 26 | 28 | 0.037586 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_143_0_line_28 |  | 26 | 29 | 0.35316 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
29 | MV_143_0_line_29 |  | 27 | 30 | 0.029056 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
30 | MV_143_0_line_30 |  | 29 | 93 | 0.018215 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
31 | MV_143_0_line_31 |  | 29 | 92 | 0.050992 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_143_0_line_32 |  | 30 | 41 | 0.17182 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
33 | MV_143_0_line_33 |  | 31 | 32 | 0.071835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_143_0_line_34 |  | 31 | 33 | 0.14319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_143_0_line_35 |  | 31 | 34 | 0.063001 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_143_0_line_36 |  | 32 | 42 | 0.064596 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_143_0_line_37 |  | 33 | 35 | 0.20174 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_143_0_line_38 |  | 33 | 36 | 0.020595 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_143_0_line_39 |  | 35 | 37 | 0.059671 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_143_0_line_40 |  | 38 | 39 | 0.31077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_143_0_line_41 |  | 38 | 40 | 0.060532 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_143_0_line_42 |  | 39 | 45 | 0.018479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_143_0_line_43 |  | 40 | 46 | 0.090034 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_143_0_line_44 |  | 41 | 43 | 0.036572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_143_0_line_45 |  | 41 | 87 | 0.10911 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_143_0_line_46 |  | 42 | 43 | 0.28489 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_143_0_line_47 |  | 42 | 44 | 0.019097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_143_0_line_48 |  | 44 | 78 | 0.058668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_143_0_line_49 |  | 44 | 88 | 0.26213 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_143_0_line_50 |  | 46 | 83 | 0.20373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_143_0_line_51 |  | 47 | 48 | 0.047799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_143_0_line_52 |  | 48 | 49 | 0.012891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_143_0_line_53 |  | 48 | 50 | 0.40865 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_143_0_line_54 |  | 48 | 51 | 0.43376 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_143_0_line_55 |  | 49 | 61 | 0.067457 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_143_0_line_56 |  | 50 | 62 | 0.018242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_143_0_line_57 |  | 51 | 63 | 0.14305 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
58 | MV_143_0_line_58 |  | 51 | 64 | 0.33861 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
59 | MV_143_0_line_59 |  | 51 | 65 | 0.053107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_143_0_line_60 |  | 52 | 53 | 0.28128 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_143_0_line_61 |  | 52 | 54 | 0.1506 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_143_0_line_62 |  | 53 | 58 | 0.0042432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_143_0_line_63 |  | 53 | 59 | 0.018191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_143_0_line_64 |  | 53 | 55 | 0.16202 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_143_0_line_65 |  | 54 | 60 | 0.058388 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_143_0_line_66 |  | 55 | 56 | 0.045618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_143_0_line_67 |  | 55 | 57 | 0.034279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_143_0_line_68 |  | 57 | 70 | 0.05342 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_143_0_line_69 |  | 60 | 71 | 0.35053 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
70 | MV_143_0_line_70 |  | 63 | 66 | 0.42366 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
71 | MV_143_0_line_71 |  | 63 | 67 | 0.057658 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_143_0_line_72 |  | 64 | 68 | 0.002863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_143_0_line_73 |  | 64 | 69 | 0.41465 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
74 | MV_143_0_line_74 |  | 66 | 72 | 0.006737 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
75 | MV_143_0_line_75 |  | 69 | 73 | 0.061439 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_143_0_line_76 |  | 69 | 71 | 0.75745 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_143_0_line_77 |  | 71 | 164 | 0.059733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_143_0_line_78 |  | 71 | 159 | 0.12881 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
79 | MV_143_0_line_79 |  | 72 | 97 | 0.003872 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_143_0_line_80 |  | 74 | 75 | 0.088866 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_143_0_line_81 |  | 75 | 76 | 0.16611 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_143_0_line_82 |  | 75 | 77 | 0.66583 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_143_0_line_83 |  | 76 | 80 | 0.21228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_143_0_line_84 |  | 76 | 81 | 0.056194 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_143_0_line_85 |  | 77 | 84 | 0.021322 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_143_0_line_86 |  | 78 | 79 | 0.017425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_143_0_line_87 |  | 80 | 82 | 0.016067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_143_0_line_88 |  | 80 | 83 | 0.027113 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_143_0_line_89 |  | 82 | 85 | 0.17029 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_143_0_line_90 |  | 85 | 86 | 0.044134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_143_0_line_91 |  | 86 | 87 | 0.051926 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_143_0_line_92 |  | 88 | 91 | 0.016083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_143_0_line_93 |  | 88 | 89 | 0.38196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_143_0_line_94 |  | 89 | 90 | 0.033419 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_143_0_line_95 |  | 93 | 94 | 0.017244 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
96 | MV_143_0_line_96 |  | 93 | 95 | 0.035147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_143_0_line_97 |  | 94 | 96 | 0.012847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_143_0_line_98 |  | 94 | 97 | 0.12958 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
99 | MV_143_0_line_99 |  | 98 | 99 | 0.006695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_143_0_line_100 |  | 99 | 100 | 0.19279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_143_0_line_101 |  | 100 | 101 | 0.021225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_143_0_line_102 |  | 100 | 102 | 0.13305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_143_0_line_103 |  | 102 | 108 | 0.52735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_143_0_line_104 |  | 102 | 109 | 0.036856 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_143_0_line_105 |  | 102 | 106 | 0.28549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_143_0_line_106 |  | 103 | 104 | 0.35899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_143_0_line_107 |  | 103 | 105 | 0.054835 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_143_0_line_108 |  | 104 | 117 | 0.031121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_143_0_line_109 |  | 104 | 106 | 0.56329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_143_0_line_110 |  | 104 | 111 | 0.64788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_143_0_line_111 |  | 106 | 107 | 0.073629 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
112 | MV_143_0_line_112 |  | 108 | 118 | 0.11676 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
113 | MV_143_0_line_113 |  | 108 | 119 | 0.7528 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_143_0_line_114 |  | 110 | 111 | 0.20969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_143_0_line_115 |  | 110 | 112 | 0.063179 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_143_0_line_116 |  | 110 | 113 | 0.080879 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_143_0_line_117 |  | 111 | 116 | 0.013284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_143_0_line_118 |  | 111 | 114 | 0.35443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_143_0_line_119 |  | 112 | 120 | 0.15828 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
120 | MV_143_0_line_120 |  | 112 | 121 | 0.050179 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_143_0_line_121 |  | 114 | 115 | 0.048972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_143_0_line_122 |  | 119 | 122 | 0.12043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_143_0_line_123 |  | 119 | 123 | 0.49942 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
124 | MV_143_0_line_124 |  | 120 | 141 | 0.21504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_143_0_line_125 |  | 120 | 130 | 0.024264 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
126 | MV_143_0_line_126 |  | 122 | 136 | 1.005 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_143_0_line_127 |  | 124 | 125 | 0.035147 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
128 | MV_143_0_line_128 |  | 124 | 126 | 0.078387 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
129 | MV_143_0_line_129 |  | 125 | 127 | 0.15664 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
130 | MV_143_0_line_130 |  | 126 | 128 | 0.057008 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
131 | MV_143_0_line_131 |  | 127 | 129 | 0.03963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_143_0_line_132 |  | 127 | 130 | 0.042485 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
133 | MV_143_0_line_133 |  | 128 | 131 | 0.06664 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
134 | MV_143_0_line_134 |  | 128 | 132 | 0.42449 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
135 | MV_143_0_line_135 |  | 129 | 133 | 0.020727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_143_0_line_136 |  | 131 | 134 | 0.072686 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_143_0_line_137 |  | 132 | 135 | 0.028156 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
138 | MV_143_0_line_138 |  | 134 | 146 | 0.78036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_143_0_line_139 |  | 135 | 159 | 0.1503 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
140 | MV_143_0_line_140 |  | 136 | 137 | 0.19587 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_143_0_line_141 |  | 136 | 138 | 1.5599 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
142 | MV_143_0_line_142 |  | 138 | 139 | 0.073266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_143_0_line_143 |  | 138 | 140 | 0.76083 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
144 | MV_143_0_line_144 |  | 139 | 143 | 0.75924 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_143_0_line_145 |  | 142 | 143 | 0.026241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_143_0_line_146 |  | 144 | 145 | 0.036228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_143_0_line_147 |  | 144 | 146 | 0.08291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_143_0_line_148 |  | 144 | 147 | 0.060245 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
149 | MV_143_0_line_149 |  | 147 | 148 | 0.019079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_143_0_line_150 |  | 148 | 149 | 0.034155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_143_0_line_151 |  | 148 | 150 | 0.36515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_143_0_line_152 |  | 149 | 151 | 0.0094981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_143_0_line_153 |  | 150 | 156 | 0.085912 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_143_0_line_154 |  | 150 | 157 | 0.072613 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_143_0_line_155 |  | 150 | 152 | 0.05828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_143_0_line_156 |  | 150 | 154 | 0.20449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_143_0_line_157 |  | 152 | 153 | 0.035666 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_143_0_line_158 |  | 154 | 155 | 0.0616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_143_0_line_159 |  | 157 | 158 | 0.046409 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_143_0_line_160 |  | 158 | 160 | 0.013531 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_143_0_line_161 |  | 159 | 163 | 0.089882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_143_0_line_162 |  | 160 | 161 | 0.062554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_143_0_line_163 |  | 161 | 162 | 0.015407 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_143_0_trafo_166 | 25 MVA 110/20 kV | 165 | 60 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2668118.0399 | 1201353.2595
1 | 2668142.2588 | 1201308.7309
2 | 2668223.3868 | 1201076.0939
3 | 2667551.2193 | 1201663.2356
4 | 2668304.9039 | 1200918.4965
5 | 2668652.6558 | 1201199.2497
6 | 2668303.1701 | 1201115.4065
7 | 2667300.1817 | 1201456.2346
8 | 2667226.8933 | 1201423.3457
9 | 2667638.8031 | 1201732.8172
10 | 2668350.3323 | 1200922.7072
11 | 2668775.7646 | 1201135.2263
12 | 2668650.5787 | 1201264.7432
13 | 2665801.1896 | 1199578.1676
14 | 2665726.3912 | 1199536.4423
15 | 2668399.589 | 1200986.1533
16 | 2669098.6662 | 1201294.3688
17 | 2668687.1653 | 1201081.0637
18 | 2669252.5548 | 1201282.7761
19 | 2668942.7169 | 1201659.3442
20 | 2668991.6109 | 1201641.0862
21 | 2669324.8057 | 1201267.7175
22 | 2669176.9218 | 1201054.7068
23 | 2669345.1787 | 1201264.9614
24 | 2670379.6525 | 1201700.406
25 | 2670358.0863 | 1201663.1739
26 | 2670467.308 | 1201900.2715
27 | 2670314.8093 | 1201550.485
28 | 2670487.4916 | 1201931.9843
29 | 2670242.609 | 1202026.4919
30 | 2670298.6603 | 1201526.3026
31 | 2670067.6957 | 1201564.169
32 | 2670055.08 | 1201494.3454
33 | 2670112.1994 | 1201690.7566
34 | 2670004.9333 | 1201558.6969
35 | 2670035.9844 | 1201795.371
36 | 2670123.7049 | 1201707.8376
37 | 2670095.2561 | 1201794.5432
38 | 2670559.7182 | 1201392.3418
39 | 2670652.3533 | 1201615.7719
40 | 2670510.1121 | 1201357.4685
41 | 2670276.6882 | 1201355.8963
42 | 2669995.4907 | 1201469.4099
43 | 2670246.9968 | 1201335.6016
44 | 2669983.4247 | 1201454.5819
45 | 2670636.2979 | 1201624.9989
46 | 2670435.1363 | 1201307.6209
47 | 2669642.4542 | 1202293.4748
48 | 2669674.3257 | 1202257.7802
49 | 2669683.6593 | 1202266.6722
50 | 2669978.6178 | 1202265.0288
51 | 2669816.4829 | 1201984.0174
52 | 2669595.1277 | 1202345.9998
53 | 2669548.2895 | 1202470.3745
54 | 2669476.0193 | 1202284.0096
55 | 2669480.1104 | 1202521.7793
56 | 2669449.4767 | 1202555.5808
57 | 2669505.2687 | 1202544.8192
58 | 2669551.9174 | 1202471.8732
59 | 2669535.0081 | 1202481.5823
60 | 2669419.9081 | 1202300.1562
61 | 2669669.4883 | 1202319.0045
62 | 2669979.8508 | 1202246.8322
63 | 2669916.0577 | 1201984.1259
64 | 2669801.7532 | 1201849.3858
65 | 2669774.4668 | 1201963.7877
66 | 2670082.6116 | 1202056.7764
67 | 2669875.3101 | 1202024.9186
68 | 2669802.933 | 1201846.7758
69 | 2669389.1522 | 1201808.2452
70 | 2669463.4771 | 1202577.6086
71 | 2669076.6906 | 1202228.9472
72 | 2670088.956 | 1202054.4605
73 | 2669368.9648 | 1201866.2725
74 | 2670433.9796 | 1200985.4451
75 | 2670516.591 | 1201018.1945
76 | 2670608.0981 | 1201096.8559
77 | 2670673.8642 | 1201234.2277
78 | 2669965.3487 | 1201424.5187
79 | 2669948.2409 | 1201420.9607
80 | 2670506.0567 | 1201183.1926
81 | 2670643.4812 | 1201140.5116
82 | 2670503.7857 | 1201167.2895
83 | 2670478.982 | 1201181.7614
84 | 2670654.8492 | 1201243.8754
85 | 2670334.4197 | 1201184.9938
86 | 2670308.4311 | 1201210.926
87 | 2670272.1186 | 1201248.0437
88 | 2669818.3942 | 1201445.4129
89 | 2669846.8502 | 1201636.528
90 | 2669861.4245 | 1201666.6166
91 | 2669802.2682 | 1201445.7804
92 | 2670291.5232 | 1202040.898
93 | 2670231.2846 | 1202036.1314
94 | 2670215.6486 | 1202043.4966
95 | 2670246.1089 | 1202068.0139
96 | 2670221.3279 | 1202055.0259
97 | 2670092.5799 | 1202053.0689
98 | 2668223.3293 | 1203466.4273
99 | 2668228.9332 | 1203470.1157
100 | 2668393.5429 | 1203557.762
101 | 2668384.8446 | 1203577.1297
102 | 2668406.3957 | 1203503.1982
103 | 2668813.3421 | 1203193.961
104 | 2668581.1685 | 1203380.0714
105 | 2668758.5179 | 1203195.0639
106 | 2668377.6606 | 1203285.4928
107 | 2668335.894 | 1203224.8559
108 | 2668735.4657 | 1203685.163
109 | 2668435.171 | 1203480.1693
110 | 2668670.789 | 1202967.9616
111 | 2668812.2942 | 1203049.1388
112 | 2668651.7792 | 1202912.3984
113 | 2668626.1585 | 1203035.4121
114 | 2669021.7435 | 1202999.1574
115 | 2669061.8248 | 1202974.7612
116 | 2668808.3594 | 1203036.6414
117 | 2668577.7174 | 1203351.9369
118 | 2668722.3136 | 1203569.1412
119 | 2669487.0657 | 1203642.7533
120 | 2668525.4804 | 1202821.9828
121 | 2668683.9786 | 1202873.845
122 | 2669604.652 | 1203633.2161
123 | 2669541.2649 | 1204139.2199
124 | 2668517.7425 | 1202653.3697
125 | 2668482.7541 | 1202649.0994
126 | 2668595.6493 | 1202663.881
127 | 2668462.4809 | 1202804.4056
128 | 2668603.6719 | 1202607.45
129 | 2668457.5175 | 1202843.717
130 | 2668501.6951 | 1202817.1874
131 | 2668567.5879 | 1202551.4241
132 | 2668971.5514 | 1202395.6485
133 | 2668454.9227 | 1202864.2775
134 | 2668618.9399 | 1202499.9824
135 | 2668997.9744 | 1202398.7408
136 | 2670364.6213 | 1204024.7572
137 | 2670205.841 | 1203910.0636
138 | 2671223.48 | 1205326.9234
139 | 2671292.7067 | 1205351.4199
140 | 2670609.1488 | 1205775.7611
141 | 2668636.1516 | 1202761.3968
142 | 2671416.8986 | 1206122.3678
143 | 2671399.2319 | 1206103.1447
144 | 2668129.2235 | 1202186.9538
145 | 2668149.314 | 1202156.8073
146 | 2668200.1319 | 1202228.7019
147 | 2668080.0546 | 1202152.1421
148 | 2668078.9398 | 1202133.0957
149 | 2668050.0961 | 1202115.7682
150 | 2667872.8172 | 1201960.7472
151 | 2668042.2829 | 1202110.3675
152 | 2667875.4813 | 1201930.5926
153 | 2667906.4503 | 1201913.7331
154 | 2667858.5985 | 1202035.2196
155 | 2667807.2552 | 1202049.9346
156 | 2667790.7082 | 1201986.0246
157 | 2667806.4999 | 1201931.1731
158 | 2667761.8982 | 1201918.88
159 | 2669067.8503 | 1202314.8638
160 | 2667749.0818 | 1201914.5395
161 | 2667691.6997 | 1201890.4959
162 | 2667678.5718 | 1201882.4306
163 | 2668978.2179 | 1202308.1698
164 | 2669017.0578 | 1202223.2325
165 | 2669419.9081 | 1202300.1562

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98484 | -0.27703 | 0.093829 | 0.045443
1 | 0.98484 | -0.27708 | 0 | 0
2 | 0.98499 | -0.27781 | 0 | 0
3 | 0.98445 | -0.27486 | 0 | 0
4 | 0.98487 | -0.27681 | 0 | 0
5 | 0.98565 | -0.28169 | 0 | 0
6 | 0.98497 | -0.27794 | 0.12009 | 0.058162
7 | 0.9843 | -0.2737 | 0 | 0
8 | 0.98427 | -0.27346 | 0.16029 | 0.077632
9 | 0.98444 | -0.27473 | 0.098119 | 0.047521
10 | 0.98485 | -0.27667 | 0.1524 | 0.073809
11 | 0.98583 | -0.28271 | 0 | 0
12 | 0.98564 | -0.28176 | 0.077081 | 0.037332
13 | 0.98376 | -0.27744 | 0 | 0
14 | 0.98374 | -0.27732 | 0.11334 | 0.054891
15 | 0.98484 | -0.27654 | 0.11786 | 0.057084
16 | 0.98634 | -0.28568 | 0 | 0
17 | 0.9858 | -0.28289 | 0.13959 | 0.067605
18 | 0.9866 | -0.28715 | 0 | 0
19 | 0.98625 | -0.28506 | 0 | 0
20 | 0.98624 | -0.28514 | 0.12649 | 0.061261
21 | 0.98673 | -0.28785 | 0.1331 | 0.064462
22 | 0.98655 | -0.28751 | 0.12101 | 0.058607
23 | 0.98677 | -0.28808 | 0 | 0
24 | 0.99303 | -0.2441 | 0.32663 | 0.15819
25 | 0.99293 | -0.24958 | 0 | 0
26 | 0.99353 | -0.21497 | 0 | 0
27 | 0.99255 | -0.25148 | 0 | 0
28 | 0.99352 | -0.21483 | 0.32226 | 0.15608
29 | 0.99395 | -0.21288 | 0 | 0
30 | 0.99245 | -0.2527 | 0.41167 | 0.19938
31 | 0.98877 | -0.3012 | 0 | 0
32 | 0.98884 | -0.30186 | 0.086895 | 0.042085
33 | 0.98868 | -0.30047 | 0 | 0
34 | 0.98872 | -0.30147 | 0.34227 | 0.16577
35 | 0.98858 | -0.29958 | 0 | 0
36 | 0.98868 | -0.30045 | 0.085793 | 0.041552
37 | 0.98855 | -0.29931 | 0.37841 | 0.18327
38 | 0.98948 | -0.28712 | 0 | 0
39 | 0.98932 | -0.28568 | 0 | 0
40 | 0.98951 | -0.28738 | 0.27965 | 0.13544
41 | 0.99121 | -0.28534 | 0 | 0
42 | 0.98895 | -0.30108 | 0.24603 | 0.11916
43 | 0.99103 | -0.28397 | 0.073873 | 0.035778
44 | 0.98889 | -0.30064 | 0 | 0
45 | 0.98931 | -0.28559 | 0.39874 | 0.19312
46 | 0.98962 | -0.28655 | 0 | 0
47 | 0.99454 | -0.2046 | 0.33894 | 0.16416
48 | 0.99456 | -0.2048 | 0 | 0
49 | 0.99456 | -0.20478 | 0 | 0
50 | 0.99447 | -0.20405 | 0 | 0
51 | 0.99492 | -0.20773 | 0 | 0
52 | 0.99984 | 0.00034588 | 0 | 0
53 | 0.99965 | 0.0019604 | 0 | 0
54 | 0.99994 | -0.00046878 | 0 | 0
55 | 0.99961 | 0.0022709 | 0 | 0
56 | 0.9996 | 0.0023125 | 0.079145 | 0.038332
57 | 0.9996 | 0.0023116 | 0 | 0
58 | 0.99965 | 0.0019657 | 0.10503 | 0.050867
59 | 0.99964 | 0.0020136 | 0.24543 | 0.11887
60 | 1 | 0 | -18.6724 | -8.3844
61 | 0.99455 | -0.20467 | 0.13938 | 0.067506
62 | 0.99446 | -0.20401 | 0.17868 | 0.086538
63 | 0.99473 | -0.20878 | 0 | 0
64 | 0.99543 | -0.20492 | 0 | 0
65 | 0.9949 | -0.20752 | 0.33399 | 0.16176
66 | 0.99417 | -0.21174 | 0 | 0
67 | 0.99472 | -0.20888 | 0.13347 | 0.06464
68 | 0.99543 | -0.20491 | 0.25643 | 0.1242
69 | 0.99673 | -0.12828 | 0 | 0
70 | 0.9996 | 0.0023786 | 0.10818 | 0.052395
71 | 0.99792 | -0.12153 | 0 | 0
72 | 0.99416 | -0.21179 | 0.41286 | 0.19996
73 | 0.99672 | -0.1282 | 0.11942 | 0.05784
74 | 0.98937 | -0.28493 | 0.3881 | 0.18797
75 | 0.98944 | -0.2845 | 0 | 0
76 | 0.98957 | -0.28559 | 0 | 0
77 | 0.98923 | -0.28289 | 0 | 0
78 | 0.98884 | -0.30022 | 0 | 0
79 | 0.98883 | -0.3001 | 0.5819 | 0.28183
80 | 0.98984 | -0.28783 | 0 | 0
81 | 0.98953 | -0.28583 | 0.35332 | 0.17112
82 | 0.98987 | -0.28811 | 0.38072 | 0.18439
83 | 0.9898 | -0.28809 | 0 | 0
84 | 0.98922 | -0.28295 | 0.23989 | 0.11618
85 | 0.99054 | -0.28325 | 0 | 0
86 | 0.99066 | -0.28424 | 0.24414 | 0.11824
87 | 0.99089 | -0.28259 | 0 | 0
88 | 0.9882 | -0.29628 | 0 | 0
89 | 0.98807 | -0.29519 | 0 | 0
90 | 0.98806 | -0.29508 | 0.26224 | 0.12701
91 | 0.98819 | -0.29621 | 0.35544 | 0.17215
92 | 0.99391 | -0.2131 | 0.35137 | 0.17018
93 | 0.99397 | -0.21277 | 0 | 0
94 | 0.99399 | -0.21266 | 0 | 0
95 | 0.99397 | -0.21273 | 0.086027 | 0.041665
96 | 0.99399 | -0.21264 | 0.088421 | 0.042824
97 | 0.99415 | -0.21182 | 0 | 0
98 | 0.98717 | -0.20838 | 0.36193 | 0.17529
99 | 0.98717 | -0.20841 | 0 | 0
100 | 0.98726 | -0.20924 | 0 | 0
101 | 0.98725 | -0.20914 | 0.38245 | 0.18523
102 | 0.98739 | -0.2104 | 0 | 0
103 | 0.98995 | -0.23142 | 0 | 0
104 | 0.99006 | -0.23241 | 0 | 0
105 | 0.98992 | -0.23159 | 0.24726 | 0.11976
106 | 0.98821 | -0.21716 | 0 | 0
107 | 0.98816 | -0.21747 | 0.33487 | 0.16219
108 | 0.98656 | -0.20376 | 0 | 0
109 | 0.98737 | -0.21052 | 0.25728 | 0.12461
110 | 0.99357 | -0.26042 | 0 | 0
111 | 0.99262 | -0.25298 | 0 | 0
112 | 0.99387 | -0.26281 | 0 | 0
113 | 0.99353 | -0.26064 | 0.21993 | 0.10652
114 | 0.99257 | -0.25256 | 0 | 0
115 | 0.99256 | -0.25249 | 0.12526 | 0.060667
116 | 0.99262 | -0.25293 | 0.29637 | 0.14354
117 | 0.99005 | -0.2323 | 0.27242 | 0.13194
118 | 0.98648 | -0.20425 | 0.33754 | 0.16348
119 | 0.98525 | -0.21435 | 0.2691 | 0.13033
120 | 0.99421 | -0.25872 | 0 | 0
121 | 0.99385 | -0.26263 | 0.31086 | 0.15056
122 | 0.98518 | -0.21393 | 0 | 0
123 | 0.98507 | -0.21549 | 0.18222 | 0.088252
124 | 0.99461 | -0.25676 | 0.26731 | 0.12947
125 | 0.99455 | -0.25703 | 0 | 0
126 | 0.99474 | -0.25612 | 0 | 0
127 | 0.99431 | -0.25824 | 0 | 0
128 | 0.99483 | -0.25565 | 0 | 0
129 | 0.9943 | -0.25812 | 0 | 0
130 | 0.99425 | -0.25855 | 0.34397 | 0.16659
131 | 0.99445 | -0.25834 | 0.34662 | 0.16788
132 | 0.9971 | -0.12533 | 0.079122 | 0.038321
133 | 0.99429 | -0.25805 | 0.26952 | 0.13053
134 | 0.99408 | -0.26096 | 0 | 0
135 | 0.99718 | -0.12499 | 0 | 0
136 | 0.98461 | -0.20957 | 0 | 0
137 | 0.98457 | -0.20983 | 0.10501 | 0.050857
138 | 0.98357 | -0.21687 | 0 | 0
139 | 0.98356 | -0.21672 | 0.062749 | 0.030391
140 | 0.98333 | -0.21847 | 0.16524 | 0.080031
141 | 0.99419 | -0.2585 | 0.099104 | 0.047998
142 | 0.98339 | -0.21782 | 0.11237 | 0.054424
143 | 0.98339 | -0.21786 | 0 | 0
144 | 0.99121 | -0.23572 | 0.35419 | 0.17154
145 | 0.99118 | -0.23549 | 0.52071 | 0.25219
146 | 0.99148 | -0.2382 | 0 | 0
147 | 0.99101 | -0.23713 | 0.22501 | 0.10898
148 | 0.99097 | -0.23681 | 0 | 0
149 | 0.99096 | -0.2367 | 0.18527 | 0.08973
150 | 0.99039 | -0.23176 | 0 | 0
151 | 0.99096 | -0.23669 | 0.077234 | 0.037406
152 | 0.99038 | -0.23163 | 0 | 0
153 | 0.99037 | -0.23156 | 0.1846 | 0.089407
154 | 0.99036 | -0.2315 | 0 | 0
155 | 0.99035 | -0.2314 | 0.12614 | 0.061094
156 | 0.99037 | -0.23157 | 0.18275 | 0.088509
157 | 0.99032 | -0.23112 | 0.10582 | 0.051253
158 | 0.99028 | -0.23076 | 0.08943 | 0.043313
159 | 0.99757 | -0.12314 | 0 | 0
160 | 0.99027 | -0.23067 | 0.29151 | 0.14118
161 | 0.99025 | -0.23048 | 0.10879 | 0.052691
162 | 0.99025 | -0.23045 | 0.15048 | 0.072879
163 | 0.99756 | -0.12304 | 0.1006 | 0.048722
164 | 0.9979 | -0.1214 | 0.17999 | 0.087172
165 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.093829 | -0.045443 | 0.093829 | 0.044264 | 6.3209e-07 | -0.0011797 | 0.0030559 | 0.003041 | 0.0030559 | 0.98484 | -0.27703 | 0.98484 | -0.27708 | 1.389
1 | -0.46584 | -0.18571 | 0.46591 | 0.18001 | 7.0937e-05 | -0.0056985 | 0.0147 | 0.014638 | 0.0147 | 0.98484 | -0.27708 | 0.98499 | -0.27781 | 6.6817
2 | 0.37201 | 0.14145 | -0.37186 | -0.16064 | 0.0001537 | -0.019195 | 0.011666 | 0.011878 | 0.011878 | 0.98484 | -0.27708 | 0.98445 | -0.27486 | 5.3991
3 | 0.2703 | 0.11956 | -0.27027 | -0.12765 | 3.5445e-05 | -0.0080937 | 0.0086623 | 0.008761 | 0.008761 | 0.98499 | -0.27781 | 0.98487 | -0.27681 | 3.9823
4 | -0.85631 | -0.35763 | 0.85691 | 0.3436 | 0.00060194 | -0.014035 | 0.027197 | 0.027039 | 0.027197 | 0.98499 | -0.27781 | 0.98565 | -0.28169 | 12.3623
5 | 0.12009 | 0.058061 | -0.12009 | -0.058162 | 2.4227e-06 | -0.0001015 | 0.0039094 | 0.0039107 | 0.0039107 | 0.98499 | -0.27781 | 0.98497 | -0.27794 | 1.8622
6 | 0.09812 | 0.044872 | -0.098119 | -0.047521 | 1.5459e-06 | -0.0026489 | 0.0031638 | 0.0031969 | 0.0031969 | 0.98445 | -0.27486 | 0.98444 | -0.27473 | 1.4531
7 | 0.27374 | 0.11577 | -0.27369 | -0.12598 | 4.5446e-05 | -0.010215 | 0.0087152 | 0.0088364 | 0.0088364 | 0.98445 | -0.27486 | 0.9843 | -0.2737 | 4.0165
8 | 0.27027 | 0.12765 | -0.27026 | -0.12871 | 4.6784e-06 | -0.0010544 | 0.008761 | 0.0087743 | 0.0087743 | 0.98487 | -0.27681 | 0.98485 | -0.27667 | 3.9883
9 | -0.93399 | -0.38085 | 0.93417 | 0.3774 | 0.00017603 | -0.0034577 | 0.029541 | 0.029503 | 0.029541 | 0.98565 | -0.28169 | 0.98583 | -0.28271 | 13.4278
10 | 0.077082 | 0.037256 | -0.077081 | -0.037332 | 7.343e-07 | -7.5536e-05 | 0.0025074 | 0.0025084 | 0.0025084 | 0.98565 | -0.28169 | 0.98564 | -0.28176 | 1.1945
11 | 0.27369 | 0.12598 | -0.27368 | -0.12788 | 8.561e-06 | -0.0018922 | 0.0088364 | 0.0088598 | 0.0088598 | 0.9843 | -0.2737 | 0.98427 | -0.27346 | 4.0272
12 | 0.11339 | 0.050244 | -0.11334 | -0.052904 | 5.5462e-05 | -0.0026607 | 0.0036375 | 0.0036703 | 0.0036703 | 0.98427 | -0.27346 | 0.98376 | -0.27744 | 1.7477
13 | 0.11787 | 0.0549 | -0.11786 | -0.057084 | 1.8425e-06 | -0.0021842 | 0.0038112 | 0.0038387 | 0.0038387 | 0.98485 | -0.27667 | 0.98484 | -0.27654 | 1.7449
14 | -1.0738 | -0.44488 | 1.0743 | 0.43643 | 0.00057271 | -0.0084528 | 0.034034 | 0.033938 | 0.034034 | 0.98583 | -0.28271 | 0.98634 | -0.28568 | 15.47
15 | 0.13959 | 0.067487 | -0.13959 | -0.067605 | 3.8151e-06 | -0.00011809 | 0.0045402 | 0.0045417 | 0.0045417 | 0.98583 | -0.28271 | 0.9858 | -0.28289 | 2.1627
16 | 0.11334 | 0.052904 | -0.11334 | -0.054891 | 1.5567e-06 | -0.0019862 | 0.0036703 | 0.0036953 | 0.0036953 | 0.98376 | -0.27744 | 0.98374 | -0.27732 | 1.6797
17 | -1.2008 | -0.48506 | 1.2012 | 0.48106 | 0.00033828 | -0.0040023 | 0.037904 | 0.037859 | 0.037904 | 0.98634 | -0.28568 | 0.9866 | -0.28715 | 17.2292
18 | 0.1265 | 0.04863 | -0.12649 | -0.061201 | 1.1775e-05 | -0.012571 | 0.0039665 | 0.004113 | 0.004113 | 0.98634 | -0.28568 | 0.98625 | -0.28506 | 1.8695
19 | -1.3222 | -0.53939 | 1.3224 | 0.53772 | 0.00017219 | -0.001667 | 0.041782 | 0.041763 | 0.041782 | 0.9866 | -0.28715 | 0.98673 | -0.28785 | 18.9917
20 | 0.12101 | 0.058332 | -0.12101 | -0.058607 | 6.6205e-06 | -0.00027505 | 0.0039307 | 0.0039342 | 0.0039342 | 0.9866 | -0.28715 | 0.98655 | -0.28751 | 1.8735
21 | 0.12649 | 0.061201 | -0.12649 | -0.061261 | 1.5734e-06 | -5.9619e-05 | 0.004113 | 0.0041137 | 0.0041137 | 0.98625 | -0.28506 | 0.98624 | -0.28514 | 1.9589
22 | -1.4555 | -0.60218 | 1.4555 | 0.60172 | 5.8273e-05 | -0.00046065 | 0.046081 | 0.046076 | 0.046081 | 0.98673 | -0.28785 | 0.98677 | -0.28808 | 20.946
23 | -1.4555 | -0.60172 | 1.4577 | 0.58423 | 0.0021997 | -0.017497 | 0.046076 | 0.045876 | 0.046076 | 0.98677 | -0.28808 | 0.9882 | -0.29628 | 20.9435
24 | 6.5902 | 2.9893 | -6.5899 | -2.9885 | 0.00033989 | 0.0007967 | 0.21037 | 0.21037 | 0.21037 | 0.99303 | -0.2441 | 0.99293 | -0.24958 | 16.3076
25 | -6.9169 | -3.1474 | 6.9188 | 3.152 | 0.0019011 | 0.004517 | 0.22091 | 0.22091 | 0.22091 | 0.99303 | -0.2441 | 0.99353 | -0.21497 | 17.1251
26 | 6.5899 | 2.9885 | -6.5875 | -2.998 | 0.0024191 | -0.0095852 | 0.21037 | 0.2105 | 0.2105 | 0.99293 | -0.24958 | 0.99255 | -0.25148 | 32.9937
27 | 0.32227 | 0.1552 | -0.32226 | -0.15608 | 5.4256e-06 | -0.00088421 | 0.010393 | 0.010404 | 0.010404 | 0.99353 | -0.21497 | 0.99352 | -0.21483 | 4.7291
28 | -7.241 | -3.3072 | 7.244 | 3.265 | 0.0029124 | -0.042185 | 0.2313 | 0.23077 | 0.2313 | 0.99353 | -0.21497 | 0.99395 | -0.21288 | 18.1267
29 | 6.5875 | 2.998 | -6.5869 | -2.9986 | 0.00062189 | -0.00052998 | 0.2105 | 0.21051 | 0.21051 | 0.99255 | -0.25148 | 0.99245 | -0.2527 | 58.1524
30 | -7.5953 | -3.4351 | 7.5955 | 3.4329 | 0.00016494 | -0.0021685 | 0.24211 | 0.24208 | 0.24211 | 0.99395 | -0.21288 | 0.99397 | -0.21277 | 18.9738
31 | 0.35138 | 0.17012 | -0.35137 | -0.17018 | 1.1681e-05 | -5.2821e-05 | 0.011338 | 0.011339 | 0.011339 | 0.99395 | -0.21288 | 0.99391 | -0.2131 | 5.3996
32 | 6.1752 | 2.7992 | -6.1691 | -2.7924 | 0.0061345 | 0.0068041 | 0.19721 | 0.19721 | 0.19721 | 0.99245 | -0.2527 | 0.99121 | -0.28534 | 56.3467
33 | -0.80658 | -0.38063 | 0.80665 | 0.37897 | 6.4971e-05 | -0.0016577 | 0.026039 | 0.026018 | 0.026039 | 0.98877 | -0.3012 | 0.98884 | -0.30186 | 11.8359
34 | 0.4643 | 0.21493 | -0.46426 | -0.21826 | 4.2771e-05 | -0.0033295 | 0.014937 | 0.014979 | 0.014979 | 0.98877 | -0.3012 | 0.98868 | -0.30047 | 6.8085
35 | 0.34228 | 0.1657 | -0.34227 | -0.16577 | 1.3837e-05 | -6.4859e-05 | 0.011103 | 0.011103 | 0.011103 | 0.98877 | -0.3012 | 0.98872 | -0.30147 | 5.2874
36 | -0.89354 | -0.42106 | 0.89364 | 0.42104 | 9.57e-05 | -1.5468e-05 | 0.028837 | 0.028836 | 0.028837 | 0.98884 | -0.30186 | 0.98895 | -0.30108 | 13.7317
37 | 0.37846 | 0.17719 | -0.37842 | -0.18188 | 4.0289e-05 | -0.004696 | 0.012202 | 0.01226 | 0.01226 | 0.98868 | -0.30047 | 0.98858 | -0.29958 | 5.5729
38 | 0.085794 | 0.041071 | -0.085793 | -0.041552 | 2.1253e-07 | -0.00048058 | 0.0027772 | 0.0027833 | 0.0027833 | 0.98868 | -0.30047 | 0.98868 | -0.30045 | 1.2652
39 | 0.37842 | 0.18188 | -0.37841 | -0.18327 | 1.1992e-05 | -0.0013888 | 0.01226 | 0.012278 | 0.012278 | 0.98858 | -0.29958 | 0.98855 | -0.29931 | 5.581
40 | 0.39881 | 0.18545 | -0.39875 | -0.19269 | 6.8791e-05 | -0.0072431 | 0.012832 | 0.012922 | 0.012922 | 0.98948 | -0.28712 | 0.98932 | -0.28568 | 5.8738
41 | -0.39881 | -0.18545 | 0.39883 | 0.18403 | 1.3287e-05 | -0.0014111 | 0.012832 | 0.012814 | 0.012832 | 0.98948 | -0.28712 | 0.98951 | -0.28738 | 5.8325
42 | 0.39875 | 0.19269 | -0.39874 | -0.19312 | 4.1213e-06 | -0.0004306 | 0.012922 | 0.012928 | 0.012928 | 0.98932 | -0.28568 | 0.98931 | -0.28559 | 5.8763
43 | -0.67847 | -0.31947 | 0.67855 | 0.31942 | 7.6778e-05 | -5.7161e-05 | 0.021878 | 0.021877 | 0.021878 | 0.98951 | -0.28738 | 0.98962 | -0.28655 | 10.4181
44 | 3.8808 | 1.727 | -3.8801 | -1.7277 | 0.00074726 | -0.0006361 | 0.12371 | 0.12372 | 0.12372 | 0.99121 | -0.28534 | 0.99103 | -0.28397 | 56.2364
45 | 2.2882 | 1.0654 | -2.2875 | -1.0677 | 0.00078742 | -0.002325 | 0.07351 | 0.073542 | 0.073542 | 0.99121 | -0.28534 | 0.99089 | -0.28259 | 33.4281
46 | -3.7987 | -1.6875 | 3.8062 | 1.6919 | 0.0074724 | 0.0043471 | 0.12133 | 0.12133 | 0.12133 | 0.98895 | -0.30108 | 0.99103 | -0.28397 | 57.7782
47 | 2.6591 | 1.1473 | -2.6589 | -1.1477 | 0.0001822 | -0.00039187 | 0.084535 | 0.08454 | 0.08454 | 0.98895 | -0.30108 | 0.98889 | -0.30064 | 38.4275
48 | 0.58194 | 0.28006 | -0.58191 | -0.28142 | 2.7863e-05 | -0.0013615 | 0.018853 | 0.01887 | 0.01887 | 0.98889 | -0.30064 | 0.98884 | -0.30022 | 8.5773
49 | 2.0769 | 0.86767 | -2.0754 | -0.87334 | 0.0015125 | -0.0056675 | 0.065708 | 0.065777 | 0.065777 | 0.98889 | -0.30064 | 0.9882 | -0.29628 | 29.8987
50 | -0.67855 | -0.31942 | 0.67868 | 0.31469 | 0.00012982 | -0.0047262 | 0.021877 | 0.021818 | 0.021877 | 0.98962 | -0.28655 | 0.9898 | -0.28809 | 9.944
51 | -0.33894 | -0.16416 | 0.33895 | 0.16303 | 7.6152e-06 | -0.0011266 | 0.010931 | 0.010917 | 0.010931 | 0.99454 | -0.2046 | 0.99456 | -0.2048 | 4.9688
52 | 0.13938 | 0.065609 | -0.13938 | -0.065913 | 3.4438e-07 | -0.00030435 | 0.0044715 | 0.0044752 | 0.0044752 | 0.99456 | -0.2048 | 0.99456 | -0.20478 | 2.0342
53 | 0.1787 | 0.076463 | -0.17868 | -0.086108 | 1.7714e-05 | -0.0096449 | 0.0056416 | 0.0057576 | 0.0057576 | 0.99456 | -0.2048 | 0.99447 | -0.20405 | 2.6171
54 | -0.65703 | -0.3051 | 0.65729 | 0.29493 | 0.0002545 | -0.010172 | 0.021027 | 0.020903 | 0.021027 | 0.99456 | -0.2048 | 0.99492 | -0.20773 | 9.5575
55 | 0.13938 | 0.065913 | -0.13938 | -0.067506 | 1.8116e-06 | -0.0015926 | 0.0044752 | 0.0044952 | 0.0044952 | 0.99456 | -0.20478 | 0.99455 | -0.20467 | 2.0433
56 | 0.17868 | 0.086108 | -0.17868 | -0.086538 | 8.0806e-07 | -0.0004305 | 0.0057576 | 0.005763 | 0.005763 | 0.99447 | -0.20405 | 0.99446 | -0.20401 | 2.6196
57 | 8.3238 | 3.695 | -8.3222 | -3.712 | 0.0015443 | -0.016921 | 0.26424 | 0.26445 | 0.26445 | 0.99492 | -0.20773 | 0.99473 | -0.20878 | 20.7248
58 | -9.315 | -4.1505 | 9.3196 | 4.1109 | 0.0045726 | -0.039567 | 0.29589 | 0.29539 | 0.29589 | 0.99492 | -0.20773 | 0.99543 | -0.20492 | 23.1888
59 | 0.334 | 0.16051 | -0.33399 | -0.16176 | 8.2081e-06 | -0.0012527 | 0.010752 | 0.010768 | 0.010768 | 0.99492 | -0.20773 | 0.9949 | -0.20752 | 4.8944
60 | 0.5379 | 0.2462 | -0.53779 | -0.25288 | 0.00011007 | -0.0066798 | 0.01708 | 0.017161 | 0.017161 | 0.99984 | 0.00034588 | 0.99965 | 0.0019604 | 7.8007
61 | -0.5379 | -0.2462 | 0.53796 | 0.24262 | 5.8503e-05 | -0.0035776 | 0.01708 | 0.017037 | 0.01708 | 0.99984 | 0.00034588 | 0.99994 | -0.00046878 | 7.7636
62 | 0.10503 | 0.050766 | -0.10503 | -0.050867 | 6.4342e-08 | -0.00010122 | 0.0033687 | 0.0033699 | 0.0033699 | 0.99965 | 0.0019604 | 0.99965 | 0.0019657 | 1.5318
63 | 0.24543 | 0.11843 | -0.24543 | -0.11887 | 1.505e-06 | -0.00043358 | 0.0078694 | 0.0078749 | 0.0078749 | 0.99965 | 0.0019604 | 0.99964 | 0.0020136 | 3.5795
64 | 0.18734 | 0.083683 | -0.18733 | -0.087547 | 7.6524e-06 | -0.0038632 | 0.0059251 | 0.0059715 | 0.0059715 | 0.99965 | 0.0019604 | 0.99961 | 0.0022709 | 2.7143
65 | -0.53796 | -0.24262 | 0.53799 | 0.24257 | 3.0194e-05 | -5.0787e-05 | 0.017037 | 0.017036 | 0.017037 | 0.99994 | -0.00046878 | 1 | 0 | 8.1128
66 | 0.079146 | 0.037244 | -0.079145 | -0.038332 | 3.9067e-07 | -0.0010882 | 0.0025261 | 0.0025396 | 0.0025396 | 0.99961 | 0.0022709 | 0.9996 | 0.0023125 | 1.1544
67 | 0.10818 | 0.050303 | -0.10818 | -0.051121 | 5.4483e-07 | -0.00081764 | 0.0034454 | 0.0034555 | 0.0034555 | 0.99961 | 0.0022709 | 0.9996 | 0.0023116 | 1.5707
68 | 0.10818 | 0.051121 | -0.10818 | -0.052395 | 8.5543e-07 | -0.0012742 | 0.0034555 | 0.0034713 | 0.0034713 | 0.9996 | 0.0023116 | 0.9996 | 0.0023786 | 1.5779
69 | 18.1204 | 8.1313 | -18.0999 | -8.077 | 0.020568 | 0.054343 | 0.57334 | 0.57336 | 0.57336 | 1 | 0 | 0.99792 | -0.12153 | 44.4462
70 | 8.1887 | 3.6474 | -8.1843 | -3.6975 | 0.0044405 | -0.050149 | 0.26015 | 0.26077 | 0.26077 | 0.99473 | -0.20878 | 0.99417 | -0.21174 | 20.4368
71 | 0.13347 | 0.064573 | -0.13347 | -0.06464 | 1.9023e-06 | -6.6916e-05 | 0.0043028 | 0.0043037 | 0.0043037 | 0.99473 | -0.20878 | 0.99472 | -0.20888 | 2.0494
72 | 0.25643 | 0.12413 | -0.25643 | -0.1242 | 2.6093e-07 | -6.7657e-05 | 0.0082619 | 0.0082628 | 0.0082628 | 0.99543 | -0.20492 | 0.99543 | -0.20491 | 3.7558
73 | -9.5761 | -4.235 | 9.5829 | 4.2522 | 0.0068241 | 0.017213 | 0.30365 | 0.30364 | 0.30365 | 0.99543 | -0.20492 | 0.99673 | -0.12828 | 23.5388
74 | 8.1843 | 3.6975 | -8.1842 | -3.6983 | 7.0785e-05 | -0.00079688 | 0.26077 | 0.26078 | 0.26078 | 0.99417 | -0.21174 | 0.99416 | -0.21179 | 20.4376
75 | 0.11942 | 0.056383 | -0.11942 | -0.05784 | 1.2056e-06 | -0.001457 | 0.0038249 | 0.0038431 | 0.0038431 | 0.99673 | -0.12828 | 0.99672 | -0.1282 | 1.7469
76 | -9.7023 | -4.3086 | 9.7133 | 4.2202 | 0.011023 | -0.088469 | 0.30746 | 0.30636 | 0.30746 | 0.99673 | -0.12828 | 0.99792 | -0.12153 | 24.0957
77 | 0.17999 | 0.085753 | -0.17999 | -0.087172 | 2.6607e-06 | -0.0014194 | 0.0057675 | 0.0057853 | 0.0057853 | 0.99792 | -0.12153 | 0.9979 | -0.1214 | 2.6297
78 | 8.2065 | 3.7711 | -8.2038 | -3.7776 | 0.0027178 | -0.0065264 | 0.26126 | 0.26136 | 0.26136 | 0.99792 | -0.12153 | 0.99757 | -0.12314 | 40.9653
79 | 7.7714 | 3.4984 | -7.7713 | -3.4988 | 3.6636e-05 | -0.00046027 | 0.24747 | 0.24747 | 0.24747 | 0.99416 | -0.21179 | 0.99415 | -0.21182 | 19.3945
80 | -0.3881 | -0.18797 | 0.38812 | 0.18788 | 2.5063e-05 | -8.8154e-05 | 0.012582 | 0.012581 | 0.012582 | 0.98937 | -0.28493 | 0.98944 | -0.2845 | 5.9914
81 | -0.62806 | -0.28849 | 0.62815 | 0.28463 | 8.9959e-05 | -0.0038565 | 0.020165 | 0.020118 | 0.020165 | 0.98944 | -0.2845 | 0.98957 | -0.28559 | 9.1658
82 | 0.23994 | 0.10061 | -0.23989 | -0.11616 | 5.245e-05 | -0.015545 | 0.007591 | 0.0077778 | 0.0077778 | 0.98944 | -0.2845 | 0.98923 | -0.28289 | 3.5354
83 | -0.98149 | -0.4557 | 0.98177 | 0.45082 | 0.00028185 | -0.0048809 | 0.031567 | 0.031507 | 0.031567 | 0.98957 | -0.28559 | 0.98984 | -0.28783 | 14.3487
84 | 0.35333 | 0.17106 | -0.35332 | -0.17112 | 1.3131e-05 | -5.7465e-05 | 0.011452 | 0.011453 | 0.011453 | 0.98957 | -0.28559 | 0.98953 | -0.28583 | 5.4536
85 | 0.23989 | 0.11616 | -0.23989 | -0.11618 | 2.2983e-06 | -2.347e-05 | 0.0077778 | 0.0077781 | 0.0077781 | 0.98923 | -0.28289 | 0.98922 | -0.28295 | 3.7039
86 | 0.58191 | 0.28142 | -0.5819 | -0.28183 | 8.2856e-06 | -0.00040435 | 0.01887 | 0.018875 | 0.018875 | 0.98884 | -0.30022 | 0.98883 | -0.3001 | 8.5797
87 | -1.6605 | -0.76549 | 1.6605 | 0.76513 | 6.0985e-05 | -0.00035778 | 0.053324 | 0.053319 | 0.053324 | 0.98984 | -0.28783 | 0.98987 | -0.28811 | 24.2382
88 | 0.6787 | 0.31467 | -0.67868 | -0.31469 | 2.2995e-05 | -1.7308e-05 | 0.021818 | 0.021818 | 0.021818 | 0.98984 | -0.28783 | 0.9898 | -0.28809 | 10.3895
89 | -2.0412 | -0.94952 | 2.0426 | 0.95014 | 0.0013078 | 0.00061981 | 0.065654 | 0.065652 | 0.065654 | 0.98987 | -0.28811 | 0.99054 | -0.28325 | 31.2638
90 | -2.0426 | -0.95014 | 2.0428 | 0.94918 | 0.0002539 | -0.00095872 | 0.065652 | 0.065639 | 0.065652 | 0.99054 | -0.28325 | 0.99066 | -0.28424 | 29.8416
91 | -2.287 | -1.0674 | 2.2875 | 1.0677 | 0.00050037 | 0.00025257 | 0.073543 | 0.073542 | 0.073543 | 0.99066 | -0.28424 | 0.99089 | -0.28259 | 35.0203
92 | 0.35544 | 0.17177 | -0.35544 | -0.17215 | 2.8566e-06 | -0.00037414 | 0.011532 | 0.011537 | 0.011537 | 0.9882 | -0.29628 | 0.98819 | -0.29621 | 5.2441
93 | 0.26228 | 0.11734 | -0.26224 | -0.12623 | 3.6388e-05 | -0.0088938 | 0.0083936 | 0.0085032 | 0.0085032 | 0.9882 | -0.29628 | 0.98807 | -0.29519 | 3.8651
94 | 0.26224 | 0.12623 | -0.26224 | -0.12701 | 3.2295e-06 | -0.00077802 | 0.0085032 | 0.0085131 | 0.0085131 | 0.98807 | -0.29519 | 0.98806 | -0.29508 | 3.8696
95 | -7.6815 | -3.4738 | 7.6817 | 3.4717 | 0.0001597 | -0.002051 | 0.24484 | 0.24482 | 0.24484 | 0.99397 | -0.21277 | 0.99399 | -0.21266 | 19.1884
96 | 0.086027 | 0.040836 | -0.086027 | -0.041665 | 3.6024e-07 | -0.00082897 | 0.0027657 | 0.0027761 | 0.0027761 | 0.99397 | -0.21277 | 0.99397 | -0.21273 | 1.2618
97 | 0.088421 | 0.042521 | -0.088421 | -0.042824 | 1.3944e-07 | -0.00030302 | 0.0028494 | 0.0028532 | 0.0028532 | 0.99399 | -0.21266 | 0.99399 | -0.21264 | 1.2969
98 | -7.7701 | -3.5142 | 7.7713 | 3.4988 | 0.0012271 | -0.0154 | 0.24767 | 0.24747 | 0.24767 | 0.99399 | -0.21266 | 0.99415 | -0.21182 | 19.4096
99 | -0.36193 | -0.17529 | 0.36193 | 0.17513 | 1.2358e-06 | -0.00015541 | 0.01176 | 0.011758 | 0.01176 | 0.98717 | -0.20838 | 0.98717 | -0.20841 | 5.3453
100 | -0.36193 | -0.17513 | 0.36196 | 0.17066 | 3.5409e-05 | -0.0044758 | 0.011758 | 0.011701 | 0.011758 | 0.98717 | -0.20841 | 0.98726 | -0.20924 | 5.3444
101 | 0.38245 | 0.18474 | -0.38245 | -0.18523 | 4.3726e-06 | -0.00049264 | 0.012419 | 0.012425 | 0.012425 | 0.98726 | -0.20924 | 0.98725 | -0.20914 | 5.6479
102 | -0.74442 | -0.35539 | 0.74452 | 0.35233 | 0.00010317 | -0.0030661 | 0.02412 | 0.024081 | 0.02412 | 0.98726 | -0.20924 | 0.98739 | -0.2104 | 10.9637
103 | 1.2372 | 0.55317 | -1.2361 | -0.5651 | 0.0011094 | -0.011936 | 0.039622 | 0.03977 | 0.03977 | 0.98739 | -0.2104 | 0.98656 | -0.20376 | 18.0774
104 | 0.25729 | 0.12457 | -0.25728 | -0.12461 | 4.5867e-06 | -4.0022e-05 | 0.0083573 | 0.0083579 | 0.0083579 | 0.98739 | -0.2104 | 0.98737 | -0.21052 | 3.9799
105 | -2.239 | -1.0301 | 2.241 | 1.024 | 0.0019766 | -0.0060648 | 0.072056 | 0.071975 | 0.072056 | 0.98739 | -0.2104 | 0.98821 | -0.21716 | 32.7525
106 | -0.24727 | -0.1197 | 0.2473 | 0.1113 | 3.0353e-05 | -0.0083917 | 0.0080109 | 0.0079073 | 0.0080109 | 0.98995 | -0.23142 | 0.99006 | -0.23241 | 3.6413
107 | 0.24727 | 0.1197 | -0.24726 | -0.11976 | 6.2705e-06 | -6.0224e-05 | 0.0080109 | 0.0080117 | 0.0080117 | 0.98995 | -0.23142 | 0.98992 | -0.23159 | 3.8151
108 | 0.27243 | 0.13121 | -0.27242 | -0.13194 | 3.2329e-06 | -0.00072739 | 0.0088166 | 0.0088258 | 0.0088258 | 0.99006 | -0.23241 | 0.99005 | -0.2323 | 4.0117
109 | 2.581 | 1.1745 | -2.5759 | -1.1861 | 0.0051507 | -0.011631 | 0.082681 | 0.082841 | 0.082841 | 0.99006 | -0.23241 | 0.98821 | -0.21716 | 37.655
110 | -3.1008 | -1.417 | 3.1093 | 1.4043 | 0.0085304 | -0.012672 | 0.099403 | 0.09922 | 0.099403 | 0.99006 | -0.23241 | 0.99262 | -0.25298 | 45.1831
111 | 0.33489 | 0.16211 | -0.33487 | -0.16219 | 1.5498e-05 | -7.6126e-05 | 0.010869 | 0.01087 | 0.01087 | 0.98821 | -0.21716 | 0.98816 | -0.21747 | 5.1761
112 | 0.33756 | 0.16336 | -0.33754 | -0.16348 | 2.5055e-05 | -0.00011997 | 0.010973 | 0.010975 | 0.010975 | 0.98656 | -0.20376 | 0.98648 | -0.20425 | 5.2262
113 | 0.89855 | 0.40174 | -0.89743 | -0.40192 | 0.0011129 | -0.00017642 | 0.028801 | 0.028811 | 0.028811 | 0.98656 | -0.20376 | 0.98525 | -0.21435 | 13.7195
114 | 3.5345 | 1.5948 | -3.5309 | -1.5987 | 0.0035552 | -0.0038832 | 0.11266 | 0.11272 | 0.11272 | 0.99357 | -0.26042 | 0.99262 | -0.25298 | 51.2375
115 | -3.7544 | -1.7013 | 3.7556 | 1.7001 | 0.0012095 | -0.0011308 | 0.11976 | 0.11974 | 0.11976 | 0.99357 | -0.26042 | 0.99387 | -0.26281 | 54.4363
116 | 0.21994 | 0.10643 | -0.21993 | -0.10652 | 7.2633e-06 | -9.0763e-05 | 0.007099 | 0.0071002 | 0.0071002 | 0.99357 | -0.26042 | 0.99353 | -0.26064 | 3.381
117 | 0.29638 | 0.14323 | -0.29637 | -0.14354 | 1.6259e-06 | -0.00031203 | 0.0095729 | 0.0095769 | 0.0095769 | 0.99262 | -0.25298 | 0.99262 | -0.25293 | 4.3531
118 | 0.12527 | 0.05118 | -0.12526 | -0.059516 | 7.5059e-06 | -0.0083352 | 0.0039354 | 0.0040334 | 0.0040334 | 0.99262 | -0.25298 | 0.99257 | -0.25256 | 1.8334
119 | -4.0665 | -1.8495 | 4.0678 | 1.8451 | 0.0012866 | -0.0044306 | 0.12976 | 0.12969 | 0.12976 | 0.99387 | -0.26281 | 0.99421 | -0.25872 | 35.8446
120 | 0.31087 | 0.14938 | -0.31086 | -0.15056 | 6.7326e-06 | -0.0011814 | 0.010018 | 0.010033 | 0.010033 | 0.99387 | -0.26281 | 0.99385 | -0.26263 | 4.5603
121 | 0.12526 | 0.059516 | -0.12526 | -0.060667 | 1.0674e-06 | -0.0011516 | 0.0040334 | 0.0040479 | 0.0040479 | 0.99257 | -0.25256 | 0.99256 | -0.25249 | 1.84
122 | 0.44608 | 0.18389 | -0.44605 | -0.18667 | 3.2201e-05 | -0.0027814 | 0.014137 | 0.014168 | 0.014168 | 0.98525 | -0.21435 | 0.98518 | -0.21393 | 6.4402
123 | 0.18225 | 0.087693 | -0.18222 | -0.088252 | 3.1285e-05 | -0.00055905 | 0.0059258 | 0.0059332 | 0.0059332 | 0.98525 | -0.21435 | 0.98507 | -0.21549 | 2.8253
124 | 0.099107 | 0.042924 | -0.099104 | -0.047998 | 2.8773e-06 | -0.005074 | 0.0031359 | 0.0031973 | 0.0031973 | 0.99421 | -0.25872 | 0.99419 | -0.2585 | 1.4533
125 | -4.1669 | -1.888 | 4.167 | 1.8866 | 0.00013226 | -0.0014325 | 0.13283 | 0.13281 | 0.13283 | 0.99421 | -0.25872 | 0.99425 | -0.25855 | 20.8195
126 | 0.44605 | 0.18667 | -0.44577 | -0.20987 | 0.00027451 | -0.023196 | 0.014168 | 0.014445 | 0.014445 | 0.98518 | -0.21393 | 0.98461 | -0.20957 | 6.5661
127 | 4.7822 | 2.1687 | -4.7819 | -2.1707 | 0.0002523 | -0.0020424 | 0.1524 | 0.15243 | 0.15243 | 0.99461 | -0.25676 | 0.99455 | -0.25703 | 23.8918
128 | -5.0495 | -2.2981 | 5.0501 | 2.2936 | 0.00062779 | -0.0045193 | 0.16102 | 0.16096 | 0.16102 | 0.99461 | -0.25676 | 0.99474 | -0.25612 | 25.2385
129 | 4.7819 | 2.1707 | -4.7808 | -2.1798 | 0.0011255 | -0.0090988 | 0.15243 | 0.15255 | 0.15255 | 0.99455 | -0.25703 | 0.99431 | -0.25824 | 23.9101
130 | -5.0501 | -2.2936 | 5.0506 | 2.2903 | 0.00045628 | -0.0032877 | 0.16096 | 0.16092 | 0.16096 | 0.99474 | -0.25612 | 0.99483 | -0.25565 | 25.2293
131 | 0.26953 | 0.12911 | -0.26952 | -0.13005 | 3.9883e-06 | -0.00093428 | 0.0086766 | 0.0086883 | 0.0086883 | 0.99431 | -0.25824 | 0.9943 | -0.25812 | 3.9492
132 | 4.5113 | 2.0507 | -4.511 | -2.0532 | 0.0002718 | -0.0024859 | 0.14387 | 0.1439 | 0.1439 | 0.99431 | -0.25824 | 0.99425 | -0.25855 | 22.5554
133 | 2.9599 | 1.3854 | -2.9589 | -1.3848 | 0.0010678 | 0.00059013 | 0.094832 | 0.094833 | 0.094833 | 0.99483 | -0.25565 | 0.99445 | -0.25834 | 45.1586
134 | -8.0105 | -3.6757 | 8.0204 | 3.7018 | 0.0099118 | 0.026072 | 0.25575 | 0.25574 | 0.25575 | 0.99483 | -0.25565 | 0.9971 | -0.12533 | 39.6509
135 | 0.26952 | 0.13005 | -0.26952 | -0.13053 | 2.0903e-06 | -0.00048863 | 0.0086883 | 0.0086945 | 0.0086945 | 0.9943 | -0.25812 | 0.99429 | -0.25805 | 3.9521
136 | 2.6122 | 1.2169 | -2.6113 | -1.2164 | 0.00090629 | 0.00048189 | 0.083654 | 0.083655 | 0.083655 | 0.99445 | -0.25834 | 0.99408 | -0.26096 | 39.8358
137 | -8.0995 | -3.7401 | 8.1001 | 3.7387 | 0.00058037 | -0.0014322 | 0.25829 | 0.25826 | 0.25829 | 0.9971 | -0.12533 | 0.99718 | -0.12499 | 40.4837
138 | 2.6113 | 1.2164 | -2.604 | -1.2326 | 0.0073104 | -0.016196 | 0.083655 | 0.083882 | 0.083882 | 0.99408 | -0.26096 | 0.99148 | -0.2382 | 38.1283
139 | -8.1001 | -3.7387 | 8.1032 | 3.731 | 0.0030963 | -0.0076504 | 0.25826 | 0.25815 | 0.25826 | 0.99718 | -0.12499 | 0.99757 | -0.12314 | 40.4803
140 | 0.10501 | 0.050632 | -0.10501 | -0.050857 | 4.0804e-06 | -0.00022413 | 0.0034179 | 0.0034208 | 0.0034208 | 0.98461 | -0.20957 | 0.98457 | -0.20983 | 1.629
141 | 0.34076 | 0.15924 | -0.34042 | -0.16083 | 0.00033868 | -0.0015913 | 0.011028 | 0.01105 | 0.01105 | 0.98461 | -0.20957 | 0.98357 | -0.21687 | 5.262
142 | 0.17514 | 0.081652 | -0.17514 | -0.083343 | 3.1579e-06 | -0.0016913 | 0.0056715 | 0.0056927 | 0.0056927 | 0.98357 | -0.21687 | 0.98356 | -0.21672 | 2.5876
143 | 0.16528 | 0.079177 | -0.16524 | -0.080031 | 3.9301e-05 | -0.00085385 | 0.0053789 | 0.0053901 | 0.0053901 | 0.98357 | -0.21687 | 0.98333 | -0.21847 | 2.5667
144 | 0.11239 | 0.052953 | -0.11237 | -0.053818 | 1.8041e-05 | -0.00086537 | 0.0036465 | 0.0036575 | 0.0036575 | 0.98356 | -0.21672 | 0.98339 | -0.21786 | 1.7417
145 | -0.11237 | -0.054424 | 0.11237 | 0.053818 | 4.6962e-07 | -0.00060575 | 0.0036652 | 0.0036575 | 0.0036652 | 0.98339 | -0.21782 | 0.98339 | -0.21786 | 1.666
146 | 0.52073 | 0.25135 | -0.52071 | -0.25219 | 1.3723e-05 | -0.00084574 | 0.01684 | 0.01685 | 0.01685 | 0.99121 | -0.23572 | 0.99118 | -0.23549 | 7.6593
147 | -2.6032 | -1.2344 | 2.604 | 1.2326 | 0.00077903 | -0.0017144 | 0.083907 | 0.083882 | 0.083907 | 0.99121 | -0.23572 | 0.99148 | -0.2382 | 38.1393
148 | 1.7283 | 0.81146 | -1.728 | -0.81132 | 0.0003319 | 0.00013725 | 0.055607 | 0.055607 | 0.055607 | 0.99121 | -0.23572 | 0.99101 | -0.23713 | 26.4797
149 | 1.503 | 0.70235 | -1.5029 | -0.70278 | 5.9489e-05 | -0.00042971 | 0.048325 | 0.048331 | 0.048331 | 0.99101 | -0.23713 | 0.99097 | -0.23681 | 21.9686
150 | 0.26251 | 0.12611 | -0.2625 | -0.12691 | 3.2856e-06 | -0.00079984 | 0.0084837 | 0.0084938 | 0.0084938 | 0.99097 | -0.23681 | 0.99096 | -0.2367 | 3.8608
151 | 1.2404 | 0.57666 | -1.2396 | -0.58499 | 0.00077609 | -0.0083265 | 0.039848 | 0.039954 | 0.039954 | 0.99097 | -0.23681 | 0.99039 | -0.23176 | 18.1607
152 | 0.077234 | 0.037183 | -0.077234 | -0.037406 | 7.9168e-08 | -0.00022267 | 0.0024971 | 0.0024999 | 0.0024999 | 0.99096 | -0.2367 | 0.99096 | -0.23669 | 1.1363
153 | 0.18275 | 0.086498 | -0.18275 | -0.088509 | 4.0004e-06 | -0.0020108 | 0.0058933 | 0.0059186 | 0.0059186 | 0.99039 | -0.23176 | 0.99037 | -0.23157 | 2.6903
154 | 0.74613 | 0.35642 | -0.74607 | -0.3581 | 5.6361e-05 | -0.0016837 | 0.024102 | 0.024123 | 0.024123 | 0.99039 | -0.23176 | 0.99032 | -0.23112 | 10.9651
155 | 0.18461 | 0.087208 | -0.1846 | -0.088572 | 2.7633e-06 | -0.0013641 | 0.005951 | 0.0059681 | 0.0059681 | 0.99039 | -0.23176 | 0.99038 | -0.23163 | 2.7128
156 | 0.12615 | 0.054864 | -0.12614 | -0.059652 | 4.4513e-06 | -0.0047876 | 0.0040096 | 0.0040673 | 0.0040673 | 0.99039 | -0.23176 | 0.99036 | -0.2315 | 1.8488
157 | 0.1846 | 0.088572 | -0.1846 | -0.089407 | 1.699e-06 | -0.00083475 | 0.0059681 | 0.0059787 | 0.0059787 | 0.99038 | -0.23163 | 0.99037 | -0.23156 | 2.7176
158 | 0.12614 | 0.059652 | -0.12614 | -0.061094 | 1.3665e-06 | -0.0014421 | 0.0040673 | 0.0040855 | 0.0040855 | 0.99036 | -0.2315 | 0.99035 | -0.2314 | 1.857
159 | 0.64025 | 0.30685 | -0.64022 | -0.30793 | 2.6554e-05 | -0.0010788 | 0.020696 | 0.020709 | 0.020709 | 0.99032 | -0.23112 | 0.99028 | -0.23076 | 9.4134
160 | 0.55079 | 0.26462 | -0.55079 | -0.26493 | 5.7331e-06 | -0.00031513 | 0.017813 | 0.017817 | 0.017817 | 0.99028 | -0.23076 | 0.99027 | -0.23067 | 8.0986
161 | 0.1006 | 0.046587 | -0.1006 | -0.048722 | 1.2451e-06 | -0.0021352 | 0.0032081 | 0.0032346 | 0.0032346 | 0.99757 | -0.12314 | 0.99756 | -0.12304 | 1.4703
162 | 0.25928 | 0.12375 | -0.25927 | -0.12521 | 5.8702e-06 | -0.0014629 | 0.0083749 | 0.0083934 | 0.0083934 | 0.99027 | -0.23067 | 0.99025 | -0.23048 | 3.8152
163 | 0.15048 | 0.072519 | -0.15048 | -0.072879 | 4.882e-07 | -0.00036059 | 0.0048695 | 0.0048741 | 0.0048741 | 0.99025 | -0.23048 | 0.99025 | -0.23045 | 2.2155

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 19.0034 | 8.5447

## res_load
| p_mw | q_mvar
0 | 0.093829 | 0.045443
1 | 0.12009 | 0.058162
2 | 0.16029 | 0.077632
3 | 0.098119 | 0.047521
4 | 0.1524 | 0.073809
5 | 0.077081 | 0.037332
6 | 0.11334 | 0.054891
7 | 0.11786 | 0.057084
8 | 0.13959 | 0.067605
9 | 0.12649 | 0.061261
10 | 0.1331 | 0.064462
11 | 0.12101 | 0.058607
12 | 0.32663 | 0.15819
13 | 0.32226 | 0.15608
14 | 0.41167 | 0.19938
15 | 0.086895 | 0.042085
16 | 0.34227 | 0.16577
17 | 0.085793 | 0.041552
18 | 0.37841 | 0.18327
19 | 0.27965 | 0.13544
20 | 0.24603 | 0.11916
21 | 0.073873 | 0.035778
22 | 0.39874 | 0.19312
23 | 0.33894 | 0.16416
24 | 0.079145 | 0.038332
25 | 0.10503 | 0.050867
26 | 0.24543 | 0.11887
27 | 0.33103 | 0.16033
28 | 0.13938 | 0.067506
29 | 0.17868 | 0.086538
30 | 0.33399 | 0.16176
31 | 0.13347 | 0.06464
32 | 0.25643 | 0.1242
33 | 0.10818 | 0.052395
34 | 0.41286 | 0.19996
35 | 0.11942 | 0.05784
36 | 0.3881 | 0.18797
37 | 0.5819 | 0.28183
38 | 0.35332 | 0.17112
39 | 0.38072 | 0.18439
40 | 0.23989 | 0.11618
41 | 0.24414 | 0.11824
42 | 0.26224 | 0.12701
43 | 0.35544 | 0.17215
44 | 0.35137 | 0.17018
45 | 0.086027 | 0.041665
46 | 0.088421 | 0.042824
47 | 0.36193 | 0.17529
48 | 0.38245 | 0.18523
49 | 0.24726 | 0.11976
50 | 0.33487 | 0.16219
51 | 0.25728 | 0.12461
52 | 0.21993 | 0.10652
53 | 0.12526 | 0.060667
54 | 0.29637 | 0.14354
55 | 0.27242 | 0.13194
56 | 0.33754 | 0.16348
57 | 0.2691 | 0.13033
58 | 0.31086 | 0.15056
59 | 0.18222 | 0.088252
60 | 0.26731 | 0.12947
61 | 0.34397 | 0.16659
62 | 0.34662 | 0.16788
63 | 0.079122 | 0.038321
64 | 0.26952 | 0.13053
65 | 0.10501 | 0.050857
66 | 0.062749 | 0.030391
67 | 0.16524 | 0.080031
68 | 0.099104 | 0.047998
69 | 0.11237 | 0.054424
70 | 0.35419 | 0.17154
71 | 0.52071 | 0.25219
72 | 0.22501 | 0.10898
73 | 0.18527 | 0.08973
74 | 0.077234 | 0.037406
75 | 0.1846 | 0.089407
76 | 0.12614 | 0.061094
77 | 0.18275 | 0.088509
78 | 0.10582 | 0.051253
79 | 0.08943 | 0.043313
80 | 0.29151 | 0.14118
81 | 0.10879 | 0.052691
82 | 0.15048 | 0.072879
83 | 0.1006 | 0.048722
84 | 0.17999 | 0.087172

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1